## Registers
No | Section | Address_Hex | Address_Dec | Definition | Data_Type | FC_Code | Registers | Unit | Scale_Factor | R/W | Description
--- control ---
1 | control | 0x03E9 | 1001 | Generation Start | S16 | FC03 | 1 | W |  | RO
2 | control | 0x03EA | 1002 | Generation Stop | S16 | FC03 | 1 | W |  | RO
--- realtime_data ---
3 | realtime_data | 0x7531 | 30001 | Model KO_KO_명 | S16 | FC03 | 1 |  |  | RO
4 | realtime_data | 0x7539 | 30009 | Serial KO_KO_번호 | S16 | FC03 | 1 |  |  | RO
5 | realtime_data | 0x7541 | 30017 | Inverter Version | S16 | FC03 | 1 |  |  | RO
6 | realtime_data | 0x7542 | 30018 | Inverter Capacity | S16 | FC03 | 1 | kW |  | RO
7 | realtime_data | 0x7543 | 30019 | Current Time (Year) | S16 | FC03 | 1 |  |  | RO
8 | realtime_data | 0x7544 | 30020 | Current Time (Month) | S16 | FC03 | 1 |  |  | RO
9 | realtime_data | 0x7545 | 30021 | Current Time (Day) | S16 | FC03 | 1 |  |  | RO
10 | realtime_data | 0x7546 | 30022 | Current Time (Hour) | S16 | FC03 | 1 |  |  | RO
11 | realtime_data | 0x7547 | 30023 | Current Time (Minute) | S16 | FC03 | 1 |  |  | RO
12 | realtime_data | 0x7548 | 30024 | Current Time (Second) | S16 | FC03 | 1 |  |  | RO
13 | realtime_data | 0x7549 | 30025 | System Operation Status | S16 | FC03 | 1 |  |  | RO
14 | realtime_data | 0x754A | 30026 | Generation Status | S16 | FC03 | 1 |  |  | RO
15 | realtime_data | 0x754B | 30027 | Inverter Status | S16 | FC03 | 1 |  |  | RO
--- fault ---
16 | fault | 0x754C | 30028 | SW Fault Status | S16 | FC03 | 1 |  |  | RO
17 | fault | 0x754D | 30029 | HW Fault Status | S16 | FC03 | 1 |  |  | RO
18 | fault | 0x754E | 30030 | Today Generation Duration ( Inverter Normal Running Duration ) | S16 | FC03 | 1 |  |  | RO
19 | fault | 0x754F | 30031 | Today Generation Time Time (Hour,Min) | S16 | FC03 | 1 |  |  | RO
20 | fault | 0x7550 | 30032 | Today Latest Stop Time (Hour, Min) | S16 | FC03 | 1 |  |  | RO
21 | fault | 0x7551 | 30033 | Total Generation Duration | U32 | FC03 | 2 |  |  | RO
22 | fault | 0x7553 | 30035 | PV Voltage | Float32 | FC03 | 2 | V |  | RO
23 | fault | 0x7555 | 30037 | Inverter DC Voltage | Float32 | FC03 | 2 | V |  | RO
24 | fault | 0x7557 | 30039 | PV Current | Float32 | FC03 | 2 | A |  | RO
25 | fault | 0x7559 | 30041 | PV Power | Float32 | FC03 | 2 | W |  | RO
26 | fault | 0x755B | 30043 | Voltage (KO_KO_종합) | Float32 | FC03 | 2 | V |  | RO
27 | fault | 0x755D | 30045 | Current (KO_KO_종합) | Float32 | FC03 | 2 | A |  | RO
28 | fault | 0x755F | 30047 | Active Power (KO_KO_종합) | Float32 | FC03 | 2 | W |  | RO
29 | fault | 0x7561 | 30049 | Apparent Power (KO_KO_종합) | Float32 | FC03 | 2 | VA |  | RO
30 | fault | 0x7563 | 30051 | Power Factor (KO_KO_종합) | Float32 | FC03 | 2 | % |  | RO
31 | fault | 0x7565 | 30053 | Frequency | Float32 | FC03 | 2 | Hz |  | RO
32 | fault | 0x7567 | 30055 | Today Generated Energy | Float32 | FC03 | 2 | Wh |  | RO
33 | fault | 0x7569 | 30057 | Total Generated Energy | Float32 | FC03 | 2 | Wh |  | RO
34 | fault | 0x756B | 30059 | L1 Voltage | Float32 | FC03 | 2 | V |  | RO
35 | fault | 0x756D | 30061 | L2 Voltage | Float32 | FC03 | 2 | V |  | RO
36 | fault | 0x003E | 62 | L3 Voltage | Float32 | FC03 | 2 | V |  | RO
37 | fault | 0x7571 | 30065 | L1 Current | Float32 | FC03 | 2 | A |  | RO
38 | fault | 0x7573 | 30067 | L2 Current | Float32 | FC03 | 2 | A |  | RO
39 | fault | 0x7575 | 30069 | L3 Current | Float32 | FC03 | 2 | A |  | RO
40 | fault | 0x7577 | 30071 | L1 Active Power | Float32 | FC03 | 2 | W |  | RO
41 | fault | 0x7579 | 30073 | L2 Active Power | Float32 | FC03 | 2 | W |  | RO
42 | fault | 0x757B | 30075 | L3 Active Power | Float32 | FC03 | 2 | W |  | RO
43 | fault | 0x757D | 30077 | L1 Apparent Power | Float32 | FC03 | 2 | VA |  | RO
44 | fault | 0x757F | 30079 | L2 Apparent Power | Float32 | FC03 | 2 | VA |  | RO
45 | fault | 0x7581 | 30081 | L3 Apparent Power | Float32 | FC03 | 2 | VA |  | RO
46 | fault | 0x7583 | 30083 | L1 Power Factor | Float32 | FC03 | 2 | % |  | RO
47 | fault | 0x7585 | 30085 | L2 Power Factor | Float32 | FC03 | 2 | % |  | RO
48 | fault | 0x7587 | 30087 | L3 Power Factor | Float32 | FC03 | 2 | % |  | RO
49 | fault | 0x7589 | 30089 | PV MPPT Voltage | Float32 | FC03 | 2 |  |  | RO
50 | fault | 0x758B | 30091 | KO_KO_방열판 Temperature ( Inverter Internal Temperature ) | Float32 | FC03 | 2 |  |  | RO
51 | fault | 0x758F | 30095 | KO_KO_적산 Power KO_KO_량 | U32 | FC03 | 2 | MWh |  | RO
52 | fault | 0x7591 | 30097 | KO_KO_적산 Power KO_KO_량 | U32 | FC03 | 2 | Wh |  | RO
53 | fault | 0x7593 | 30099 | PV Status Total(SUM) | S16 | FC03 | 1 |  |  | RO
54 | fault | 0x7594 | 30100 | PV1 Status Total | S16 | FC03 | 1 |  |  | RO
55 | fault | 0x7595 | 30101 | PV2 Status Total | S16 | FC03 | 1 |  |  | RO
56 | fault | 0x7596 | 30102 | Inverter Status | S16 | FC03 | 1 |  |  | RO
57 | fault | 0x7597 | 30103 | Grid Status | S16 | FC03 | 1 |  |  | RO
58 | fault | 0x7598 | 30104 | Converter Status | S16 | FC03 | 1 |  |  | RO
59 | fault | 0x7599 | 30105 | PV 1 Voltage | Float32 | FC03 | 2 | V |  | RO
60 | fault | 0x759B | 30107 | PV 1 Current | Float32 | FC03 | 2 | A |  | RO
61 | fault | 0x759D | 30109 | PV 1 Power | Float32 | FC03 | 2 | W |  | RO
62 | fault | 0x759F | 30111 | PV 2 Voltage | Float32 | FC03 | 2 | V |  | RO
63 | fault | 0x75A1 | 30113 | PV 2 Current | Float32 | FC03 | 2 | A |  | RO
64 | fault | 0x7599 | 30105 | PV 2 Power | Float32 | FC03 | 2 | W |  | RO
65 | fault | 0x75A5 | 30117 | AD CH1( Solar Irradiance Horizontal ) | S16 | FC03 | 1 |  |  | RO
66 | fault | 0x75A6 | 30118 | AD CH2( Solar Irradiance Inclined ) | S16 | FC03 | 1 |  |  | RO
67 | fault | 0x75A7 | 30119 | AD CH3( Temperature Outdoor ) | S16 | FC03 | 1 |  |  | RO
68 | fault | 0x75A8 | 30120 | AD CH4( Temperature KO_KO_모듈) | S16 | FC03 | 1 |  |  | RO
69 | fault | 0x75A9 | 30121 | CH1 Current( Integrated Junction Box Channel 1 Current ) | S16 | FC03 | 1 |  |  | RO
70 | fault | 0x75AA | 30122 | CH2 Current( Integrated Junction Box Channel 2 Current ) | S16 | FC03 | 1 |  |  | RO
71 | fault | 0x75AB | 30123 | CH3 Current( Integrated Junction Box Channel 3 Current ) | S16 | FC03 | 1 |  |  | RO
72 | fault | 0x75AC | 30124 | CH4 Current( Integrated Junction Box Channel 4 Current ) | S16 | FC03 | 1 |  |  | RO
73 | fault | 0x75AD | 30125 | KO_KO_미사용 | U16 | FC03 | 1 |  |  | RO
--- write_reg ---
74 | write_reg | 0xA411 | 42001 | Inverter Capacity | S16 | FC03 | 1 | W |  | RO
75 | write_reg | 0xA412 | 42002 | Uint16 | S16 | FC03 | 1 |  |  | RO
76 | write_reg | 0xA413 | 42003 | Uint16 | S16 | FC03 | 1 |  |  | RO
77 | write_reg | 0xA414 | 42004 | Uint16 | S16 | FC03 | 1 |  |  | RO
78 | write_reg | 0xA415 | 42005 | Uint16 | S16 | FC03 | 1 |  |  | RO
79 | write_reg | 0xA416 | 42006 | Uint16 | S16 | FC03 | 1 |  |  | RO
80 | write_reg | 0xA417 | 42007 | Uint16 | S16 | FC03 | 1 |  |  | RO
81 | write_reg | 0xA418 | 42008 | Uint16 | S16 | FC03 | 1 |  |  | RO
82 | write_reg | 0xA419 | 42009 | Uint16 | S16 | FC03 | 1 |  |  | RO
83 | write_reg | 0xA41A | 42010 | Uint16 | S16 | FC03 | 1 |  |  | RO
84 | write_reg | 0xA41B | 42011 | Uint16 | S16 | FC03 | 1 |  |  | RO
85 | write_reg | 0xA41C | 42012 | Uint16 | S16 | FC03 | 1 |  |  | RO
86 | write_reg | 0xA41D | 42013 | Uint16 | S16 | FC03 | 1 |  |  | RO
87 | write_reg | 0xA41E | 42014 | Uint16 | S16 | FC03 | 1 |  |  | RO
88 | write_reg | 0xA41F | 42015 | Uint16 | S16 | FC03 | 1 |  |  | RO

## Status_Definitions
Code | Name | Description | Bit_Definition
0 | INITIAL | Initial mode
1 | STANDBY | Standby mode
3 | ON_GRID | On-Grid mode
4 | OFF_GRID | Off-Grid mode
5 | FAULT | Fault mode
9 | SHUTDOWN | Shutdown mode
NOTE: Add/edit status codes. Descriptions used in Stage 2 InverterMode mapping.

## Error_Fault_Codes
Register | Bit | Error_No | Description | Notes
(No error codes detected from PDF)

## Grid_Codes
Code_Hex | Description
(No regulation codes detected from PDF)
NOTE: Register 0x5101 - Grid regulation/country code setting

## Fuse_Open_Data
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x1034~0x1035 — PV string fuse open status bits

## Status_Bits_03FC
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x03FC~03FD — DEA-AVM inverter action/run-state bits

## Fuse_Check_Mask
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x513D~0x513E — PV string fuse check enable/disable mask

## REMS_Error_Bits
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: REMS Error Code register — bit-field inverter alarm flags

## REMS_Registers
No | Description | Length_Bytes | Unit
(Not detected from PDF)
NOTE: REMS protocol register layout (function code 0x7E)