## Register_Mapping
No | Section | Source_Addr_Hex | Source_Addr_Dec | Source_Name | Source_Type | Source_Unit | Source_Scale | Source_RW | Source_Regs | → | Solarize_Name | Solarize_Addr_Hex | Match_Type | Notes
--- control ---
1 | control | 0x03E9 | 1001 | Generation Start | S16 | W |  | RO | 1 | → | DEA_L1_CURRENT_HIGH | 0x03E9 | Auto
2 | control | 0x03EA | 1002 | Generation Stop | S16 | W |  | RO | 1 | → | DEA_L2_CURRENT_LOW | 0x03EA | Auto
--- realtime_data ---
3 | realtime_data | 0x7531 | 30001 | Model KO_명 | S16 |  |  | RO | 1 | → | MODEL_CODE |  | Ref(78%)
4 | realtime_data | 0x7539 | 30009 | Serial KO_번호 | S16 |  |  | RO | 1 | → | SERIAL_NUMBER |  | Ref(64%)
5 | realtime_data | 0x7541 | 30017 | Inverter Version | S16 |  |  | RO | 1 | → | INVERTER_ON_OFF |  | Ref(71%)
6 | realtime_data | 0x7542 | 30018 | Inverter Capacity | S16 | kW |  | RO | 1 | → | INVERTER_STATUS |  | Ref(69%)
7 | realtime_data | 0x7543 | 30019 | Current Time (Year) | S16 |  |  | RO | 1 | → |  |  | Unmapped
8 | realtime_data | 0x7544 | 30020 | Current Time (Month) | S16 |  |  | RO | 1 | → |  |  | Unmapped
9 | realtime_data | 0x7545 | 30021 | Current Time (Day) | S16 |  |  | RO | 1 | → | T_CURRENT |  | Ref(56%)
10 | realtime_data | 0x7546 | 30022 | Current Time (Hour) | S16 |  |  | RO | 1 | → | DEA_L3_CURRENT_HIGH |  | Ref(56%)
11 | realtime_data | 0x7547 | 30023 | Current Time (Minute) | S16 |  |  | RO | 1 | → |  |  | Unmapped
12 | realtime_data | 0x7548 | 30024 | Current Time (Second) | S16 |  |  | RO | 1 | → |  |  | Unmapped
13 | realtime_data | 0x7549 | 30025 | System Operation Status | S16 |  |  | RO | 1 | → | SYSTEM_STATUS |  | Ref(72%)
14 | realtime_data | 0x754A | 30026 | Generation Status | S16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(69%)
15 | realtime_data | 0x754B | 30027 | Inverter Status | S16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(100%)
--- fault ---
16 | fault | 0x754C | 30028 | SW Fault Status | S16 |  |  | RO | 1 | → | ERROR_CODE1 | 0x754C | Ref(supp)
17 | fault | 0x754D | 30029 | HW Fault Status | S16 |  |  | RO | 1 | → | ERROR_CODE2 | 0x754D | Ref(supp)
18 | fault | 0x754E | 30030 | Today Generation Duration ( Inverter Normal Running Duration ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
19 | fault | 0x754F | 30031 | Today Generation Time Time (Hour,Min) | S16 |  |  | RO | 1 | → | TOTAL_GENERATION_TIME_HIGH |  | Ref(72%)
20 | fault | 0x7550 | 30032 | Today Latest Stop Time (Hour, Min) | S16 |  |  | RO | 1 | → |  |  | Unmapped
21 | fault | 0x7551 | 30033 | Total Generation Duration | U32 |  |  | RO | 2 | → | TOTAL_GENERATION_TIME_LOW |  | Ref(80%)
22 | fault | 0x7553 | 30035 | PV Voltage | Float32 | V |  | RO | 2 | → | PV_VOLTAGE |  | Ref(100%)
23 | fault | 0x7555 | 30037 | Inverter DC Voltage | Float32 | V |  | RO | 2 | → | INV_R_VOLTAGE |  | Ref(75%)
24 | fault | 0x7557 | 30039 | PV Current | Float32 | A |  | RO | 2 | → | PV_CURRENT |  | Ref(100%)
25 | fault | 0x7559 | 30041 | PV Power | Float32 | W |  | RO | 2 | → | PV_POWER |  | Ref(100%)
26 | fault | 0x755B | 30043 | Voltage (KO_종합) | Float32 | V |  | RO | 2 | → | S_VOLTAGE |  | Ref(74%)
27 | fault | 0x755D | 30045 | Current (KO_종합) | Float32 | A |  | RO | 2 | → | T_CURRENT |  | Ref(74%)
28 | fault | 0x755F | 30047 | Active Power (KO_종합) | Float32 | W |  | RO | 2 | → | ACTIVE_POWER |  | Ref(89%)
29 | fault | 0x7561 | 30049 | Apparent Power (KO_종합) | Float32 | VA |  | RO | 2 | → | MPPT3_POWER_LOW |  | Ref(69%)
30 | fault | 0x7563 | 30051 | Power Factor (KO_종합) | Float32 | % |  | RO | 2 | → | POWER_FACTOR |  | Ref(89%)
31 | fault | 0x7565 | 30053 | Frequency | Float32 | Hz |  | RO | 2 | → | FREQUENCY |  | Ref(100%)
32 | fault | 0x7567 | 30055 | Today Generated Energy | Float32 | Wh |  | RO | 2 | → | TODAY_ENERGY |  | Ref(71%)
33 | fault | 0x7569 | 30057 | Total Generated Energy | Float32 | Wh |  | RO | 2 | → | TOTAL_ENERGY |  | Ref(71%)
34 | fault | 0x756B | 30059 | L1 Voltage | Float32 | V |  | RO | 2 | → | L1_VOLTAGE | 0x1001 | Auto
35 | fault | 0x756D | 30061 | L2 Voltage | Float32 | V |  | RO | 2 | → | L2_VOLTAGE | 0x1006 | Auto
36 | fault | 0x003E | 62 | L3 Voltage | Float32 | V |  | RO | 2 | → | L3_VOLTAGE | 0x100B | Auto
37 | fault | 0x7571 | 30065 | L1 Current | Float32 | A |  | RO | 2 | → | L1_CURRENT | 0x1002 | Auto
38 | fault | 0x7573 | 30067 | L2 Current | Float32 | A |  | RO | 2 | → | L2_CURRENT | 0x1007 | Auto
39 | fault | 0x7575 | 30069 | L3 Current | Float32 | A |  | RO | 2 | → | L3_CURRENT | 0x100C | Auto
40 | fault | 0x7577 | 30071 | L1 Active Power | Float32 | W |  | RO | 2 | → | ACTIVE_POWER |  | Ref(89%)
41 | fault | 0x7579 | 30073 | L2 Active Power | Float32 | W |  | RO | 2 | → | ACTIVE_POWER |  | Ref(89%)
42 | fault | 0x757B | 30075 | L3 Active Power | Float32 | W |  | RO | 2 | → | ACTIVE_POWER |  | Ref(89%)
43 | fault | 0x757D | 30077 | L1 Apparent Power | Float32 | VA |  | RO | 2 | → | REACTIVE_POWER |  | Ref(58%)
44 | fault | 0x757F | 30079 | L2 Apparent Power | Float32 | VA |  | RO | 2 | → | REACTIVE_POWER |  | Ref(58%)
45 | fault | 0x7581 | 30081 | L3 Apparent Power | Float32 | VA |  | RO | 2 | → | REACTIVE_POWER |  | Ref(58%)
46 | fault | 0x7583 | 30083 | L1 Power Factor | Float32 | % |  | RO | 2 | → | POWER_FACTOR |  | Ref(89%)
47 | fault | 0x7585 | 30085 | L2 Power Factor | Float32 | % |  | RO | 2 | → | POWER_FACTOR |  | Ref(89%)
48 | fault | 0x7587 | 30087 | L3 Power Factor | Float32 | % |  | RO | 2 | → | POWER_FACTOR |  | Ref(89%)
49 | fault | 0x7589 | 30089 | PV MPPT Voltage | Float32 |  |  | RO | 2 | → | MPPT3_VOLTAGE |  | Ref(86%)
50 | fault | 0x758B | 30091 | KO_방열판 Temperature ( Inverter Internal Temperature ) | Float32 |  |  | RO | 2 | → |  |  | Unmapped
51 | fault | 0x758F | 30095 | KO_적산 Power KO_량 | U32 | MWh |  | RO | 2 | → | S_POWER_LOW |  | Ref(73%)
52 | fault | 0x7591 | 30097 | KO_적산 Power KO_량 | U32 | Wh |  | RO | 2 | → | S_POWER_LOW |  | Ref(73%)
53 | fault | 0x7593 | 30099 | PV Status Total(SUM) | S16 |  |  | RO | 1 | → |  |  | Unmapped
54 | fault | 0x7594 | 30100 | PV1 Status Total | S16 |  |  | RO | 1 | → |  |  | Unmapped
55 | fault | 0x7595 | 30101 | PV2 Status Total | S16 |  |  | RO | 1 | → |  |  | Unmapped
56 | fault | 0x7596 | 30102 | Inverter Status | S16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(100%)
57 | fault | 0x7597 | 30103 | Grid Status | S16 |  |  | RO | 1 | → | GRID_STANDARD |  | Ref(67%)
58 | fault | 0x7598 | 30104 | Converter Status | S16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(90%)
59 | fault | 0x7599 | 30105 | PV 1 Voltage | Float32 | V |  | RO | 2 | → | PV1_VOLTAGE |  | Ref(96%)
60 | fault | 0x759B | 30107 | PV 1 Current | Float32 | A |  | RO | 2 | → | PV1_CURRENT |  | Ref(96%)
61 | fault | 0x759D | 30109 | PV 1 Power | Float32 | W |  | RO | 2 | → | PV1_POWER |  | Ref(95%)
62 | fault | 0x759F | 30111 | PV 2 Voltage | Float32 | V |  | RO | 2 | → | PV2_VOLTAGE |  | Ref(96%)
63 | fault | 0x75A1 | 30113 | PV 2 Current | Float32 | A |  | RO | 2 | → | PV2_CURRENT |  | Ref(96%)
64 | fault | 0x7599 | 30105 | PV 2 Power | Float32 | W |  | RO | 2 | → | PV2_POWER |  | Ref(95%)
65 | fault | 0x75A5 | 30117 | AD CH1( Solar Irradiance Horizontal ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
66 | fault | 0x75A6 | 30118 | AD CH2( Solar Irradiance Inclined ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
67 | fault | 0x75A7 | 30119 | AD CH3( Temperature Outdoor ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
68 | fault | 0x75A8 | 30120 | AD CH4( Temperature KO_모듈) | S16 |  |  | RO | 1 | → |  |  | Unmapped
69 | fault | 0x75A9 | 30121 | CH1 Current( Integrated Junction Box Channel 1 Current ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
70 | fault | 0x75AA | 30122 | CH2 Current( Integrated Junction Box Channel 2 Current ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
71 | fault | 0x75AB | 30123 | CH3 Current( Integrated Junction Box Channel 3 Current ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
72 | fault | 0x75AC | 30124 | CH4 Current( Integrated Junction Box Channel 4 Current ) | S16 |  |  | RO | 1 | → |  |  | Unmapped
73 | fault | 0x75AD | 30125 | KO_미사용 | U16 |  |  | RO | 1 | → |  |  | Unmapped
--- write_reg ---
74 | write_reg | 0xA411 | 42001 | Inverter Capacity | S16 | W |  | RO | 1 | → | INVERTER_STATUS |  | Ref(69%)
75 | write_reg | 0xA412 | 42002 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
76 | write_reg | 0xA413 | 42003 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
77 | write_reg | 0xA414 | 42004 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
78 | write_reg | 0xA415 | 42005 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
79 | write_reg | 0xA416 | 42006 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
80 | write_reg | 0xA417 | 42007 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
81 | write_reg | 0xA418 | 42008 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
82 | write_reg | 0xA419 | 42009 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
83 | write_reg | 0xA41A | 42010 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
84 | write_reg | 0xA41B | 42011 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
85 | write_reg | 0xA41C | 42012 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
86 | write_reg | 0xA41D | 42013 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
87 | write_reg | 0xA41E | 42014 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
88 | write_reg | 0xA41F | 42015 | Uint16 | S16 |  |  | RO | 1 | → |  |  | Unmapped
Mode: OFFLINE ¦ Match stats: Auto/Ref=55, Unmapped=33 ¦ Edit "Solarize_Name" for Unmapped rows (red = needs review).

## Status_Mapping
Raw_Code | Raw_Name | InverterMode_State | Solarize_Code | Notes
0 | INITIAL | INITIAL | 0
1 | STANDBY | STANDBY | 1
3 | ON_GRID | ON_GRID | 3
4 | OFF_GRID | ON_GRID | 3
5 | FAULT | FAULT | 5
9 | SHUTDOWN | SHUTDOWN | 9
NOTE: Edit "InverterMode_State" column: INITIAL/STANDBY/ON_GRID/FAULT/SHUTDOWN

## DER_AVM_Control
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x07D0 | 2000 | DER_POWER_FACTOR_SET | S16 | FC06 | 1 |  | 0.001 | RW | Power factor setpoint [-1000,-800],[800,1000]
0x07D1 | 2001 | DER_ACTION_MODE | U16 | FC06 | 1 |  | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
0x07D2 | 2002 | DER_REACTIVE_POWER_PCT | S16 | FC06 | 1 | % | 0.1 | RW | Reactive power % [-484,484]
0x07D3 | 2003 | DER_ACTIVE_POWER_PCT | U16 | FC06 | 1 | % | 0.1 | RW | Active power % [0,1100]
0x0834 | 2100 | INVERTER_ON_OFF | U16 | FC06 | 1 |  | 1 | RW | On/Off control: 0=ON, 1=OFF
0x0835 | 2101 | CLEAR_PV_INSULATION_WARNING | U16 | FC06 | 1 |  | 1 | WO | Clear PV insulation warning: 1=Clear
0x6001 | 24577 | INVERTER_CONTROL | U16 | FC06 | 1 |  | 1 | WO | Inverter control: 0=Power on, 1=Shut down
0x600D | 24589 | IV_CURVE_SCAN | U16 | FC06 | 1 |  | 1 | RW | IV curve scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
0x600F | 24591 | POWER_FACTOR_DYNAMIC | S16 | FC06 | 1 |  | 0.001 | RW | Dynamic power factor control
0x6010 | 24592 | REACTIVE_POWER_DYNAMIC | S16 | FC06 | 1 | % | 0.01 | RW | Dynamic reactive power control (%)
0x3005 | 12293 | POWER_DERATING_PCT | U16 | FC06 | 1 | % | 1 | RW | Active power derating [0-110]%
NOTE: DER-AVM control registers (always included). Do not modify addresses.

## DEA_AVM_Monitor
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x03E8 | 1000 | DEA_L1_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L1 current (low word)
0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 current (high word)
0x03EA | 1002 | DEA_L2_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L2 current (low word)
0x03EB | 1003 | DEA_L2_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 current (high word)
0x03EC | 1004 | DEA_L3_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L3 current (low word)
0x03ED | 1005 | DEA_L3_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 current (high word)
0x03EE | 1006 | DEA_L1_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L1 voltage (low word)
0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 voltage (high word)
0x03F0 | 1008 | DEA_L2_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L2 voltage (low word)
0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 voltage (high word)
0x03F2 | 1010 | DEA_L3_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L3 voltage (low word)
0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 voltage (high word)
0x03F4 | 1012 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | FC03 | 2 | kW | 0.1 | RO | DEA total active power (low word)
0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total active power (high word)
0x03F6 | 1014 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | FC03 | 2 | Var | 1 | RO | DEA total reactive power (low word)
0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total reactive power (high word)
0x03F8 | 1016 | DEA_POWER_FACTOR_LOW | S32 | FC03 | 2 |  | 0.001 | RO | DEA power factor (low word)
0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | S32 | FC03 | 1 |  |  | RO | DEA power factor (high word)
0x03FA | 1018 | DEA_FREQUENCY_LOW | S32 | FC03 | 2 | Hz | 0.1 | RO | DEA frequency (low word)
0x03FB | 1019 | DEA_FREQUENCY_HIGH | S32 | FC03 | 1 |  |  | RO | DEA frequency (high word)
0x03FC | 1020 | DEA_STATUS_FLAG_LOW | S32 | FC03 | 2 |  | 1 | RO | DEA status flag (low word)
0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | S32 | FC03 | 1 |  |  | RO | DEA status flag (high word)
NOTE: DEA-AVM monitoring registers (always included). Do not modify addresses.