## Register_Mapping
No | Section | Source_Addr_Hex | Source_Addr_Dec | Source_Name | Source_Type | Source_Unit | Source_Scale | Source_RW | Source_Regs | → | Solarize_Name | Solarize_Addr_Hex | Match_Type | Notes
--- Device Information (System Info) ---
1 | Device Information (System Info) | 0x7530 | 30000 | Model | string |  |  | RO | 15 | → | MODEL_CODE |  | Ref(67%)
2 | Device Information (System Info) | 0x753F | 30015 | SN | string |  |  | RO | 10 | → |  |  | Unmapped
3 | Device Information (System Info) | 0x7549 | 30025 | PN | string |  |  | RO | 10 | → |  |  | Unmapped
4 | Device Information (System Info) | 0x7553 | 30035 | Firmware Version | string |  |  | RO | 15 | → | FIRMWARE_VERSION |  | Ref(100%)
5 | Device Information (System Info) | 0x7562 | 30050 | Softwareversion | string |  |  | RO | 15 | → | FIRMWARE_VERSION |  | Ref(77%)
6 | Device Information (System Info) | 0x7574 | 30068 | Protocolversion [Modbus ] | U32 |  |  | RO | 2 | → | OPERATION_MODE |  | Ref(56%)
7 | Device Information (System Info) | 0x7576 | 30070 | Model ID | U16 |  |  | RO | 1 | → | MODEL_CODE |  | Ref(78%)
8 | Device Information (System Info) | 0x7577 | 30071 | Numberof PV strings | U16 |  |  | RO | 1 | → | PV_STRING_BASE |  | Ref(61%)
9 | Device Information (System Info) | 0x7578 | 30072 | Numberof MPP Ts | U16 |  |  | RO | 1 | → |  |  | Unmapped
10 | Device Information (System Info) | 0x7579 | 30073 | Ratedpower | U32 | kW |  | RO | 2 | → | REACTIVE_POWER |  | Ref(75%)
11 | Device Information (System Info) | 0x757B | 30075 | Maximumactivepower (Pmax) | U32 | kW |  | RO | 2 | → | ACTIVE_POWER_PCT |  | Ref(67%)
12 | Device Information (System Info) | 0x757D | 30077 | Maximumapparent (Smax) | U32 | kVA |  | RO | 2 | → |  |  | Unmapped
13 | Device Information (System Info) | 0x757F | 30079 | Real - timemaximumreactivepower (Qmax, fedtothepowergrid) | S32 | kVar |  | RO | 2 | → |  |  | Unmapped
14 | Device Information (System Info) | 0x7581 | 30081 | Real - timemaximumreactivepower (- Qmax, absorbedfromthepowergrid) | S32 | kVar |  | RO | 2 | → |  |  | Unmapped
15 | Device Information (System Info) | 0x7583 | 30083 | Maximumactivepower (Pmaxr _ eal) | U32 | kW |  | RO | 2 | → | ACTIVE_POWER_PCT |  | Ref(59%)
16 | Device Information (System Info) | 0x7585 | 30085 | Maximumapparentcapability (Smaxr _ eal) | U32 | kVA |  | RO | 2 | → |  |  | Unmapped
17 | Device Information (System Info) | 0x7599 | 30105 | Productsalesarea | string |  |  | RO | 2 | → |  |  | Unmapped
18 | Device Information (System Info) | 0x759B | 30107 | Productsoftware ID | U16 |  |  | RO | 1 | → |  |  | Unmapped
19 | Device Information (System Info) | 0x759C | 30108 | Product Software Version Number | U16 |  |  | RO | 1 | → | MASTER_FIRMWARE_VERSION |  | Ref(56%)
20 | Device Information (System Info) | 0x759D | 30109 | Power Grid Standard Code Protocol Version | U16 |  |  | RO | 1 | → |  |  | Unmapped
21 | Device Information (System Info) | 0x759E | 30110 | Unique ID ofthesoftware . | U16 |  |  | RO | 1 | → |  |  | Unmapped
22 | Device Information (System Info) | 0x759F | 30111 | Numberofupgradepackages | U16 |  |  | RO | 1 | → |  |  | Unmapped
23 | Device Information (System Info) | 0x75A0 | 30112 | Informationaboutsubpackage 1 | U32 |  |  | RO | 2 | → |  |  | Unmapped
24 | Device Information (System Info) | 0x75A2 | 30114 | Subpackage 2 information | U32 |  |  | RO | 2 | → |  |  | Unmapped
25 | Device Information (System Info) | 0x75A4 | 30116 | Informationaboutsubpackage 3 | U32 |  |  | RO | 2 | → |  |  | Unmapped
26 | Device Information (System Info) | 0x75A6 | 30118 | Subpackage 4 information | U32 |  |  | RO | 2 | → |  |  | Unmapped
27 | Device Information (System Info) | 0x75A8 | 30120 | Subpackage 5 information | U32 |  |  | RO | 2 | → |  |  | Unmapped
28 | Device Information (System Info) | 0x75AA | 30122 | Informationaboutsubpackage 6 | U32 |  |  | RO | 2 | → |  |  | Unmapped
29 | Device Information (System Info) | 0x75AC | 30124 | Subpackage 7 information | U32 |  |  | RO | 2 | → |  |  | Unmapped
30 | Device Information (System Info) | 0x75AE | 30126 | Subpackage 8 information | U32 |  |  | RO | 2 | → |  |  | Unmapped
31 | Device Information (System Info) | 0x75B0 | 30128 | Subpackage 9 information | U32 |  |  | RO | 2 | → |  |  | Unmapped
32 | Device Information (System Info) | 0x75B2 | 30130 | Informationaboutsubpackage 10 | U32 |  |  | RO | 2 | → |  |  | Unmapped
33 | Device Information (System Info) | 0x75EF | 30191 | [Third- partylabeling] SN | string |  |  | RO | 10 | → |  |  | Unmapped
34 | Device Information (System Info) | 0x75F9 | 30201 | [Third- partylabel ] Manufacturermodel | U16 |  |  | RO | 1 | → |  |  | Unmapped
35 | Device Information (System Info) | 0x75FF | 30207 | Subdevice Support ID | U32 |  |  | RO | 2 | → | DEVICE_MODEL |  | Ref(56%)
36 | Device Information (System Info) | 0x7601 | 30209 | Subdevicepresenceflag. | U32 |  |  | RO | 2 | → |  |  | Unmapped
37 | Device Information (System Info) | 0x7724 | 30500 | Numberofuniquesouthboundsoftware IDs | U16 |  |  | RO | 1 | → |  |  | Unmapped
38 | Device Information (System Info) | 0x7725 | 30501 | Unique ID 1 ofthesouthboundsoftware . | U16 |  |  | RO | 1 | → |  |  | Unmapped
39 | Device Information (System Info) | 0x7726 | 30502 | Unique ID 2 ofthesouthboundsoftware | U16 |  |  | RO | 1 | → |  |  | Unmapped
40 | Device Information (System Info) | 0x772A | 30506 | Numberofupgradepackagesforsouthbounddevice 1 | U16 |  |  | RO | 1 | → |  |  | Unmapped
41 | Device Information (System Info) | 0x772B | 30507 | Informationaboutsubpackage 1 ofsouthbounddevice 1 | U32 |  |  | RO | 2 | → |  |  | Unmapped
42 | Device Information (System Info) | 0x772D | 30509 | Informationaboutsubpackage 2 ofsouthbounddevice 1 | U32 |  |  | RO | 2 | → |  |  | Unmapped
43 | Device Information (System Info) | 0x772F | 30511 | Informationaboutsubpackage 3 ofsouthbounddevice 1 | U32 |  |  | RO | 2 | → |  |  | Unmapped
44 | Device Information (System Info) | 0x7735 | 30517 | Numberofupgradepackagesforsouthbounddevice 2 | U16 |  |  | RO | 1 | → |  |  | Unmapped
45 | Device Information (System Info) | 0x7736 | 30518 | Informationaboutsubpackage 1 ofsouthbounddevice 2 | U32 |  |  | RO | 2 | → |  |  | Unmapped
46 | Device Information (System Info) | 0x7738 | 30520 | Informationaboutsubpackage 2 ofsouthbounddevice 2 | U32 |  |  | RO | 2 | → |  |  | Unmapped
47 | Device Information (System Info) | 0x773A | 30522 | Informationaboutsubpackage 3 ofsouthbounddevice 2 | U32 |  |  | RO | 2 | → |  |  | Unmapped
48 | Device Information (System Info) | 0x773C | 30524 | Informationaboutsubpackage 4 ofsouthbounddevice 2 | U32 |  |  | RO | 2 | → |  |  | Unmapped
49 | Device Information (System Info) | 0x7761 | 30561 | Ofefringnameofsouthbounddevice 1 | string |  |  | RO | 15 | → |  |  | Unmapped
50 | Device Information (System Info) | 0x7770 | 30576 | Offeringnameofsouthbounddevice 2 | string |  |  | RO | 15 | → |  |  | Unmapped
51 | Device Information (System Info) | 0x777F | 30591 | Ofefringnameofsouthbounddevice 3. | string |  |  | RO | 15 | → |  |  | Unmapped
52 | Device Information (System Info) | 0x7918 | 31000 | Hardwareversion | string |  |  | RO | 15 | → | FIRMWARE_VERSION |  | Ref(77%)
53 | Device Information (System Info) | 0x7927 | 31015 | Monitoring Board SN | string |  |  | RO | 10 | → |  |  | Unmapped
54 | Device Information (System Info) | 0x7931 | 31025 | Monitoringsoftwareversion | string |  |  | RO | 15 | → | EMS_FIRMWARE_VERSION |  | Ref(62%)
55 | Device Information (System Info) | 0x7940 | 31040 | Main DSP version | string |  |  | RO | 15 | → | DSP_VERSION |  | Ref(81%)
56 | Device Information (System Info) | 0x795E | 31070 | CPL D versionnumber | string |  |  | RO | 15 | → | DSP_VERSION |  | Ref(60%)
57 | Device Information (System Info) | 0x796D | 31085 | AFCI versionnumber | string |  |  | RO | 15 | → | ARM_VERSION |  | Ref(62%)
58 | Device Information (System Info) | 0x798B | 31115 | DC- MBU S versionnumber | string |  |  | RO | 15 | → | DSP_VERSION |  | Ref(61%)
59 | Device Information (System Info) | 0x79E0 | 31200 | Registrationcode | string |  |  | RO | 10 | → | OPERATION_MODE |  | Ref(67%)
--- Inverter Realtime Data ---
60 | Inverter Realtime Data | 0x7D00 | 32000 | [Remotecommunication] Single- noderemotecommunication | U16 |  |  | RO | 1 | → |  |  | Unmapped
61 | Inverter Realtime Data | 0x7D02 | 32002 | [Remotesignal] Runningstatus (monitoring) | U16 |  |  | RO | 1 | → |  |  | Unmapped
62 | Inverter Realtime Data | 0x7D03 | 32003 | [Remotesignal] Runningstatus (powerprocessing) | U32 |  |  | RO | 2 | → |  |  | Unmapped
63 | Inverter Realtime Data | 0x7D08 | 32008 | [Remotesignal] Alarm 1 | U16 |  |  | RO | 1 | → |  |  | Unmapped
64 | Inverter Realtime Data | 0x7D09 | 32009 | [Remotesignal] Alarm 2 | U16 |  |  | RO | 1 | → |  |  | Unmapped
65 | Inverter Realtime Data | 0x7D0A | 32010 | [Remotesignal] Alarm 3 | U16 |  |  | RO | 1 | → |  |  | Unmapped
66 | Inverter Realtime Data | 0x7D0B | 32011 | [Remotesignal] Alarm 4 | U16 |  |  | RO | 1 | → |  |  | Unmapped
67 | Inverter Realtime Data | 0x7D0C | 32012 | [Remotesignal] Alarm 5 | U16 |  |  | RO | 1 | → |  |  | Unmapped
68 | Inverter Realtime Data | 0x7D0D | 32013 | [Remotesignal] Alarm 6 | U16 |  |  | RO | 1 | → |  |  | Unmapped
69 | Inverter Realtime Data | 0x7D0F | 32015 | Device SN featurecode | U16 |  |  | RO | 1 | → | DEVICE_MODEL |  | Ref(61%)
70 | Inverter Realtime Data | 0x7D10 | 32016 | PV1 voltage | S16 | V |  | RO | 1 | → | PV1_VOLTAGE |  | Ref(100%)
71 | Inverter Realtime Data | 0x7D11 | 32017 | PV1 current | S16 | A |  | RO | 1 | → | PV1_CURRENT |  | Ref(100%)
72 | Inverter Realtime Data | 0x7D12 | 32018 | PV2 Voltage | S16 | V |  | RO | 1 | → | PV2_VOLTAGE |  | Ref(100%)
73 | Inverter Realtime Data | 0x7D13 | 32019 | PV2 current | S16 | A |  | RO | 1 | → | PV2_CURRENT |  | Ref(100%)
74 | Inverter Realtime Data | 0x7D14 | 32020 | PV3 Voltage | S16 | V |  | RO | 1 | → | PV3_VOLTAGE |  | Ref(100%)
75 | Inverter Realtime Data | 0x7D15 | 32021 | PV3 current | S16 | A |  | RO | 1 | → | PV3_CURRENT |  | Ref(100%)
76 | Inverter Realtime Data | 0x7D16 | 32022 | PV4 Voltage | S16 | V |  | RO | 1 | → | PV4_VOLTAGE |  | Ref(100%)
77 | Inverter Realtime Data | 0x7D17 | 32023 | PV4 current | S16 | A |  | RO | 1 | → | PV4_CURRENT |  | Ref(100%)
78 | Inverter Realtime Data | 0x7D18 | 32024 | PV5 voltage | S16 | V |  | RO | 1 | → | PV5_VOLTAGE |  | Ref(100%)
79 | Inverter Realtime Data | 0x7D19 | 32025 | PV5 current | S16 | A |  | RO | 1 | → | PV5_CURRENT |  | Ref(100%)
80 | Inverter Realtime Data | 0x7D1A | 32026 | PV6 voltage | S16 | V |  | RO | 1 | → | PV6_VOLTAGE |  | Ref(100%)
81 | Inverter Realtime Data | 0x7D1B | 32027 | PV6 current | S16 | A |  | RO | 1 | → | PV6_CURRENT |  | Ref(100%)
82 | Inverter Realtime Data | 0x7D1C | 32028 | PV7 Voltage | S16 | V |  | RO | 1 | → | PV7_VOLTAGE |  | Ref(100%)
83 | Inverter Realtime Data | 0x7D1D | 32029 | PV7 current | S16 | A |  | RO | 1 | → | PV7_CURRENT |  | Ref(100%)
84 | Inverter Realtime Data | 0x7D1E | 32030 | PV8 Voltage | S16 | V |  | RO | 1 | → | PV8_VOLTAGE |  | Ref(100%)
85 | Inverter Realtime Data | 0x7D1F | 32031 | PV8 current | S16 | A |  | RO | 1 | → | PV8_CURRENT |  | Ref(100%)
86 | Inverter Realtime Data | 0x7D40 | 32064 | DC power | S32 | kW |  | RO | 2 | → | AC_POWER |  | Ref(88%)
87 | Inverter Realtime Data | 0x7D42 | 32066 | Powergridline A and B voltage | U16 | V |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(60%)
88 | Inverter Realtime Data | 0x7D43 | 32067 | Powergrid B/C linevoltage | U16 | V |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(67%)
89 | Inverter Realtime Data | 0x7D44 | 32068 | Powergrid CA linevoltage | U16 | V |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(68%)
90 | Inverter Realtime Data | 0x7D45 | 32069 | Powergridphase A voltage | U16 | V |  | RO | 1 | → | PHASE_A_VOLTAGE |  | Ref(77%)
91 | Inverter Realtime Data | 0x7D46 | 32070 | Powergridphase B voltage | U16 | V |  | RO | 1 | → | PHASE_B_VOLTAGE |  | Ref(77%)
92 | Inverter Realtime Data | 0x7D47 | 32071 | Powergridphase C voltage | U16 | V |  | RO | 1 | → | PHASE_C_VOLTAGE |  | Ref(77%)
93 | Inverter Realtime Data | 0x7D48 | 32072 | Powergridphase A current | S32 | A |  | RO | 2 | → | PHASE_A_CURRENT |  | Ref(77%)
94 | Inverter Realtime Data | 0x7D4A | 32074 | Powergridphase B current | S32 | A |  | RO | 2 | → | PHASE_B_CURRENT |  | Ref(77%)
95 | Inverter Realtime Data | 0x7D4C | 32076 | Powergridphase C current | S32 | A |  | RO | 2 | → | PHASE_C_CURRENT |  | Ref(77%)
96 | Inverter Realtime Data | 0x7D4E | 32078 | Peakactivepowerofthecurrentday | S32 | kW |  | RO | 2 | → |  |  | Unmapped
97 | Inverter Realtime Data | 0x7D50 | 32080 | Activepower | S32 | kW |  | RO | 2 | → | ACTIVE_POWER |  | Ref(96%)
98 | Inverter Realtime Data | 0x7D52 | 32082 | reactivepower | S32 | kVar |  | RO | 2 | → | REACTIVE_POWER |  | Ref(96%)
99 | Inverter Realtime Data | 0x7D54 | 32084 | Powerfactor | S16 |  |  | RO | 1 | → | POWER_FACTOR |  | Ref(96%)
100 | Inverter Realtime Data | 0x7D55 | 32085 | Gridfrequency | U16 | Hz |  | RO | 1 | → | GRID_FREQUENCY |  | Ref(96%)
101 | Inverter Realtime Data | 0x7D56 | 32086 | Inverterefficiency | U16 | % |  | RO | 1 | → | INVERTER_ON_OFF |  | Ref(61%)
102 | Inverter Realtime Data | 0x7D57 | 32087 | Internaltemperature | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(75%)
103 | Inverter Realtime Data | 0x7D58 | 32088 | Insulationimpedance | U16 | MΩ |  | RO | 1 | → |  |  | Unmapped
104 | Inverter Realtime Data | 0x7D59 | 32089 | Device Status | U16 |  |  | RO | 1 | → | DEVICE_TYPE |  | Ref(67%)
105 | Inverter Realtime Data | 0x7D5A | 32090 | Fault Code | U16 |  |  | RO | 1 | → | FAULT_CODE_1 |  | Ref(91%)
106 | Inverter Realtime Data | 0x7D5B | 32091 | Start -uptime | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
107 | Inverter Realtime Data | 0x7D5D | 32093 | Shutdowntime | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
108 | Inverter Realtime Data | 0x7D5F | 32095 | Activepower [fast ] | S32 | kW |  | RO | 2 | → | REACTIVE_POWER_SET |  | Ref(82%)
109 | Inverter Realtime Data | 0x7D6A | 32106 | Accumulatedpowergeneration | U32 | kWh |  | RO | 2 | → | ACCUMULATED_ENERGY |  | Ref(68%)
110 | Inverter Realtime Data | 0x7D6C | 32108 | Total DC Input Power | U32 | kWh |  | RO | 2 | → | PV_TOTAL_INPUT_POWER_LOW |  | Ref(77%)
111 | Inverter Realtime Data | 0x7D6E | 32110 | Statisticaltimeofthecurrentenergyyield . | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
112 | Inverter Realtime Data | 0x7D70 | 32112 | Current Hour Electricity | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
113 | Inverter Realtime Data | 0x7D72 | 32114 | Current- daypowergeneration | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
114 | Inverter Realtime Data | 0x7D74 | 32116 | Electricitygeneratedinthecurrentmonth | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
115 | Inverter Realtime Data | 0x7D76 | 32118 | Electricitygeneratedinthecurrentyear | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
116 | Inverter Realtime Data | 0x7D97 | 32151 | Numberofcriticalalarms | U16 |  |  | RO | 1 | → |  |  | Unmapped
117 | Inverter Realtime Data | 0x7D98 | 32152 | Numberofmajoralarms | U16 |  |  | RO | 1 | → |  |  | Unmapped
118 | Inverter Realtime Data | 0x7D99 | 32153 | Numberof Minor Alarms | U16 |  |  | RO | 1 | → |  |  | Unmapped
119 | Inverter Realtime Data | 0x7D9A | 32154 | Numberof Warning Alarms | U16 |  |  | RO | 1 | → |  |  | Unmapped
120 | Inverter Realtime Data | 0x7D9B | 32155 | Alarmclearance SN | U16 |  |  | RO | 1 | → |  |  | Unmapped
121 | Inverter Realtime Data | 0x7D9C | 32156 | Last Hour Power Statistics Time | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
122 | Inverter Realtime Data | 0x7D9E | 32158 | Electricitygeneratedintheprevioushour | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
123 | Inverter Realtime Data | 0x7DA0 | 32160 | Electricitystatisticstimeofthepreviousday | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
124 | Inverter Realtime Data | 0x7DA2 | 32162 | Electricitygeneratedinthepreviousday | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
125 | Inverter Realtime Data | 0x7DA4 | 32164 | Statisticaltimeofthepreviousmonth. | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
126 | Inverter Realtime Data | 0x7DA6 | 32166 | Electricitygeneratedinthepreviousmonth | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
127 | Inverter Realtime Data | 0x7DA8 | 32168 | Electricitystatisticstimeofthepreviousyear | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
128 | Inverter Realtime Data | 0x7DAA | 32170 | Electricitygeneratedinthepreviousyear | U32 | kWh |  | RO | 2 | → |  |  | Unmapped
129 | Inverter Realtime Data | 0x7DAC | 32172 | Serialnumberofthelatestactivealarm. | U32 |  |  | RO | 2 | → |  |  | Unmapped
130 | Inverter Realtime Data | 0x7DAE | 32174 | Latest Historical Alarm Serial Number | U32 |  |  | RO | 2 | → |  |  | Unmapped
131 | Inverter Realtime Data | 0x7DB0 | 32176 | Totalbusvoltage | S16 | V |  | RO | 1 | → | BUS_VOLTAGE |  | Ref(77%)
132 | Inverter Realtime Data | 0x7DB1 | 32177 | Maximum PV voltage | S16 | V |  | RO | 1 | → | PV_VOLTAGE |  | Ref(71%)
133 | Inverter Realtime Data | 0x7DB2 | 32178 | Minimum PV voltage | S16 | V |  | RO | 1 | → | PV_VOLTAGE |  | Ref(71%)
134 | Inverter Realtime Data | 0x7DB3 | 32179 | Average PV negative- to- groundvoltage | S16 | V |  | RO | 1 | → |  |  | Unmapped
135 | Inverter Realtime Data | 0x7DB4 | 32180 | Maximum PV positive- to- groundvoltage | S16 | V |  | RO | 1 | → |  |  | Unmapped
136 | Inverter Realtime Data | 0x7DB5 | 32181 | Minimum PV negative- to- groundvoltage | S16 | V |  | RO | 1 | → |  |  | Unmapped
137 | Inverter Realtime Data | 0x7DB6 | 32182 | Inverter- to- PE withstandvoltage | U16 | V |  | RO | 1 | → | INV_T_VOLTAGE |  | Ref(59%)
138 | Inverter Realtime Data | 0x7DB7 | 32183 | ISO featureinformation | U16 |  |  | RO | 1 | → |  |  | Unmapped
139 | Inverter Realtime Data | 0x7DBE | 32190 | Built -in PID runningstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(65%)
140 | Inverter Realtime Data | 0x7DBF | 32191 | PV negative- to- groundvoltage | S16 | V |  | RO | 1 | → | GRID_T_VOLTAGE |  | Ref(57%)
141 | Inverter Realtime Data | 0x7DC0 | 32192 | Directionofthebuilt -in PID compensation | U16 |  |  | RO | 1 | → |  |  | Unmapped
142 | Inverter Realtime Data | 0x7DD4 | 32212 | Total DC energyyieldof MPP T1 | U32 | kWh |  | RO | 2 | → | TOTAL_ENERGY_LOW |  | Ref(62%)
143 | Inverter Realtime Data | 0x7DD6 | 32214 | Total DC energyyieldof MPP T2 | U32 | kWh |  | RO | 2 | → | TOTAL_ENERGY_LOW |  | Ref(62%)
144 | Inverter Realtime Data | 0x7DD8 | 32216 | MPP T3 DC Total Energy Yield | U32 | kWh |  | RO | 2 | → | TOTAL_ENERGY_L |  | Ref(67%)
145 | Inverter Realtime Data | 0x7DDA | 32218 | MPP T4 DC Accumulated Energy Yield | U32 | kWh |  | RO | 2 | → | ACCUMULATED_ENERGY |  | Ref(69%)
146 | Inverter Realtime Data | 0x7DFC | 32252 | Monitoringalarm 1 | U16 |  |  | RO | 1 | → |  |  | Unmapped
147 | Inverter Realtime Data | 0x7DFD | 32253 | Monitoringalarm 2 | U16 |  |  | RO | 1 | → |  |  | Unmapped
148 | Inverter Realtime Data | 0x7DFE | 32254 | Monitoralarm 3 | U16 |  |  | RO | 1 | → |  |  | Unmapped
149 | Inverter Realtime Data | 0x7DFF | 32255 | [External] Poweralarm 1 | U16 |  |  | RO | 1 | → |  |  | Unmapped
150 | Inverter Realtime Data | 0x7E00 | 32256 | [External] Poweralarm 2 | U16 |  |  | RO | 1 | → |  |  | Unmapped
151 | Inverter Realtime Data | 0x7E01 | 32257 | [External] Poweralarm 3 | U16 |  |  | RO | 1 | → |  |  | Unmapped
152 | Inverter Realtime Data | 0x7E02 | 32258 | [External] Poweralarm 4 | U16 |  |  | RO | 1 | → |  |  | Unmapped
153 | Inverter Realtime Data | 0x7E03 | 32259 | [External] Poweralarm 5 | U16 |  |  | RO | 1 | → |  |  | Unmapped
154 | Inverter Realtime Data | 0x7E04 | 32260 | [External] Poweralarm 6 | U16 |  |  | RO | 1 | → |  |  | Unmapped
155 | Inverter Realtime Data | 0x7E05 | 32261 | [External] Poweralarm 7 | U16 |  |  | RO | 1 | → |  |  | Unmapped
156 | Inverter Realtime Data | 0x7E06 | 32262 | [External] Poweralarm 8 | U16 |  |  | RO | 1 | → |  |  | Unmapped
157 | Inverter Realtime Data | 0x7E07 | 32263 | [External] Poweralarm 9 | U16 |  |  | RO | 1 | → |  |  | Unmapped
158 | Inverter Realtime Data | 0x7E08 | 32264 | [External] Poweralarm 10 | U16 |  |  | RO | 1 | → |  |  | Unmapped
159 | Inverter Realtime Data | 0x7E09 | 32265 | [External] Poweralarm 11 | U16 |  |  | RO | 1 | → |  |  | Unmapped
160 | Inverter Realtime Data | 0x7E0A | 32266 | [External] Poweralarm 12 | U16 |  |  | RO | 1 | → |  |  | Unmapped
161 | Inverter Realtime Data | 0x7E0B | 32267 | [External] Poweralarm 13 | U16 |  |  | RO | 1 | → |  |  | Unmapped
162 | Inverter Realtime Data | 0x7E0C | 32268 | [External] Poweralarm 14 | U16 |  |  | RO | 1 | → |  |  | Unmapped
163 | Inverter Realtime Data | 0x7E0D | 32269 | [External] Poweralarm 15 | U16 |  |  | RO | 1 | → |  |  | Unmapped
164 | Inverter Realtime Data | 0x7E0E | 32270 | [External] Poweralarm 16 | U16 |  |  | RO | 1 | → |  |  | Unmapped
165 | Inverter Realtime Data | 0x7E0F | 32271 | Monitoralarm 4 | U16 |  |  | RO | 1 | → |  |  | Unmapped
166 | Inverter Realtime Data | 0x7E10 | 32272 | Monitoralarm 5 | U16 |  |  | RO | 1 | → |  |  | Unmapped
167 | Inverter Realtime Data | 0x7E11 | 32273 | [External] Poweralarm 17 | U16 |  |  | RO | 1 | → |  |  | Unmapped
168 | Inverter Realtime Data | 0x7E2C | 32300 | String 1 accessstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(63%)
169 | Inverter Realtime Data | 0x7E2D | 32301 | String 2 accessstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(63%)
170 | Inverter Realtime Data | 0x7E2E | 32302 | String 3 accessstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(63%)
171 | Inverter Realtime Data | 0x7E2F | 32303 | String 4 accessstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(63%)
172 | Inverter Realtime Data | 0x7E30 | 32304 | String 5 accessstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(63%)
173 | Inverter Realtime Data | 0x7E31 | 32305 | Connectionstatusofstring 6 | U16 |  |  | RO | 1 | → |  |  | Unmapped
174 | Inverter Realtime Data | 0x7E32 | 32306 | String 7 accessstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(63%)
175 | Inverter Realtime Data | 0x7E33 | 32307 | String 8 accessstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(63%)
176 | Inverter Realtime Data | 0x84D0 | 34000 | Stent System Status | U32 |  |  | RO | 2 | → | SYSTEM_STATUS |  | Ref(81%)
177 | Inverter Realtime Data | 0x84D2 | 34002 | Tiltangle 1 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
178 | Inverter Realtime Data | 0x84D3 | 34003 | Azimuth 1 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
179 | Inverter Realtime Data | 0x84D4 | 34004 | Tiltangle 2 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
180 | Inverter Realtime Data | 0x84D5 | 34005 | Azimuth 2 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
181 | Inverter Realtime Data | 0x84D6 | 34006 | Tiltangle 3 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
182 | Inverter Realtime Data | 0x84D7 | 34007 | Azimuth 3 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
183 | Inverter Realtime Data | 0x84D8 | 34008 | Tiltangle 4 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
184 | Inverter Realtime Data | 0x84D9 | 34009 | Azimuth 4 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
185 | Inverter Realtime Data | 0x84DA | 34010 | Tiltangle 5 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
186 | Inverter Realtime Data | 0x84DB | 34011 | Azimuth 5 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
187 | Inverter Realtime Data | 0x84DC | 34012 | Tiltangle 6 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
188 | Inverter Realtime Data | 0x84DD | 34013 | Azimuth 6 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
189 | Inverter Realtime Data | 0x84DE | 34014 | Tiltangle 7 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
190 | Inverter Realtime Data | 0x84DF | 34015 | Azimuth 7 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
191 | Inverter Realtime Data | 0x84E0 | 34016 | Tiltangle 8 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
192 | Inverter Realtime Data | 0x84E1 | 34017 | Azimuth 8 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
193 | Inverter Realtime Data | 0x84E2 | 34018 | Tiltangle 9 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
194 | Inverter Realtime Data | 0x84E3 | 34019 | Azimuth 9 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
195 | Inverter Realtime Data | 0x84E4 | 34020 | Tiltangle 10 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
196 | Inverter Realtime Data | 0x84E5 | 34021 | Azimuth 10 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
197 | Inverter Realtime Data | 0x84E6 | 34022 | Tiltangle 11 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
198 | Inverter Realtime Data | 0x84E7 | 34023 | Azimuth 11 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
199 | Inverter Realtime Data | 0x84E8 | 34024 | Tiltangle 12 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
200 | Inverter Realtime Data | 0x84E9 | 34025 | Azimuth 12 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
201 | Inverter Realtime Data | 0x84EA | 34026 | Tiltangle 13 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
202 | Inverter Realtime Data | 0x84EB | 34027 | Bearing 13 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
203 | Inverter Realtime Data | 0x84EC | 34028 | Tiltangle 14 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
204 | Inverter Realtime Data | 0x84ED | 34029 | Azimuth 14 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
205 | Inverter Realtime Data | 0x84EE | 34030 | Tiltangle 15 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
206 | Inverter Realtime Data | 0x84EF | 34031 | Bearingangle 15 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
207 | Inverter Realtime Data | 0x84F0 | 34032 | Tiltangle 16 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
208 | Inverter Realtime Data | 0x84F1 | 34033 | Bearing 16 sampling | S16 | ° |  | RO | 1 | → |  |  | Unmapped
209 | Inverter Realtime Data | 0x84F2 | 34034 | Trackingsystemcontroller | U16 |  |  | RO | 1 | → | INVERTER_CONTROL |  | Ref(55%)
210 | Inverter Realtime Data | 0x84F3 | 34035 | Support System Type | U16 |  |  | RO | 1 | → |  |  | Unmapped
211 | Inverter Realtime Data | 0x84F4 | 34036 | Operatingmode | U16 |  |  | RO | 1 | → | OPERATION_MODE |  | Ref(89%)
212 | Inverter Realtime Data | 0x84F5 | 34037 | Totalnumberofstents | U16 |  |  | RO | 1 | → |  |  | Unmapped
213 | Inverter Realtime Data | 0x84F6 | 34038 | Supportaccessstatus | U32 |  |  | RO | 2 | → | SYSTEM_STATUS |  | Ref(56%)
214 | Inverter Realtime Data | 0x84F8 | 34040 | Workingmodemask | U32 |  |  | RO | 2 | → | WORKING_MODE |  | Ref(81%)
215 | Inverter Realtime Data | 0x851B | 34075 | Support 1 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
216 | Inverter Realtime Data | 0x851C | 34076 | Support 1 user- definedfaultstatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
217 | Inverter Realtime Data | 0x851D | 34077 | Support 2 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
218 | Inverter Realtime Data | 0x851E | 34078 | Support 2 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
219 | Inverter Realtime Data | 0x851F | 34079 | Support 3 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
220 | Inverter Realtime Data | 0x8520 | 34080 | Support 3 user- definedfaultstatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
221 | Inverter Realtime Data | 0x8521 | 34081 | Support 4 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
222 | Inverter Realtime Data | 0x8522 | 34082 | Support 4 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
223 | Inverter Realtime Data | 0x8523 | 34083 | Support 5 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
224 | Inverter Realtime Data | 0x8524 | 34084 | Support 5 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
225 | Inverter Realtime Data | 0x8525 | 34085 | Support 6 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
226 | Inverter Realtime Data | 0x8526 | 34086 | Support 6 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
227 | Inverter Realtime Data | 0x8527 | 34087 | Support 7 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
228 | Inverter Realtime Data | 0x8528 | 34088 | Support 7 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
229 | Inverter Realtime Data | 0x8529 | 34089 | Support 8 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
230 | Inverter Realtime Data | 0x852A | 34090 | Support 8 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
231 | Inverter Realtime Data | 0x852B | 34091 | Support 9 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
232 | Inverter Realtime Data | 0x852C | 34092 | Support 9 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
233 | Inverter Realtime Data | 0x852D | 34093 | Support 10 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
234 | Inverter Realtime Data | 0x852E | 34094 | Support 10 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
235 | Inverter Realtime Data | 0x852F | 34095 | Support 11 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
236 | Inverter Realtime Data | 0x8530 | 34096 | Support 11 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
237 | Inverter Realtime Data | 0x8531 | 34097 | Support 12 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
238 | Inverter Realtime Data | 0x8532 | 34098 | Support 12 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
239 | Inverter Realtime Data | 0x8533 | 34099 | Support 13 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
240 | Inverter Realtime Data | 0x8534 | 34100 | Support 13 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
241 | Inverter Realtime Data | 0x8535 | 34101 | Support 14 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
242 | Inverter Realtime Data | 0x8536 | 34102 | Support 14 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
243 | Inverter Realtime Data | 0x8537 | 34103 | Support 15 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
244 | Inverter Realtime Data | 0x8538 | 34104 | Support 15 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
245 | Inverter Realtime Data | 0x8539 | 34105 | Support 16 General Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
246 | Inverter Realtime Data | 0x853A | 34106 | Support 16 Custom Fault Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
247 | Inverter Realtime Data | 0x88B8 | 35000 | Runningtimeofcapacitorbank | U32 | hour |  | RO | 2 | → |  |  | Unmapped
248 | Inverter Realtime Data | 0x88BA | 35002 | Internalfan 1 runningtime | U32 | hour |  | RO | 2 | → | INTERNAL_TEMP |  | Ref(58%)
249 | Inverter Realtime Data | 0x88C2 | 35010 | Internalalarm | U16 | V |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(69%)
250 | Inverter Realtime Data | 0x88CD | 35021 | Internal Temperature 1 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(74%)
251 | Inverter Realtime Data | 0x88CE | 35022 | Internal Temperature 2 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(74%)
252 | Inverter Realtime Data | 0x88CF | 35023 | Internal Temperature 3 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(74%)
253 | Inverter Realtime Data | 0x88D0 | 35024 | Internal Temperature 4 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(74%)
254 | Inverter Realtime Data | 0x88D1 | 35025 | Internal Temperature 5 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(74%)
255 | Inverter Realtime Data | 0x88D2 | 35026 | Internal Temperature 6 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(74%)
256 | Inverter Realtime Data | 0x88D3 | 35027 | Internaltemperature 7 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(71%)
257 | Inverter Realtime Data | 0x88D4 | 35028 | Internaltemperature 8 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(71%)
258 | Inverter Realtime Data | 0x88D5 | 35029 | Internaltemperature 9 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(71%)
259 | Inverter Realtime Data | 0x88D6 | 35030 | Internaltemperature 10 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(69%)
260 | Inverter Realtime Data | 0x88D7 | 35031 | Internaltemperature 11 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(69%)
261 | Inverter Realtime Data | 0x88D8 | 35032 | Internaltemperature 12 | S16 | °C |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(69%)
262 | Inverter Realtime Data | 0x88DE | 35038 | Phase A DC component DCI | S16 | A |  | RO | 1 | → | PHASE_A_CURRENT |  | Ref(62%)
263 | Inverter Realtime Data | 0x88DF | 35039 | Phase B DC component DCI | S16 | A |  | RO | 1 | → | PHASE_B_CURRENT |  | Ref(62%)
264 | Inverter Realtime Data | 0x88E0 | 35040 | Phase C DC component DCI | S16 | A |  | RO | 1 | → | PHASE_C_CURRENT |  | Ref(62%)
265 | Inverter Realtime Data | 0x88E1 | 35041 | Leakagecurrent RCD | S16 | mA |  | RO | 1 | → | L1_CURRENT |  | Ref(57%)
266 | Inverter Realtime Data | 0x88E2 | 35042 | Positivebusvoltage | S16 | V |  | RO | 1 | → | BUS_VOLTAGE |  | Ref(69%)
267 | Inverter Realtime Data | 0x88E3 | 35043 | Negativebusvoltage | S16 | V |  | RO | 1 | → | BUS_VOLTAGE |  | Ref(69%)
268 | Inverter Realtime Data | 0x88E4 | 35044 | BUS negativevoltagetoground | S16 | V |  | RO | 1 | → | BUS_VOLTAGE |  | Ref(58%)
269 | Inverter Realtime Data | 0x8916 | 35094 | I-V scanstatus | U16 |  |  | RO | 1 | → | IV_SCAN_STATUS |  | Ref(93%)
270 | Inverter Realtime Data | 0x8917 | 35095 | I-V scanningcapability | U16 |  |  | RO | 1 | → |  |  | Unmapped
271 | Inverter Realtime Data | 0x891E | 35102 | [Management System] NMS IP address | U32 |  |  | RO | 2 | → |  |  | Unmapped
272 | Inverter Realtime Data | 0x8920 | 35104 | [STA ] Wireless Routing Access Signal Strength | U16 |  |  | RO | 1 | → |  |  | Unmapped
273 | Inverter Realtime Data | 0x8921 | 35105 | [STA ] WLA N listscanningstatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
274 | Inverter Realtime Data | 0x8922 | 35106 | Wifi- Mac | string |  |  | RO | 3 | → |  |  | Unmapped
275 | Inverter Realtime Data | 0x8928 | 35112 | [NTP ] Last NTP synchronizationstatus. | U16 |  |  | RO | 1 | → |  |  | Unmapped
276 | Inverter Realtime Data | 0x8929 | 35113 | [NTP ] NTP Last Synchronization Time | U32 |  |  | RO | 2 | → |  |  | Unmapped
277 | Inverter Realtime Data | 0x892B | 35115 | Deferredactivationstate | U16 |  |  | RO | 1 | → |  |  | Unmapped
278 | Inverter Realtime Data | 0x892C | 35116 | [4G] Monthlyusedtraffic | U32 | MB |  | RO | 2 | → |  |  | Unmapped
279 | Inverter Realtime Data | 0x892E | 35118 | [4G] Monthly Remaining Traffic | U32 | MB |  | RO | 2 | → |  |  | Unmapped
280 | Inverter Realtime Data | 0x8930 | 35120 | [4G] Averagedailytrafficusage | U32 | MB |  | RO | 2 | → |  |  | Unmapped
281 | Inverter Realtime Data | 0x8932 | 35122 | [4G] Trafficstatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
282 | Inverter Realtime Data | 0x8934 | 35124 | [STA ] Routerconnectiontime | U16 | s |  | RO | 1 | → |  |  | Unmapped
283 | Inverter Realtime Data | 0x8935 | 35125 | [STA ] Routerconnectionstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(60%)
284 | Inverter Realtime Data | 0x8936 | 35126 | [FE] Connectionstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(61%)
285 | Inverter Realtime Data | 0x8940 | 35136 | [Smart I- V-V- Diagnosis ] Authorization Function | U32 |  |  | RO | 2 | → |  |  | Unmapped
286 | Inverter Realtime Data | 0x8942 | 35138 | Smart I- V-V- Diagnosis (License) Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
287 | Inverter Realtime Data | 0x8943 | 35139 | [Smart I- V-V- Diagnosis ] Licenseexpirationdate | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
288 | Inverter Realtime Data | 0x8945 | 35141 | Licenseloadingtime | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
289 | Inverter Realtime Data | 0x8947 | 35143 | License Deregistration Time | EpochSecond | s |  | RO | 2 | → | TOTAL_GENERATION_TIME_LOW |  | Ref(58%)
290 | Inverter Realtime Data | 0x8949 | 35145 | License SN | string |  |  | RO | 10 | → |  |  | Unmapped
291 | Inverter Realtime Data | 0x8953 | 35155 | Invalidationcode . | string |  |  | RO | 64 | → | ACTION_MODE |  | Ref(59%)
292 | Inverter Realtime Data | 0x8993 | 35219 | Authorization Feature Signature | U16 |  |  | RO | 2 | → |  |  | Unmapped
293 | Inverter Realtime Data | 0x8995 | 35221 | [Stringmonitoring] Licensestatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(59%)
294 | Inverter Realtime Data | 0x8996 | 35222 | [String Monitoring] License Expiration Time | EpochSecond | s |  | RO | 2 | → |  |  | Unmapped
295 | Inverter Realtime Data | 0x89B1 | 35249 | [4G] Modulestatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
296 | Inverter Realtime Data | 0x89B2 | 35250 | [4G] IP address | U32 |  |  | RO | 2 | → |  |  | Unmapped
297 | Inverter Realtime Data | 0x89B4 | 35252 | [4G] Subnet Mask | U32 |  |  | RO | 2 | → |  |  | Unmapped
298 | Inverter Realtime Data | 0x89B6 | 35254 | [4G] IMEI | string |  |  | RO | 10 | → |  |  | Unmapped
299 | Inverter Realtime Data | 0x89C0 | 35264 | [4G] signalstrength | U16 |  |  | RO | 1 | → |  |  | Unmapped
300 | Inverter Realtime Data | 0x89C1 | 35265 | [4G] PIN numberinputtimes | U16 |  |  | RO | 1 | → |  |  | Unmapped
301 | Inverter Realtime Data | 0x89C2 | 35266 | [4G] PIN checkstatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
302 | Inverter Realtime Data | 0x89E4 | 35300 | Activepoweradjustmentstatus | string |  |  | RO | 4 | → | REACTIVE_POWER_SET |  | Ref(58%)
303 | Inverter Realtime Data | 0x89E8 | 35304 | Reactivepoweradjustmentstatus | string |  |  | RO | 4 | → | REACTIVE_POWER_SET |  | Ref(64%)
304 | Inverter Realtime Data | 0x8CC1 | 36033 | Upgradestatus ID. | U16 |  |  | RO | 1 | → | DEA_STATUS_FLAG_HIGH |  | Ref(56%)
305 | Inverter Realtime Data | 0x9088 | 37000 | [Module 1] Runningstatusofthebattery | U16 |  |  | RO | 1 | → |  |  | Unmapped
306 | Inverter Realtime Data | 0x90EC | 37100 | Meter Status | U16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(81%)
307 | Inverter Realtime Data | 0x90ED | 37101 | Gridvoltage (phase A voltage) | S32 | V |  | RO | 2 | → | R_PHASE_VOLTAGE |  | Ref(71%)
308 | Inverter Realtime Data | 0x90EF | 37103 | Phase B voltage | S32 | V |  | RO | 2 | → | PHASE_B_VOLTAGE |  | Ref(100%)
309 | Inverter Realtime Data | 0x90F1 | 37105 | Phase C voltage | S32 | V |  | RO | 2 | → | PHASE_C_VOLTAGE |  | Ref(100%)
310 | Inverter Realtime Data | 0x90F3 | 37107 | Gridcurrent (phase A current) | S32 | A |  | RO | 2 | → | PHASE_A_CURRENT |  | Ref(71%)
311 | Inverter Realtime Data | 0x90F5 | 37109 | Phase B current | S32 | A |  | RO | 2 | → | PHASE_B_CURRENT |  | Ref(100%)
312 | Inverter Realtime Data | 0x90F7 | 37111 | Phase C current | S32 | A |  | RO | 2 | → | PHASE_C_CURRENT |  | Ref(100%)
313 | Inverter Realtime Data | 0x90F9 | 37113 | Activepower | S32 | W |  | RO | 2 | → | ACTIVE_POWER |  | Ref(96%)
314 | Inverter Realtime Data | 0x90FB | 37115 | reactivepower | S32 | Var |  | RO | 2 | → | REACTIVE_POWER |  | Ref(96%)
315 | Inverter Realtime Data | 0x90FD | 37117 | Powerfactor | S16 |  |  | RO | 1 | → | POWER_FACTOR |  | Ref(96%)
316 | Inverter Realtime Data | 0x90FE | 37118 | Gridfrequency | S16 | Hz |  | RO | 1 | → | GRID_FREQUENCY |  | Ref(96%)
317 | Inverter Realtime Data | 0x90FF | 37119 | Positiveactivepower | S32 | kWh |  | RO | 2 | → | REACTIVE_POWER |  | Ref(73%)
318 | Inverter Realtime Data | 0x9101 | 37121 | Reverseactivepower | S32 | kWh |  | RO | 2 | → | REACTIVE_POWER |  | Ref(81%)
319 | Inverter Realtime Data | 0x9103 | 37123 | Accumulatedreactivepower | S32 | kVarh |  | RO | 2 | → | REACTIVE_POWER |  | Ref(68%)
320 | Inverter Realtime Data | 0x9105 | 37125 | Meter Type | U16 |  |  | RO | 1 | → | DEVICE_TYPE |  | Ref(67%)
321 | Inverter Realtime Data | 0x9106 | 37126 | A-B linevoltage | S32 | V |  | RO | 2 | → | PHASE_B_VOLTAGE |  | Ref(73%)
322 | Inverter Realtime Data | 0x9108 | 37128 | BC linevoltage | S32 | V |  | RO | 2 | → | BUS_VOLTAGE |  | Ref(72%)
323 | Inverter Realtime Data | 0x910A | 37130 | CA linevoltage | S32 | V |  | RO | 2 | → | S_VOLTAGE |  | Ref(70%)
324 | Inverter Realtime Data | 0x910C | 37132 | Phase A activepower | S32 | W |  | RO | 2 | → | REACTIVE_POWER |  | Ref(73%)
325 | Inverter Realtime Data | 0x910E | 37134 | Phase B activepower | S32 | W |  | RO | 2 | → | REACTIVE_POWER |  | Ref(73%)
326 | Inverter Realtime Data | 0x9110 | 37136 | Phase C activepower | S32 | W |  | RO | 2 | → | REACTIVE_POWER |  | Ref(73%)
327 | Inverter Realtime Data | 0x9112 | 37138 | Meter Model Check Result | U16 |  |  | RO | 1 | → | METER_T_CURRENT |  | Ref(56%)
328 | Inverter Realtime Data | 0x9150 | 37200 | Totalnumberofoptimizers | U16 |  |  | RO | 1 | → |  |  | Unmapped
329 | Inverter Realtime Data | 0x9151 | 37201 | Numberofonlineoptimizers | U16 |  |  | RO | 1 | → |  |  | Unmapped
330 | Inverter Realtime Data | 0x9152 | 37202 | Featuredatasequencenumber | U16 |  |  | RO | 1 | → |  |  | Unmapped
331 | Inverter Realtime Data | 0x9153 | 37203 | Physical Location Locating Progress | U16 |  |  | RO | 1 | → |  |  | Unmapped
332 | Inverter Realtime Data | 0x9154 | 37204 | Logexportprogress | U16 |  |  | RO | 1 | → |  |  | Unmapped
333 | Inverter Realtime Data | 0x9155 | 37205 | Real - timedataqueryprogress | U16 |  |  | RO | 1 | → |  |  | Unmapped
334 | Inverter Realtime Data | 0x9156 | 37206 | Currentstatusofthephysicallocation | U16 |  |  | RO | 1 | → |  |  | Unmapped
335 | Inverter Realtime Data | 0x9157 | 37207 | Numberof Searched Optimizers | U16 |  |  | RO | 1 | → |  |  | Unmapped
336 | Inverter Realtime Data | 0x9158 | 37208 | Relative Positioning Status | U16 |  |  | RO | 1 | → | IV_SCAN_STATUS |  | Ref(59%)
337 | Inverter Realtime Data | 0x9159 | 37209 | Layout File Storage Progress | U16 | % |  | RO | 1 | → |  |  | Unmapped
338 | Inverter Realtime Data | 0x915A | 37210 | Layout File Change SN | U16 |  |  | RO | 1 | → |  |  | Unmapped
339 | Inverter Realtime Data | 0x915B | 37211 | Disconnectiondetectionprogress | U16 | % |  | RO | 1 | → |  |  | Unmapped
340 | Inverter Realtime Data | 0x915C | 37212 | Disconnectedstatus | U16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(67%)
341 | Inverter Realtime Data | 0x9182 | 37250 | [DC- MBU S] Networkingstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(56%)
342 | Inverter Realtime Data | 0x9183 | 37251 | Numberof Networked Networks | U16 |  |  | RO | 1 | → |  |  | Unmapped
343 | Inverter Realtime Data | 0x9184 | 37252 | Numberofneighboringnetworks | U16 |  |  | RO | 1 | → |  |  | Unmapped
344 | Inverter Realtime Data | 0x9185 | 37253 | Fast Shutdown Self Test Status | U16 |  |  | RO | 1 | → |  |  | Unmapped
345 | Inverter Realtime Data | 0x9186 | 37254 | Runningstatus | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(96%)
346 | Inverter Realtime Data | 0x9187 | 37255 | SN | string |  |  | RO | 10 | → |  |  | Unmapped
347 | Inverter Realtime Data | 0x9218 | 37400 | SN | string |  |  | RO | 10 | → |  |  | Unmapped
348 | Inverter Realtime Data | 0x9222 | 37410 | Type | U16 |  |  | RO | 1 | → |  |  | Unmapped
349 | Inverter Realtime Data | 0x9235 | 37429 | Maximumnumberofconnecteddevices | U16 |  |  | RO | 1 | → |  |  | Unmapped
350 | Inverter Realtime Data | 0x9236 | 37430 | RAT | string |  |  | RO | 10 | → |  |  | Unmapped
351 | Inverter Realtime Data | 0x9240 | 37440 | Carriers | string |  |  | RO | 15 | → |  |  | Unmapped
352 | Inverter Realtime Data | 0x925E | 37470 | Totalratedcapacityofgrid- tiedinverters | U32 | kW |  | RO | 2 | → |  |  | Unmapped
353 | Inverter Realtime Data | 0x9260 | 37472 | Conversionfactor | U32 |  |  | RO | 2 | → | POWER_FACTOR |  | Ref(64%)
354 | Inverter Realtime Data | 0x9262 | 37474 | Current Percentage | U16 | % |  | RO | 1 | → |  |  | Unmapped
355 | Inverter Realtime Data | 0x9263 | 37475 | [Scheduleserver] Communicationstatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
356 | Inverter Realtime Data | 0x9264 | 37476 | [Scheduleserver] Latestconnectionstatus | U16 |  |  | RO | 1 | → |  |  | Unmapped
357 | Inverter Realtime Data | 0x9265 | 37477 | [Scheduleserver] Latestconnectiontime | U32 |  |  | RO | 2 | → |  |  | Unmapped
358 | Inverter Realtime Data | 0x9267 | 37479 | Softwareversion | string |  |  | RO | 15 | → | FIRMWARE_VERSION |  | Ref(77%)
359 | Inverter Realtime Data | 0x9276 | 37494 | Numberofconnecteddevices | U16 |  |  | RO | 1 | → |  |  | Unmapped
360 | Inverter Realtime Data | 0x9278 | 37496 | Silenceflag | U16 |  |  | RO | 1 | → |  |  | Unmapped
361 | Inverter Realtime Data | 0x9279 | 37497 | Upgrade Status | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(64%)
362 | Inverter Realtime Data | 0x928E | 37518 | Invertercomprehensivestatus | U16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(67%)
363 | Inverter Realtime Data | 0x928F | 37519 | Inverterintegratedstatussupportflag | U16 |  |  | RO | 1 | → | INVERTER_STATUS |  | Ref(56%)
--- Inverter Parameters (Setup) ---
364 | Inverter Parameters (Setup) | 0x9C40 | 40000 | Systemtime (localtime ) | EpochSecond | s |  | RW | 2 | → |  |  | Unmapped
365 | Inverter Parameters (Setup) | 0x9C65 | 40037 | Q-U characteristiccurvemode | U16 |  |  | RW | 1 | → |  |  | Unmapped
366 | Inverter Parameters (Setup) | 0x9C66 | 40038 | Q-U Scheduling Trigger Power Percentage | S16 | % |  | RW | 1 | → |  |  | Unmapped
367 | Inverter Parameters (Setup) | 0x9CB8 | 40120 | Activepowerisderatedbyafixedvalue. | U16 | kW |  | RW | 1 | → |  |  | Unmapped
368 | Inverter Parameters (Setup) | 0x9CBA | 40122 | Powerfactor | S16 |  |  | RW | 1 | → | POWER_FACTOR |  | Ref(96%)
369 | Inverter Parameters (Setup) | 0x9CBB | 40123 | Reactivepowercompensation (Q/S ) [lowprecision] | S16 |  |  | RW | 1 | → | REACTIVE_POWER_LOW |  | Ref(57%)
370 | Inverter Parameters (Setup) | 0x9CBC | 40124 | Reactivepoweradjustmenttime | U16 | s |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(67%)
371 | Inverter Parameters (Setup) | 0x9CBD | 40125 | Activepowerpercentagederating (lowprecision) | S16 | % |  | RW | 1 | → |  |  | Unmapped
372 | Inverter Parameters (Setup) | 0x9CBE | 40126 | Activepowerisderatedbyafixedvalue. | U32 | W |  | RW | 2 | → |  |  | Unmapped
373 | Inverter Parameters (Setup) | 0x9CC0 | 40128 | Nightreactivepowercompensation (Q/S ) | S16 |  |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(58%)
374 | Inverter Parameters (Setup) | 0x9CC1 | 40129 | Fixedvalueofreactivepoweratnight | S32 | kVar |  | RW | 2 | → | DEA_REACTIVE_POWER_HIGH |  | Ref(65%)
375 | Inverter Parameters (Setup) | 0x9CC5 | 40133 | Cos? - P/Pncharacteristiccurve | string |  |  | RW | 21 | → |  |  | Unmapped
376 | Inverter Parameters (Setup) | 0x9CDA | 40154 | Q-U characteristiccurve | string |  |  | RW | 21 | → |  |  | Unmapped
377 | Inverter Parameters (Setup) | 0x9CEF | 40175 | PF-U characteristiccurve | string |  |  | RW | 21 | → |  |  | Unmapped
378 | Inverter Parameters (Setup) | 0x9D04 | 40196 | [Characteristiccurve] Reactivepoweradjustmenttime | U16 | s |  | RW | 1 | → |  |  | Unmapped
379 | Inverter Parameters (Setup) | 0x9D06 | 40198 | Q-U Scheduling Exit Power Percentage | S16 | % |  | RW | 1 | → |  |  | Unmapped
380 | Inverter Parameters (Setup) | 0x9D07 | 40199 | Activepowerpercentagecontrol [lowprecision] | S16 | % |  | RW | 1 | → |  |  | Unmapped
381 | Inverter Parameters (Setup) | 0x9D08 | 40200 | Startthesystem. | U16 |  |  | WO | 1 | → |  |  | Unmapped
382 | Inverter Parameters (Setup) | 0x9D09 | 40201 | Shutdown. | U16 |  |  | WO | 1 | → |  |  | Unmapped
383 | Inverter Parameters (Setup) | 0x9D0A | 40202 | Quickpower- onandpower- off | U16 |  |  | WO | 1 | → |  |  | Unmapped
384 | Inverter Parameters (Setup) | 0x9D0D | 40205 | reset | U16 |  |  | WO | 1 | → |  |  | Unmapped
385 | Inverter Parameters (Setup) | 0x9D0E | 40206 | Insulationimpedancediagnosis | U16 |  |  | WO | 1 | → |  |  | Unmapped
386 | Inverter Parameters (Setup) | 0x9D6C | 40300 | Dry Contact Scheduling Settings | string |  |  | RW | 33 | → |  |  | Unmapped
387 | Inverter Parameters (Setup) | 0x9DA2 | 40354 | Q-P characteristiccurve | string |  |  | RW | 21 | → |  |  | Unmapped
388 | Inverter Parameters (Setup) | 0x9DB7 | 40375 | Q-U characteristiccurveminimum PF limit | U16 |  |  | RW | 1 | → |  |  | Unmapped
389 | Inverter Parameters (Setup) | 0x9DB8 | 40376 | Q-U characteristiccurvevaliditydelaytime | U16 | s |  | RW | 1 | → |  |  | Unmapped
390 | Inverter Parameters (Setup) | 0x9E34 | 40500 | System Time (UTC ) | EpochSecond | s |  | WO | 2 | → | SYSTEM_STATUS |  | Ref(64%)
391 | Inverter Parameters (Setup) | 0xA410 | 42000 | Powergridstandardcode | U16 |  |  | RW | 1 | → | GRID_STANDARD |  | Ref(71%)
392 | Inverter Parameters (Setup) | 0xA411 | 42001 | Outputmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
393 | Inverter Parameters (Setup) | 0xA412 | 42002 | Voltagelevel | U16 | V |  | RW | 1 | → | S_VOLTAGE |  | Ref(67%)
394 | Inverter Parameters (Setup) | 0xA413 | 42003 | Frequency Class | U16 | Hz |  | RW | 1 | → | FREQUENCY |  | Ref(75%)
395 | Inverter Parameters (Setup) | 0xA41C | 42012 | Replacethetargetmodel. | U16 |  |  | RW | 1 | → |  |  | Unmapped
396 | Inverter Parameters (Setup) | 0xA41E | 42014 | Remotepowerscheduling | U16 |  |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(56%)
397 | Inverter Parameters (Setup) | 0xA41F | 42015 | reactivepowergradient | U32 | %/s |  | RW | 2 | → | REACTIVE_POWER_SET |  | Ref(77%)
398 | Inverter Parameters (Setup) | 0xA421 | 42017 | Activepowerchangegradient | U32 | %/s |  | RW | 2 | → | ACTIVE_POWER_PCT |  | Ref(63%)
399 | Inverter Parameters (Setup) | 0xA423 | 42019 | Scheduledinstructionholdtime | U32 | s |  | RW | 2 | → |  |  | Unmapped
400 | Inverter Parameters (Setup) | 0xA425 | 42021 | Maximumapparentpower | U32 | kVA |  | RW | 2 | → |  |  | Unmapped
401 | Inverter Parameters (Setup) | 0xA427 | 42023 | Maximumactivepower | U32 | kW |  | RW | 2 | → | ACTIVE_POWER |  | Ref(73%)
402 | Inverter Parameters (Setup) | 0xA429 | 42025 | apparentpowerreference | U32 | kVar |  | RW | 2 | → |  |  | Unmapped
403 | Inverter Parameters (Setup) | 0xA42B | 42027 | Activepowerreference | U32 | kW |  | RW | 2 | → | ACTIVE_POWER |  | Ref(69%)
404 | Inverter Parameters (Setup) | 0xA42D | 42029 | Plantactivepowergradient | U16 | min/100% |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(62%)
405 | Inverter Parameters (Setup) | 0xA42E | 42030 | Plantactiveaveragefilteringtime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
406 | Inverter Parameters (Setup) | 0xA430 | 42032 | Filteringtimefor PF-U voltagedetection | U16 | s |  | RW | 1 | → |  |  | Unmapped
407 | Inverter Parameters (Setup) | 0xA431 | 42033 | Drycontactscheduling | U16 |  |  | RW | 1 | → |  |  | Unmapped
408 | Inverter Parameters (Setup) | 0xA432 | 42034 | Audibleandvisualalarm | U16 |  |  | RW | 1 | → |  |  | Unmapped
409 | Inverter Parameters (Setup) | 0xA438 | 42040 | Frequency Active Power Derating Recovery Delay Time | U16 | s |  | RW | 1 | → |  |  | Unmapped
410 | Inverter Parameters (Setup) | 0xA439 | 42041 | Frequency Active Power Derating Effective Delay Time | U16 | ms |  | RW | 1 | → |  |  | Unmapped
411 | Inverter Parameters (Setup) | 0xA43A | 42042 | Frequencyactivepowerderatinghysteresis | U16 |  |  | RW | 1 | → |  |  | Unmapped
412 | Inverter Parameters (Setup) | 0xA43B | 42043 | Frequencymodulationcontrolresponsedeadband | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
413 | Inverter Parameters (Setup) | 0xA43C | 42044 | Of-fgridswitchovermode | U16 |  |  | RW | 1 | → |  |  | Unmapped
414 | Inverter Parameters (Setup) | 0xA43D | 42045 | Off- gridmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
415 | Inverter Parameters (Setup) | 0xA43E | 42046 | PQ mode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(57%)
416 | Inverter Parameters (Setup) | 0xA43F | 42047 | PV Panel Type | U16 |  |  | RW | 1 | → | DEVICE_TYPE |  | Ref(58%)
417 | Inverter Parameters (Setup) | 0xA440 | 42048 | PID compensationdirection | U16 |  |  | RW | 1 | → |  |  | Unmapped
418 | Inverter Parameters (Setup) | 0xA441 | 42049 | Stringconnectionmode | U16 |  |  | RW | 1 | → | ACTION_MODE |  | Ref(58%)
419 | Inverter Parameters (Setup) | 0xA442 | 42050 | Isolation Settings | U16 |  |  | RW | 1 | → | IV_SCAN_STATUS |  | Ref(56%)
420 | Inverter Parameters (Setup) | 0xA443 | 42051 | Frequencymodulationcontrolpowerchangegradient | U16 | %/min |  | RW | 1 | → |  |  | Unmapped
421 | Inverter Parameters (Setup) | 0xA444 | 42052 | Frequencymodulationcontrolpowerchangelimitingamplitude | U16 | % |  | RW | 1 | → |  |  | Unmapped
422 | Inverter Parameters (Setup) | 0xA445 | 42053 | FM controldelayresponsetime | U16 | ms |  | RW | 1 | → |  |  | Unmapped
423 | Inverter Parameters (Setup) | 0xA446 | 42054 | MPP T multimodalscanning | U16 |  |  | RW | 1 | → |  |  | Unmapped
424 | Inverter Parameters (Setup) | 0xA447 | 42055 | MPP T scanninginterval | U16 | min |  | RW | 1 | → |  |  | Unmapped
425 | Inverter Parameters (Setup) | 0xA448 | 42056 | Predicted MPP T power | U32 | kW |  | RO | 2 | → | REACTIVE_POWER |  | Ref(63%)
426 | Inverter Parameters (Setup) | 0xA44D | 42061 | Powergridfaultrecoveryautomaticstartup | U16 |  |  | RW | 1 | → |  |  | Unmapped
427 | Inverter Parameters (Setup) | 0xA44E | 42062 | Powerlimit 0% shutdown | U16 |  |  | RW | 1 | → |  |  | Unmapped
428 | Inverter Parameters (Setup) | 0xA44F | 42063 | Automaticpower- offwhencommunicationisdisconnected | U16 |  |  | RW | 1 | → |  |  | Unmapped
429 | Inverter Parameters (Setup) | 0xA450 | 42064 | Automaticpower- onaftercommunicationrecovery | U16 |  |  | RW | 1 | → |  |  | Unmapped
430 | Inverter Parameters (Setup) | 0xA451 | 42065 | Power Quality Optimization Mode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(58%)
431 | Inverter Parameters (Setup) | 0xA452 | 42066 | RCD Enhancement | U16 |  |  | RW | 1 | → |  |  | Unmapped
432 | Inverter Parameters (Setup) | 0xA453 | 42067 | Nightreactivepower | U16 |  |  | RW | 1 | → | REACTIVE_POWER |  | Ref(81%)
433 | Inverter Parameters (Setup) | 0xA454 | 42068 | Abnormalgroundingshutdown | U16 |  |  | RW | 1 | → |  |  | Unmapped
434 | Inverter Parameters (Setup) | 0xA455 | 42069 | Night PID protection | U16 |  |  | RW | 1 | → | DAILY_PRODUCTION |  | Ref(56%)
435 | Inverter Parameters (Setup) | 0xA456 | 42070 | Nightreactivepowerparameterstakeeffect | U16 |  |  | RW | 1 | → | REACTIVE_POWER_PCT |  | Ref(57%)
436 | Inverter Parameters (Setup) | 0xA458 | 42072 | Communication Disconnection Detection Time | U16 | s |  | RW | 1 | → |  |  | Unmapped
437 | Inverter Parameters (Setup) | 0xA459 | 42073 | AFCI | U16 |  |  | RW | 1 | → |  |  | Unmapped
438 | Inverter Parameters (Setup) | 0xA45A | 42074 | AFCI detectionadaptationmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
439 | Inverter Parameters (Setup) | 0xA45B | 42075 | Communicationlinkfailureprotection | U16 |  |  | RW | 1 | → |  |  | Unmapped
440 | Inverter Parameters (Setup) | 0xA45C | 42076 | Failureprotectionactivepowermode | U16 |  |  | RW | 1 | → | REACTIVE_POWER |  | Ref(57%)
441 | Inverter Parameters (Setup) | 0xA45D | 42077 | Active Power Limitfor Failure Protection [kW] [Low Precision] | U32 | kW |  | RW | 2 | → |  |  | Unmapped
442 | Inverter Parameters (Setup) | 0xA45F | 42079 | Failureprotectionreactivepowermode | U16 |  |  | RW | 1 | → |  |  | Unmapped
443 | Inverter Parameters (Setup) | 0xA460 | 42080 | Frequencyrateprotection | U16 |  |  | RW | 1 | → | FREQUENCY |  | Ref(56%)
444 | Inverter Parameters (Setup) | 0xA461 | 42081 | Frequencychangerateprotectionpoint | U16 | Hz/s |  | RW | 1 | → |  |  | Unmapped
445 | Inverter Parameters (Setup) | 0xA462 | 42082 | Frequencychangerateprotectiontime | U16 | s |  | RW | 1 | → |  |  | Unmapped
446 | Inverter Parameters (Setup) | 0xA463 | 42083 | Reactivepowerlimitforfailureprotection [Q/S ] [lowprecision] | S16 |  |  | RW | 1 | → |  |  | Unmapped
447 | Inverter Parameters (Setup) | 0xA464 | 42084 | Power- onvoltageupperlimitforgridconnection | U16 | V |  | RW | 1 | → |  |  | Unmapped
448 | Inverter Parameters (Setup) | 0xA465 | 42085 | Power- onvoltagelowerlimitforgridconnection | U16 | V |  | RW | 1 | → |  |  | Unmapped
449 | Inverter Parameters (Setup) | 0xA466 | 42086 | Power- onfrequencyupperlimitforgridconnection | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
450 | Inverter Parameters (Setup) | 0xA467 | 42087 | Power- onfrequencylowerlimitforgridconnection | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
451 | Inverter Parameters (Setup) | 0xA468 | 42088 | Powergridreconnectionvoltageupperlimit | U16 | V |  | RW | 1 | → |  |  | Unmapped
452 | Inverter Parameters (Setup) | 0xA469 | 42089 | Power Grid Reconnection Voltage Lower Threshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
453 | Inverter Parameters (Setup) | 0xA46A | 42090 | Powergridreconnectionfrequencyupperlimit | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
454 | Inverter Parameters (Setup) | 0xA46B | 42091 | Powergridreconnectionfrequencylowerlimit | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
455 | Inverter Parameters (Setup) | 0xA46C | 42092 | Automatic Power Grid Reconnection Time | U16 | s |  | RW | 1 | → |  |  | Unmapped
456 | Inverter Parameters (Setup) | 0xA471 | 42097 | Insulationimpedanceprotectionpoint | U16 | MΩ |  | RW | 1 | → |  |  | Unmapped
457 | Inverter Parameters (Setup) | 0xA472 | 42098 | Voltageunbalanceprotectionthreshold | U16 | % |  | RW | 1 | → |  |  | Unmapped
458 | Inverter Parameters (Setup) | 0xA473 | 42099 | Phaseprotectionpoint | U16 | ° |  | RW | 1 | → |  |  | Unmapped
459 | Inverter Parameters (Setup) | 0xA474 | 42100 | Power- onsoftstarttimeduetopowergridfaults | U16 | s |  | RW | 1 | → |  |  | Unmapped
460 | Inverter Parameters (Setup) | 0xA475 | 42101 | Cos? - P/Pntriggervoltage | U16 | % |  | RW | 1 | → | STRING8_VOLTAGE |  | Ref(65%)
461 | Inverter Parameters (Setup) | 0xA476 | 42102 | Cos? - P/Pnexitvoltage | U16 | % |  | RW | 1 | → | S_PHASE_VOLTAGE |  | Ref(65%)
462 | Inverter Parameters (Setup) | 0xA477 | 42103 | Startupsoftstarttime | U16 | s |  | RW | 1 | → |  |  | Unmapped
463 | Inverter Parameters (Setup) | 0xA478 | 42104 | Powergridfaultrecoverytime | U16 | s |  | RW | 1 | → |  |  | Unmapped
464 | Inverter Parameters (Setup) | 0xA479 | 42105 | Timefordeterminingshort - termpowergridinterruption | U32 | ms |  | RW | 2 | → |  |  | Unmapped
465 | Inverter Parameters (Setup) | 0xA47B | 42107 | Shutdowngradient | U32 | %/s |  | RW | 2 | → |  |  | Unmapped
466 | Inverter Parameters (Setup) | 0xA47D | 42109 | Linelosscompensation | U16 | % |  | RW | 1 | → |  |  | Unmapped
467 | Inverter Parameters (Setup) | 0xA47E | 42110 | Gridfaultzerocurrentmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
468 | Inverter Parameters (Setup) | 0xA47F | 42111 | Gridvoltagejumptriggerthreshold | U16 | % |  | RW | 1 | → |  |  | Unmapped
469 | Inverter Parameters (Setup) | 0xA480 | 42112 | HVR T | U16 |  |  | RW | 1 | → |  |  | Unmapped
470 | Inverter Parameters (Setup) | 0xA481 | 42113 | HVR T Trigger Threshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
471 | Inverter Parameters (Setup) | 0xA482 | 42114 | HVR T positivesequencereactivepowercompensationfactor | U16 |  |  | RW | 1 | → |  |  | Unmapped
472 | Inverter Parameters (Setup) | 0xA483 | 42115 | V phasetoground | U16 |  |  | RW | 1 | → |  |  | Unmapped
473 | Inverter Parameters (Setup) | 0xA484 | 42116 | Short- termpowergridinterruptionandquickstartup | U16 |  |  | RW | 1 | → |  |  | Unmapped
474 | Inverter Parameters (Setup) | 0xA486 | 42118 | LVRT activecurrentmaintenancecoefficient | U16 |  |  | RW | 1 | → |  |  | Unmapped
475 | Inverter Parameters (Setup) | 0xA487 | 42119 | LVRT | U16 |  |  | RW | 1 | → |  |  | Unmapped
476 | Inverter Parameters (Setup) | 0xA488 | 42120 | LVRT Trigger Threshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
477 | Inverter Parameters (Setup) | 0xA489 | 42121 | Powergridvoltageprotectionshieldduring VRT | U16 |  |  | RW | 1 | → |  |  | Unmapped
478 | Inverter Parameters (Setup) | 0xA48A | 42122 | LVRT positivesequencereactivepowercompensationfactor | U16 |  |  | RW | 1 | → |  |  | Unmapped
479 | Inverter Parameters (Setup) | 0xA48B | 42123 | VRT exithysteresisthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
480 | Inverter Parameters (Setup) | 0xA48C | 42124 | VRT activecurrentlimitingpercentage | U16 | % |  | RW | 1 | → |  |  | Unmapped
481 | Inverter Parameters (Setup) | 0xA48D | 42125 | VRT activepowerrecoverygradient | U16 | %/s |  | RW | 1 | → | DER_ACTIVE_POWER_PCT |  | Ref(59%)
482 | Inverter Parameters (Setup) | 0xA48E | 42126 | HVR T negativesequencereactivecompensationfactor | U16 |  |  | RW | 1 | → |  |  | Unmapped
483 | Inverter Parameters (Setup) | 0xA48F | 42127 | LVRT negativesequencereactivepowercompensationfactor | U16 |  |  | RW | 1 | → |  |  | Unmapped
484 | Inverter Parameters (Setup) | 0xA490 | 42128 | phaseangledeviationprotection | U16 |  |  | RW | 1 | → |  |  | Unmapped
485 | Inverter Parameters (Setup) | 0xA491 | 42129 | Active Islanding Protection | U16 |  |  | RW | 1 | → | CUMULATIVE_PRODUCTION_H |  | Ref(56%)
486 | Inverter Parameters (Setup) | 0xA492 | 42130 | Passive Islanding Protection | U16 |  |  | RW | 1 | → |  |  | Unmapped
487 | Inverter Parameters (Setup) | 0xA493 | 42131 | OVG R Associated Shutdown | U16 |  |  | RW | 1 | → |  |  | Unmapped
488 | Inverter Parameters (Setup) | 0xA494 | 42132 | Drycontactfunction | U16 |  |  | RW | 1 | → | DAILY_CONSUMPTION |  | Ref(57%)
489 | Inverter Parameters (Setup) | 0xA495 | 42133 | LVRT reactivecurrentlimitingpercentage | U16 | % |  | RW | 1 | → |  |  | Unmapped
490 | Inverter Parameters (Setup) | 0xA496 | 42134 | LVRT zerocurrentmodethreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
491 | Inverter Parameters (Setup) | 0xA497 | 42135 | LVRT mode | U16 |  |  | RW | 1 | → | INVERTER_MODE |  | Ref(73%)
492 | Inverter Parameters (Setup) | 0xA498 | 42136 | RCD currentlimit | U16 | mA |  | RW | 1 | → | R_CURRENT |  | Ref(72%)
493 | Inverter Parameters (Setup) | 0xA49A | 42138 | Voltagerisesuppression | U16 |  |  | RW | 1 | → |  |  | Unmapped
494 | Inverter Parameters (Setup) | 0xA49B | 42139 | Voltagerisesuppressionreactivepoweradjustmentpoint | U16 | % |  | RW | 1 | → |  |  | Unmapped
495 | Inverter Parameters (Setup) | 0xA49C | 42140 | Voltagerisesuppressionactivederatingthreshold | U16 | % |  | RW | 1 | → |  |  | Unmapped
496 | Inverter Parameters (Setup) | 0xA49D | 42141 | frequencymodulationcontrol | U16 |  |  | RW | 1 | → |  |  | Unmapped
497 | Inverter Parameters (Setup) | 0xA49E | 42142 | frequencymodulationcontroldifferentialmodulationrate | U16 | % |  | RW | 1 | → |  |  | Unmapped
498 | Inverter Parameters (Setup) | 0xA49F | 42143 | Overfrequencyderating | U16 |  |  | RW | 1 | → | R_FREQUENCY |  | Ref(62%)
499 | Inverter Parameters (Setup) | 0xA4A0 | 42144 | Overfrequencyderatingcutofffrequency | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
500 | Inverter Parameters (Setup) | 0xA4A1 | 42145 | Overfrequencyderatingcut- offpower | U16 | % |  | RW | 1 | → |  |  | Unmapped
501 | Inverter Parameters (Setup) | 0xA4A2 | 42146 | Triggeringfrequencyofoverfrequencyderating | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
502 | Inverter Parameters (Setup) | 0xA4A3 | 42147 | Overfrequencyderatingexitfrequency | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
503 | Inverter Parameters (Setup) | 0xA4A4 | 42148 | Overfrequencyderatingpowerrecoverygradient | U16 | %/min |  | RW | 1 | → |  |  | Unmapped
504 | Inverter Parameters (Setup) | 0xA4A7 | 42151 | Underfrequency Power Increase | U16 |  |  | RW | 1 | → | DEA_FREQUENCY_LOW |  | Ref(61%)
505 | Inverter Parameters (Setup) | 0xA4A8 | 42152 | Underfrequency Power Increase Recovery Gradient | U16 | %/min |  | RW | 1 | → |  |  | Unmapped
506 | Inverter Parameters (Setup) | 0xA4AB | 42155 | LVRT characteristiccurve | string |  |  | RW | 21 | → |  |  | Unmapped
507 | Inverter Parameters (Setup) | 0xA4C0 | 42176 | Cutofffrequencyofunderfrequencypowerincrease | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
508 | Inverter Parameters (Setup) | 0xA4C1 | 42177 | Cut- offpowerforunderfrequencypowerincrease | U16 | % |  | RW | 1 | → |  |  | Unmapped
509 | Inverter Parameters (Setup) | 0xA4C2 | 42178 | Underfrequency Power Increase Triggering Frequency | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
510 | Inverter Parameters (Setup) | 0xA4C3 | 42179 | Underfrequency Power Increase Exit Frequency | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
511 | Inverter Parameters (Setup) | 0xA4C4 | 42180 | Built -in PID mode | U16 |  |  | RW | 1 | → |  |  | Unmapped
512 | Inverter Parameters (Setup) | 0xA4C5 | 42181 | PID outputvoltage | S16 | V |  | RW | 1 | → | GRID_T_VOLTAGE |  | Ref(71%)
513 | Inverter Parameters (Setup) | 0xA4C6 | 42182 | PID | U16 |  |  | RW | 1 | → |  |  | Unmapped
514 | Inverter Parameters (Setup) | 0xA4C7 | 42183 | Nightoff- gridrepair | U16 |  |  | RW | 1 | → |  |  | Unmapped
515 | Inverter Parameters (Setup) | 0xA4D0 | 42192 | Activepowerchangegradient | U32 | %/s |  | RW | 2 | → | ACTIVE_POWER_PCT |  | Ref(63%)
516 | Inverter Parameters (Setup) | 0xA4D8 | 42200 | Q-U curve | string |  |  | RW | 21 | → | T_CURRENT |  | Ref(56%)
517 | Inverter Parameters (Setup) | 0xA4ED | 42221 | P-U curve | string |  |  | RW | 21 | → | PV_CURRENT |  | Ref(63%)
518 | Inverter Parameters (Setup) | 0xA502 | 42242 | P-U curveadjustmenttime | U16 | s |  | RW | 1 | → |  |  | Unmapped
519 | Inverter Parameters (Setup) | 0xA52F | 42287 | Undervoltageprotectionthresholdfor 10 minutes | U16 | V |  | RW | 1 | → |  |  | Unmapped
520 | Inverter Parameters (Setup) | 0xA530 | 42288 | Ten- minuteundervoltageprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
521 | Inverter Parameters (Setup) | 0xA532 | 42290 | Ten- minuteovervoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
522 | Inverter Parameters (Setup) | 0xA533 | 42291 | Ten- minuteovervoltageprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
523 | Inverter Parameters (Setup) | 0xA535 | 42293 | Level-1 overvoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
524 | Inverter Parameters (Setup) | 0xA536 | 42294 | Level-1 overvoltageprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
525 | Inverter Parameters (Setup) | 0xA538 | 42296 | Level-2 overvoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
526 | Inverter Parameters (Setup) | 0xA539 | 42297 | Level 2 Overvoltage Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
527 | Inverter Parameters (Setup) | 0xA53B | 42299 | Level-3 overvoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
528 | Inverter Parameters (Setup) | 0xA53C | 42300 | Level-3 overvoltageprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
529 | Inverter Parameters (Setup) | 0xA53E | 42302 | Level-4 overvoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
530 | Inverter Parameters (Setup) | 0xA53F | 42303 | Level-4 overvoltageprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
531 | Inverter Parameters (Setup) | 0xA541 | 42305 | Level-5 overvoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
532 | Inverter Parameters (Setup) | 0xA542 | 42306 | Level-5 overvoltageprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
533 | Inverter Parameters (Setup) | 0xA544 | 42308 | Level-6 overvoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
534 | Inverter Parameters (Setup) | 0xA545 | 42309 | Level-6 overvoltageprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
535 | Inverter Parameters (Setup) | 0xA547 | 42311 | Level-1 undervoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
536 | Inverter Parameters (Setup) | 0xA548 | 42312 | Level-1 Undervoltage Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
537 | Inverter Parameters (Setup) | 0xA54A | 42314 | Level-2 undervoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
538 | Inverter Parameters (Setup) | 0xA54B | 42315 | Level 2 Undervoltage Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
539 | Inverter Parameters (Setup) | 0xA54D | 42317 | Level-3 undervoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
540 | Inverter Parameters (Setup) | 0xA54E | 42318 | Level-3 Undervoltage Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
541 | Inverter Parameters (Setup) | 0xA550 | 42320 | Level-4 undervoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
542 | Inverter Parameters (Setup) | 0xA551 | 42321 | Level-4 Undervoltage Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
543 | Inverter Parameters (Setup) | 0xA553 | 42323 | Level-5 undervoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
544 | Inverter Parameters (Setup) | 0xA554 | 42324 | Level-5 Undervoltage Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
545 | Inverter Parameters (Setup) | 0xA556 | 42326 | Level-6 undervoltageprotectionthreshold | U16 | V |  | RW | 1 | → |  |  | Unmapped
546 | Inverter Parameters (Setup) | 0xA557 | 42327 | Level-6 Undervoltage Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
547 | Inverter Parameters (Setup) | 0xA559 | 42329 | Level-1 overfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
548 | Inverter Parameters (Setup) | 0xA55A | 42330 | Level-1 Overfrequency Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
549 | Inverter Parameters (Setup) | 0xA55C | 42332 | Level-2 overfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
550 | Inverter Parameters (Setup) | 0xA55D | 42333 | Level-2 overfrequencyprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
551 | Inverter Parameters (Setup) | 0xA55F | 42335 | Level-3 overfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
552 | Inverter Parameters (Setup) | 0xA560 | 42336 | Level-3 overfrequencyprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
553 | Inverter Parameters (Setup) | 0xA562 | 42338 | Level-4 overfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
554 | Inverter Parameters (Setup) | 0xA563 | 42339 | Level-4 overfrequencyprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
555 | Inverter Parameters (Setup) | 0xA565 | 42341 | Level-5 overfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
556 | Inverter Parameters (Setup) | 0xA566 | 42342 | Level-5 overfrequencyprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
557 | Inverter Parameters (Setup) | 0xA568 | 42344 | Level-6 overfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
558 | Inverter Parameters (Setup) | 0xA569 | 42345 | Six- leveloverfrequencyprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
559 | Inverter Parameters (Setup) | 0xA56B | 42347 | Level-1 underfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
560 | Inverter Parameters (Setup) | 0xA56C | 42348 | Level-1 Underfrequency Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
561 | Inverter Parameters (Setup) | 0xA56E | 42350 | Level-2 underfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
562 | Inverter Parameters (Setup) | 0xA56F | 42351 | Level-2 underfrequencyprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
563 | Inverter Parameters (Setup) | 0xA571 | 42353 | Level-3 underfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
564 | Inverter Parameters (Setup) | 0xA572 | 42354 | Level-3 underfrequencyprotectiontime | U32 | ms |  | RW | 2 | → |  |  | Unmapped
565 | Inverter Parameters (Setup) | 0xA574 | 42356 | Level-4 underfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
566 | Inverter Parameters (Setup) | 0xA575 | 42357 | Level-4 Underfrequency Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
567 | Inverter Parameters (Setup) | 0xA577 | 42359 | Level-5 underfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
568 | Inverter Parameters (Setup) | 0xA578 | 42360 | Level-5 Underfrequency Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
569 | Inverter Parameters (Setup) | 0xA57A | 42362 | Level-6 underfrequencyprotectionthreshold | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
570 | Inverter Parameters (Setup) | 0xA57B | 42363 | Level-6 Underfrequency Protection Time | U32 | ms |  | RW | 2 | → |  |  | Unmapped
571 | Inverter Parameters (Setup) | 0xA5A0 | 42400 | Emergencystopswitch DI | U16 |  |  | RW | 1 | → |  |  | Unmapped
572 | Inverter Parameters (Setup) | 0xA5A3 | 42403 | Outputimpedanceenhancement | U16 |  |  | RW | 1 | → |  |  | Unmapped
573 | Inverter Parameters (Setup) | 0xA5A4 | 42404 | Outputimpedanceenhancementfrequencypoint | U16 | Hz |  | RW | 1 | → |  |  | Unmapped
574 | Inverter Parameters (Setup) | 0xA5A7 | 42407 | Microgridadaptability | U16 |  |  | RW | 1 | → |  |  | Unmapped
575 | Inverter Parameters (Setup) | 0xA5A9 | 42409 | Operatingmode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(89%)
576 | Inverter Parameters (Setup) | 0xA5BD | 42429 | Underfrequency Power Increase Effective Delay Time | U16 | ms |  | RW | 1 | → |  |  | Unmapped
577 | Inverter Parameters (Setup) | 0xA5C0 | 42432 | String-to- groundshortcircuitprotectionautomaticrecovery | U16 |  |  | RW | 1 | → |  |  | Unmapped
578 | Inverter Parameters (Setup) | 0xA65E | 42590 | Delayedupgrade | U16 |  |  | RW | 1 | → |  |  | Unmapped
579 | Inverter Parameters (Setup) | 0xA662 | 42594 | Intelligentstringmonitoring | U16 |  |  | RW | 1 | → |  |  | Unmapped
580 | Inverter Parameters (Setup) | 0xA663 | 42595 | Stringdetectionreferenceasymmetrycoefficient | U16 |  |  | RW | 1 | → |  |  | Unmapped
581 | Inverter Parameters (Setup) | 0xA664 | 42596 | Stringdetectionstartpowerpercentage | U16 | % |  | RW | 1 | → |  |  | Unmapped
582 | Inverter Parameters (Setup) | 0xA665 | 42597 | Communication Interruption Time | S16 | min |  | RW | 1 | → |  |  | Unmapped
583 | Inverter Parameters (Setup) | 0xA666 | 42598 | Communications | U16 |  |  | RW | 1 | → |  |  | Unmapped
584 | Inverter Parameters (Setup) | 0xA667 | 42599 | [RS4 85-2 ] Communication | U16 |  |  | RW | 1 | → |  |  | Unmapped
585 | Inverter Parameters (Setup) | 0xA6EA | 42730 | PMI | U16 |  |  | WO | 1 | → |  |  | Unmapped
586 | Inverter Parameters (Setup) | 0xA71B | 42779 | IV Curve Scanning | U16 |  |  | WO | 1 | → | IV_CURVE_SCAN |  | Ref(87%)
587 | Inverter Parameters (Setup) | 0xA794 | 42900 | Daylight Saving Time | U16 |  |  | RW | 1 | → |  |  | Unmapped
588 | Inverter Parameters (Setup) | 0xA795 | 42901 | [DST ] Offsettime | S16 | min |  | RW | 1 | → |  |  | Unmapped
589 | Inverter Parameters (Setup) | 0xA796 | 42902 | [DST ] Start Month | U16 |  |  | RW | 1 | → |  |  | Unmapped
590 | Inverter Parameters (Setup) | 0xA797 | 42903 | [DST ] Startdate | U16 |  |  | RW | 1 | → |  |  | Unmapped
591 | Inverter Parameters (Setup) | 0xA798 | 42904 | [DST ] Starttime | U16 |  |  | RW | 1 | → |  |  | Unmapped
592 | Inverter Parameters (Setup) | 0xA799 | 42905 | [DST ] Startminute | U16 |  |  | RW | 1 | → | SYSTEM_STATUS |  | Ref(57%)
593 | Inverter Parameters (Setup) | 0xA79A | 42906 | [DST ] Startsecond | U16 |  |  | RW | 1 | → | SYSTEM_STATUS |  | Ref(57%)
594 | Inverter Parameters (Setup) | 0xA79B | 42907 | [DST ] Endmonth | U16 |  |  | RW | 1 | → |  |  | Unmapped
595 | Inverter Parameters (Setup) | 0xA79C | 42908 | [DST ] Enddate | U16 |  |  | RW | 1 | → |  |  | Unmapped
596 | Inverter Parameters (Setup) | 0xA79D | 42909 | [Daylight Saving Time ] Ends | U16 |  |  | RW | 1 | → |  |  | Unmapped
597 | Inverter Parameters (Setup) | 0xA79E | 42910 | [DST ] Endminute | U16 |  |  | RW | 1 | → |  |  | Unmapped
598 | Inverter Parameters (Setup) | 0xA79F | 42911 | [DST ] Endsecond | U16 |  |  | RW | 1 | → | DSP_VERSION |  | Ref(58%)
599 | Inverter Parameters (Setup) | 0xA7F8 | 43000 | [System Time ] Year | U16 |  |  | WO | 1 | → | SYSTEM_STATUS |  | Ref(62%)
600 | Inverter Parameters (Setup) | 0xA7F9 | 43001 | [System Time ] Month | U16 |  |  | WO | 1 | → | SYSTEM_STATUS |  | Ref(60%)
601 | Inverter Parameters (Setup) | 0xA7FA | 43002 | [Systemtime ] day | U16 |  |  | WO | 1 | → | SYSTEM_STATUS |  | Ref(59%)
602 | Inverter Parameters (Setup) | 0xA7FB | 43003 | [Systemtime ] hour | U16 |  |  | WO | 1 | → | SYSTEM_STATUS |  | Ref(57%)
603 | Inverter Parameters (Setup) | 0xA7FC | 43004 | [System Time ] Min. | U16 |  |  | WO | 1 | → | SYSTEM_STATUS |  | Ref(57%)
604 | Inverter Parameters (Setup) | 0xA7FD | 43005 | [System Time ] Second | U16 |  |  | WO | 1 | → | SYSTEM_STATUS |  | Ref(58%)
605 | Inverter Parameters (Setup) | 0xA7FE | 43006 | Timezone | S16 | min |  | RW | 1 | → |  |  | Unmapped
606 | Inverter Parameters (Setup) | 0xA7FF | 43007 | Clocksource | U16 |  |  | RW | 1 | → |  |  | Unmapped
607 | Inverter Parameters (Setup) | 0xA800 | 43008 | Citycode | U32 |  |  | RW | 2 | → |  |  | Unmapped
608 | Inverter Parameters (Setup) | 0xA806 | 43014 | Inverter Installation Position Longitude | S32 | ° |  | RW | 2 | → |  |  | Unmapped
609 | Inverter Parameters (Setup) | 0xA808 | 43016 | Inverter Installation Position Latitude | S32 | ° |  | RW | 2 | → |  |  | Unmapped
610 | Inverter Parameters (Setup) | 0xA80A | 43018 | [RS4 85-1 ] Protocol Type | U16 |  |  | RW | 1 | → |  |  | Unmapped
611 | Inverter Parameters (Setup) | 0xA80B | 43019 | [RS4 85-1 ] Communicationaddress | U16 |  |  | RW | 1 | → |  |  | Unmapped
612 | Inverter Parameters (Setup) | 0xA80C | 43020 | [RS4 85-1 ] Baud Rate | U16 |  |  | RW | 1 | → |  |  | Unmapped
613 | Inverter Parameters (Setup) | 0xA80D | 43021 | [RS4 85-1 ] Verificationmode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(56%)
614 | Inverter Parameters (Setup) | 0xA80E | 43022 | [RS4 85-1 ] Portmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
615 | Inverter Parameters (Setup) | 0xA80F | 43023 | [RS4 85-1 ] Modbus Protocol Model Version | U16 |  |  | RW | 1 | → |  |  | Unmapped
616 | Inverter Parameters (Setup) | 0xA819 | 43033 | [RS4 85-2 ] Protocol Type | U16 |  |  | RW | 1 | → |  |  | Unmapped
617 | Inverter Parameters (Setup) | 0xA81A | 43034 | [RS4 85-2 ] Communicationaddress | U16 |  |  | RW | 1 | → |  |  | Unmapped
618 | Inverter Parameters (Setup) | 0xA81B | 43035 | [RS4 85-2 ] Baud Rate | U16 |  |  | RW | 1 | → |  |  | Unmapped
619 | Inverter Parameters (Setup) | 0xA81C | 43036 | [RS4 85-2 ] Verification Mode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(60%)
620 | Inverter Parameters (Setup) | 0xA81D | 43037 | [RS4 85-2 ] Portmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
621 | Inverter Parameters (Setup) | 0xA827 | 43047 | Protocol Type | U16 |  |  | RW | 1 | → |  |  | Unmapped
622 | Inverter Parameters (Setup) | 0xA828 | 43048 | Box- typetransformernumber | U16 |  |  | RW | 1 | → |  |  | Unmapped
623 | Inverter Parameters (Setup) | 0xA829 | 43049 | Winding No. | U16 |  |  | RW | 1 | → |  |  | Unmapped
624 | Inverter Parameters (Setup) | 0xA82A | 43050 | Mac Offset | U16 |  |  | RW | 1 | → | AC_POWER |  | Ref(56%)
625 | Inverter Parameters (Setup) | 0xA82C | 43052 | Powersettings | U16 | dB |  | RW | 1 | → | POWER_DERATING_PCT |  | Ref(65%)
626 | Inverter Parameters (Setup) | 0xA837 | 43063 | [Management System] TCP Frame Length | U16 |  |  | RW | 1 | → |  |  | Unmapped
627 | Inverter Parameters (Setup) | 0xA838 | 43064 | [Management System] Application- Layer Heartbeat Interval | U16 | min |  | RW | 1 | → |  |  | Unmapped
628 | Inverter Parameters (Setup) | 0xA839 | 43065 | [Management System] TCP Heartbeat Interval | U16 | s |  | RW | 1 | → |  |  | Unmapped
629 | Inverter Parameters (Setup) | 0xA83A | 43066 | [Management System] Protocol Type | U16 |  |  | RW | 1 | → |  |  | Unmapped
630 | Inverter Parameters (Setup) | 0xA83B | 43067 | [Management System] Server | string |  |  | RW | 30 | → |  |  | Unmapped
631 | Inverter Parameters (Setup) | 0xA859 | 43097 | [Managementsystem] Port 1 | U16 |  |  | RW | 1 | → |  |  | Unmapped
632 | Inverter Parameters (Setup) | 0xA85A | 43098 | [Management System] TLS Encryption | U16 |  |  | RW | 1 | → |  |  | Unmapped
633 | Inverter Parameters (Setup) | 0xA85C | 43100 | [Management System] Portmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
634 | Inverter Parameters (Setup) | 0xA85E | 43102 | [FE] Keypassword | string |  |  | WO | 32 | → |  |  | Unmapped
635 | Inverter Parameters (Setup) | 0xA88B | 43147 | [STA ] Accessinga Wireless Router | U16 |  |  | RW | 1 | → |  |  | Unmapped
636 | Inverter Parameters (Setup) | 0xA88C | 43148 | [STA ] Wireless Routing Network Name | string |  |  | RW | 16 | → |  |  | Unmapped
637 | Inverter Parameters (Setup) | 0xA89C | 43164 | [STA ] Wireless Routing Encryption Mode | U16 |  |  | RW | 1 | → |  |  | Unmapped
638 | Inverter Parameters (Setup) | 0xA89D | 43165 | [STA ] Wireless Router Login Password | string |  |  | RW | 32 | → |  |  | Unmapped
639 | Inverter Parameters (Setup) | 0xA8BD | 43197 | [FE] DHC P | U16 |  |  | RW | 1 | → |  |  | Unmapped
640 | Inverter Parameters (Setup) | 0xA8BE | 43198 | [FE] IP address | IPv4 |  |  | RW | 2 | → |  |  | Unmapped
641 | Inverter Parameters (Setup) | 0xA8C0 | 43200 | [FE] Subnet Mask | IPv4 |  |  | RW | 2 | → |  |  | Unmapped
642 | Inverter Parameters (Setup) | 0xA8C2 | 43202 | [FE] Gatewayaddress | IPv4 |  |  | RW | 2 | → |  |  | Unmapped
643 | Inverter Parameters (Setup) | 0xA8C4 | 43204 | [STA ] Preferred DNS Server | U32 |  |  | RW | 2 | → |  |  | Unmapped
644 | Inverter Parameters (Setup) | 0xA8C6 | 43206 | [STA ] Standby DNS server | U32 |  |  | RW | 2 | → |  |  | Unmapped
645 | Inverter Parameters (Setup) | 0xA8C8 | 43208 | [FE] DHC P | U16 |  |  | RW | 1 | → |  |  | Unmapped
646 | Inverter Parameters (Setup) | 0xA8C9 | 43209 | [FE] IP address | U32 |  |  | RW | 2 | → |  |  | Unmapped
647 | Inverter Parameters (Setup) | 0xA8CB | 43211 | [FE] Subnet Mask | U32 |  |  | RW | 2 | → |  |  | Unmapped
648 | Inverter Parameters (Setup) | 0xA8CD | 43213 | [FE] Gatewayaddress | U32 |  |  | RW | 2 | → |  |  | Unmapped
649 | Inverter Parameters (Setup) | 0xA8CF | 43215 | [FE] Preferred DNS server | U32 |  |  | RW | 2 | → |  |  | Unmapped
650 | Inverter Parameters (Setup) | 0xA8D1 | 43217 | [FE] Secondary DNS server | U32 |  |  | RW | 2 | → |  |  | Unmapped
651 | Inverter Parameters (Setup) | 0xA8E4 | 43236 | WLA N O& M Policy | U16 |  |  | RW | 1 | → |  |  | Unmapped
652 | Inverter Parameters (Setup) | 0xA8E5 | 43237 | [AP] SSID broadcast | U16 |  |  | RW | 1 | → |  |  | Unmapped
653 | Inverter Parameters (Setup) | 0xA8E6 | 43238 | [AP] WLA N name | string |  |  | RW | 16 | → |  |  | Unmapped
654 | Inverter Parameters (Setup) | 0xA8F6 | 43254 | [AP] WLA N Login Password | string |  |  | RW | 32 | → |  |  | Unmapped
655 | Inverter Parameters (Setup) | 0xA917 | 43287 | [AP] Gateway IP address | U32 |  |  | RW | 2 | → |  |  | Unmapped
656 | Inverter Parameters (Setup) | 0xA919 | 43289 | [AP] subnetmask | U32 |  |  | RW | 2 | → |  |  | Unmapped
657 | Inverter Parameters (Setup) | 0xA92F | 43311 | [NTP ] NTP timesynchronization | U16 |  |  | RW | 1 | → |  |  | Unmapped
658 | Inverter Parameters (Setup) | 0xA930 | 43312 | [NTP ] NTP serveraddress | string |  |  | RW | 30 | → |  |  | Unmapped
659 | Inverter Parameters (Setup) | 0xA94E | 43342 | [NTP ] NTP serverport | U16 |  |  | RW | 1 | → |  |  | Unmapped
660 | Inverter Parameters (Setup) | 0xA94F | 43343 | [NTP ] NTP Service Time Interval | U16 | min |  | RW | 1 | → |  |  | Unmapped
661 | Inverter Parameters (Setup) | 0xA955 | 43349 | Devicename | string |  |  | RW | 10 | → | DEVICE_MODEL |  | Ref(73%)
662 | Inverter Parameters (Setup) | 0xA95F | 43359 | [App ] Initialpower- onflag | U16 |  |  | RW | 1 | → | NOMINAL_POWER_LOW |  | Ref(55%)
663 | Inverter Parameters (Setup) | 0xA961 | 43361 | Parallelcommunicationmode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(56%)
664 | Inverter Parameters (Setup) | 0xA96A | 43370 | [4G] 4G module | U16 |  |  | RW | 1 | → |  |  | Unmapped
665 | Inverter Parameters (Setup) | 0xA97A | 43386 | [4G] Card No. | string |  |  | RW | 10 | → |  |  | Unmapped
666 | Inverter Parameters (Setup) | 0xA9A6 | 43430 | [4G] Networkmode | U16 |  |  | RW | 1 | → |  |  | Unmapped
667 | Inverter Parameters (Setup) | 0xA9A7 | 43431 | [4G] APN mode | U16 |  |  | RW | 1 | → | DER_ACTION_MODE |  | Ref(60%)
668 | Inverter Parameters (Setup) | 0xA9A9 | 43433 | [4G] [Default] Identityauthenticationtype | U16 |  |  | RW | 1 | → |  |  | Unmapped
669 | Inverter Parameters (Setup) | 0xA9AA | 43434 | [4G] [Default] APN | string |  |  | RW | 16 | → | EEPROM_DEFAULT |  | Ref(56%)
670 | Inverter Parameters (Setup) | 0xA9CA | 43466 | [4G] [Default] APN username | string |  |  | RW | 16 | → |  |  | Unmapped
671 | Inverter Parameters (Setup) | 0xA9DA | 43482 | [4G] [Default] APN userpassword | string |  |  | RW | 16 | → |  |  | Unmapped
672 | Inverter Parameters (Setup) | 0xA9EB | 43499 | [4G] Identityauthenticationtype | U16 |  |  | RW | 1 | → |  |  | Unmapped
673 | Inverter Parameters (Setup) | 0xA9EC | 43500 | [4G] APN | string |  |  | RW | 16 | → |  |  | Unmapped
674 | Inverter Parameters (Setup) | 0xA9FC | 43516 | [4G] APN dial- upnumber | string |  |  | RW | 16 | → | SERIAL_NUMBER |  | Ref(59%)
675 | Inverter Parameters (Setup) | 0xAA0C | 43532 | [4G] APN User Name | string |  |  | RW | 16 | → |  |  | Unmapped
676 | Inverter Parameters (Setup) | 0xAA1C | 43548 | [4G] APN userpassword | string |  |  | RW | 16 | → |  |  | Unmapped
677 | Inverter Parameters (Setup) | 0xAA2C | 43564 | [4G] Trafficpackage | U32 | MB |  | RW | 2 | → |  |  | Unmapped
678 | Inverter Parameters (Setup) | 0xAA2E | 43566 | [4G] Monthlyusedtraffic | U32 | MB |  | RW | 2 | → |  |  | Unmapped
679 | Inverter Parameters (Setup) | 0xAA30 | 43568 | [4G] PIN | string |  |  | WO | 4 | → |  |  | Unmapped
680 | Inverter Parameters (Setup) | 0xAA70 | 43632 | Stringaccessdetection | U16 |  |  | RW | 1 | → |  |  | Unmapped
681 | Inverter Parameters (Setup) | 0xAA71 | 43633 | Start -upcurrent | U16 | A |  | RW | 1 | → | STR8_CURRENT |  | Ref(81%)
682 | Inverter Parameters (Setup) | 0xAA72 | 43634 | Two- in- onedetectionstartingcurrent | U16 | A |  | RW | 1 | → |  |  | Unmapped
683 | Inverter Parameters (Setup) | 0xAA73 | 43635 | String 1 accesstype | U16 |  |  | RW | 1 | → | STRING1_CURRENT |  | Ref(65%)
684 | Inverter Parameters (Setup) | 0xAA74 | 43636 | String 2 Access Type | U16 |  |  | RW | 1 | → | STRING2_CURRENT |  | Ref(63%)
685 | Inverter Parameters (Setup) | 0xAA75 | 43637 | String 3 Access Type | U16 |  |  | RW | 1 | → | STRING3_CURRENT |  | Ref(63%)
686 | Inverter Parameters (Setup) | 0xAA76 | 43638 | String 4 Access Type | U16 |  |  | RW | 1 | → | STRING4_CURRENT |  | Ref(63%)
687 | Inverter Parameters (Setup) | 0xAA77 | 43639 | String 5 Access Type | U16 |  |  | RW | 1 | → | STRING5_CURRENT |  | Ref(63%)
688 | Inverter Parameters (Setup) | 0xAA78 | 43640 | String 6 Access Type | U16 |  |  | RW | 1 | → | STRING6_CURRENT |  | Ref(63%)
689 | Inverter Parameters (Setup) | 0xAA79 | 43641 | String 7 Access Type | U16 |  |  | RW | 1 | → | STRING7_CURRENT |  | Ref(63%)
690 | Inverter Parameters (Setup) | 0xAA7A | 43642 | String 8 Access Type | U16 |  |  | RW | 1 | → | STRING8_CURRENT |  | Ref(63%)
691 | Inverter Parameters (Setup) | 0xABE0 | 44000 | Support System Type | U16 |  |  | RW | 1 | → |  |  | Unmapped
692 | Inverter Parameters (Setup) | 0xABE1 | 44001 | Operatingmode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(89%)
693 | Inverter Parameters (Setup) | 0xABE2 | 44002 | Controlperiod | U16 | min |  | RW | 1 | → |  |  | Unmapped
694 | Inverter Parameters (Setup) | 0xABE3 | 44003 | Starttimeofreversetracinginthemorning (hour) | U16 | hour |  | RW | 1 | → |  |  | Unmapped
695 | Inverter Parameters (Setup) | 0xABE4 | 44004 | Starttimeofreversetracinginthemorning (minutes) | U16 | min |  | RW | 1 | → |  |  | Unmapped
696 | Inverter Parameters (Setup) | 0xABE5 | 44005 | Morning Backtracking Duration Minute | U16 | min |  | RW | 1 | → |  |  | Unmapped
697 | Inverter Parameters (Setup) | 0xABE6 | 44006 | Tiltanglecontrol | string |  |  | RW | 2 | → | INVERTER_CONTROL |  | Ref(56%)
698 | Inverter Parameters (Setup) | 0xABE8 | 44008 | Bearingcontrol | string |  |  | RW | 2 | → | INVERTER_CONTROL |  | Ref(60%)
699 | Inverter Parameters (Setup) | 0xABEA | 44010 | Numberofmotorscontrolledsimultaneously | U16 |  |  | RW | 1 | → |  |  | Unmapped
700 | Inverter Parameters (Setup) | 0xABEB | 44011 | Starttimeofthereversetracingintheevening (hour) | U16 | hour |  | RW | 1 | → |  |  | Unmapped
701 | Inverter Parameters (Setup) | 0xABEC | 44012 | Starttimeofthereversetracingintheevening (minute) | U16 | min |  | RW | 1 | → |  |  | Unmapped
702 | Inverter Parameters (Setup) | 0xABED | 44013 | Evening Backtracking Duration Minute | U16 | min |  | RW | 1 | → |  |  | Unmapped
703 | Inverter Parameters (Setup) | 0xABEE | 44014 | Sensorinstallationdirection | U16 |  |  | RW | 1 | → |  |  | Unmapped
704 | Inverter Parameters (Setup) | 0xABEF | 44015 | Controllertimesynchronization | U16 |  |  | RW | 1 | → |  |  | Unmapped
705 | Inverter Parameters (Setup) | 0xABF0 | 44016 | Numberofcontrolboxes | U16 |  |  | RW | 1 | → | INVERTER_CONTROL |  | Ref(56%)
706 | Inverter Parameters (Setup) | 0xAC12 | 44050 | Totalnumberofstents | U16 |  |  | RW | 1 | → |  |  | Unmapped
707 | Inverter Parameters (Setup) | 0xAC13 | 44051 | Installation Longitude | S16 | ° |  | RW | 1 | → |  |  | Unmapped
708 | Inverter Parameters (Setup) | 0xAC14 | 44052 | Installation Dimension | S16 | ° |  | RW | 1 | → | TOTAL_GENERATION_TIME_LOW |  | Ref(55%)
709 | Inverter Parameters (Setup) | 0xAC15 | 44053 | Controladdress 1 | U16 |  |  | RW | 1 | → |  |  | Unmapped
710 | Inverter Parameters (Setup) | 0xAC16 | 44054 | Controladdress 2 | U16 |  |  | RW | 1 | → |  |  | Unmapped
711 | Inverter Parameters (Setup) | 0xAC17 | 44055 | Southbound RS48 5 Check Mode | U16 |  |  | RW | 1 | → |  |  | Unmapped
712 | Inverter Parameters (Setup) | 0xAC18 | 44056 | Southbound RS48 5 baudrate | U16 |  |  | RW | 1 | → |  |  | Unmapped
713 | Inverter Parameters (Setup) | 0xAC19 | 44057 | Tiltanglecontrolupperlimit | S16 | ° |  | RW | 1 | → |  |  | Unmapped
714 | Inverter Parameters (Setup) | 0xAC1A | 44058 | Tiltanglecontrollowerlimit | S16 | ° |  | RW | 1 | → |  |  | Unmapped
715 | Inverter Parameters (Setup) | 0xAC1B | 44059 | Upperlimitofazimuthcontrol | S16 | ° |  | RW | 1 | → |  |  | Unmapped
716 | Inverter Parameters (Setup) | 0xAC1C | 44060 | Lowerlimitforazimuthcontrol | S16 | ° |  | RW | 1 | → |  |  | Unmapped
717 | Inverter Parameters (Setup) | 0xAC1D | 44061 | Sensor 1 address | U16 |  |  | RW | 1 | → |  |  | Unmapped
718 | Inverter Parameters (Setup) | 0xAC1E | 44062 | Sensor 2 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
719 | Inverter Parameters (Setup) | 0xAC1F | 44063 | Sensor 3 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
720 | Inverter Parameters (Setup) | 0xAC20 | 44064 | Sensor 4 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
721 | Inverter Parameters (Setup) | 0xAC21 | 44065 | Sensor 5 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
722 | Inverter Parameters (Setup) | 0xAC22 | 44066 | Sensor 6 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
723 | Inverter Parameters (Setup) | 0xAC23 | 44067 | Sensor 7 address | U16 |  |  | RW | 1 | → |  |  | Unmapped
724 | Inverter Parameters (Setup) | 0xAC24 | 44068 | Sensor 8 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
725 | Inverter Parameters (Setup) | 0xAC25 | 44069 | Sensor 9 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
726 | Inverter Parameters (Setup) | 0xAC26 | 44070 | Sensor 10 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
727 | Inverter Parameters (Setup) | 0xAC27 | 44071 | Sensor 11 address | U16 |  |  | RW | 1 | → |  |  | Unmapped
728 | Inverter Parameters (Setup) | 0xAC28 | 44072 | Sensor 12 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
729 | Inverter Parameters (Setup) | 0xAC29 | 44073 | Sensor 13 address | U16 |  |  | RW | 1 | → |  |  | Unmapped
730 | Inverter Parameters (Setup) | 0xAC2A | 44074 | Sensor 14 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
731 | Inverter Parameters (Setup) | 0xAC2B | 44075 | Sensor 15 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
732 | Inverter Parameters (Setup) | 0xAC2C | 44076 | Sensor 16 Address | U16 |  |  | RW | 1 | → |  |  | Unmapped
733 | Inverter Parameters (Setup) | 0xAC2D | 44077 | Trackingsystemcontroller | U16 |  |  | RW | 1 | → | INVERTER_CONTROL |  | Ref(55%)
734 | Inverter Parameters (Setup) | 0xAC2F | 44079 | Controladdress 3 | U16 |  |  | RW | 1 | → |  |  | Unmapped
735 | Inverter Parameters (Setup) | 0xAC30 | 44080 | Controladdress 4 | U16 |  |  | RW | 1 | → |  |  | Unmapped
736 | Inverter Parameters (Setup) | 0xAC31 | 44081 | Southbound RS48 5 stopbit | U16 |  |  | RW | 1 | → |  |  | Unmapped
737 | Inverter Parameters (Setup) | 0xAC32 | 44082 | Support Fault Clearance | U16 |  |  | WO | 1 | → |  |  | Unmapped
738 | Inverter Parameters (Setup) | 0xAC33 | 44083 | GPS time (localtime ): year | U16 |  |  | RW | 1 | → |  |  | Unmapped
739 | Inverter Parameters (Setup) | 0xAC39 | 44089 | windspeed | U16 | m/s |  | RW | 1 | → |  |  | Unmapped
740 | Inverter Parameters (Setup) | 0xAC3A | 44090 | Timezone | S16 | min |  | RW | 1 | → |  |  | Unmapped
741 | Inverter Parameters (Setup) | 0xAC3B | 44091 | Controladdress 5 | U16 |  |  | RW | 1 | → |  |  | Unmapped
742 | Inverter Parameters (Setup) | 0xAC3C | 44092 | Controladdress 6 | U16 |  |  | RW | 1 | → |  |  | Unmapped
743 | Inverter Parameters (Setup) | 0xAC3D | 44093 | Controladdress 7 | U16 |  |  | RW | 1 | → |  |  | Unmapped
744 | Inverter Parameters (Setup) | 0xAC3E | 44094 | Controladdress 8 | U16 |  |  | RW | 1 | → |  |  | Unmapped
745 | Inverter Parameters (Setup) | 0xAC3F | 44095 | Controladdress 9 | U16 |  |  | RW | 1 | → |  |  | Unmapped
746 | Inverter Parameters (Setup) | 0xAC40 | 44096 | Controladdress 10 | U16 |  |  | RW | 1 | → |  |  | Unmapped
747 | Inverter Parameters (Setup) | 0xAC41 | 44097 | Controladdress 11 | U16 |  |  | RW | 1 | → |  |  | Unmapped
748 | Inverter Parameters (Setup) | 0xAC42 | 44098 | Controladdress 12 | U16 |  |  | RW | 1 | → |  |  | Unmapped
749 | Inverter Parameters (Setup) | 0xAC43 | 44099 | Controladdress 13 | U16 |  |  | RW | 1 | → |  |  | Unmapped
750 | Inverter Parameters (Setup) | 0xAC44 | 44100 | Controladdress 14 | U16 |  |  | RW | 1 | → |  |  | Unmapped
751 | Inverter Parameters (Setup) | 0xAC45 | 44101 | Controladdress 15 | U16 |  |  | RW | 1 | → |  |  | Unmapped
752 | Inverter Parameters (Setup) | 0xAC46 | 44102 | Controladdress 16 | U16 |  |  | RW | 1 | → |  |  | Unmapped
753 | Inverter Parameters (Setup) | 0xAC47 | 44103 | Scienceand Technology Jingke Protocol Version | U16 |  |  | RW | 1 | → |  |  | Unmapped
754 | Inverter Parameters (Setup) | 0xAC48 | 44104 | Sensor Range | U16 | ° |  | RW | 1 | → |  |  | Unmapped
755 | Inverter Parameters (Setup) | 0xAC49 | 44105 | Controlprecision | U16 | ° |  | RW | 1 | → |  |  | Unmapped
756 | Inverter Parameters (Setup) | 0xACA8 | 44200 | KP | S16 |  |  | RW | 1 | → |  |  | Unmapped
757 | Inverter Parameters (Setup) | 0xACA9 | 44201 | KI | S16 |  |  | RW | 1 | → |  |  | Unmapped
758 | Inverter Parameters (Setup) | 0xACAA | 44202 | KD | S16 |  |  | RW | 1 | → |  |  | Unmapped
759 | Inverter Parameters (Setup) | 0xAD0C | 44300 | windspeed | U16 | m/s |  | WO | 1 | → |  |  | Unmapped
760 | Inverter Parameters (Setup) | 0xAD0D | 44301 | Winddirection | U16 | ° |  | WO | 1 | → |  |  | Unmapped
761 | Inverter Parameters (Setup) | 0xAD0E | 44302 | Startupcontrol | U16 |  |  | WO | 2 | → | INVERTER_CONTROL |  | Ref(60%)
762 | Inverter Parameters (Setup) | 0xAD10 | 44304 | Support Fault Clearance | U16 |  |  | WO | 2 | → |  |  | Unmapped
763 | Inverter Parameters (Setup) | 0xAD12 | 44306 | Stopcontrol | U16 |  |  | WO | 2 | → | INVERTER_CONTROL |  | Ref(59%)
764 | Inverter Parameters (Setup) | 0xAD78 | 44408 | Temperature 1 | S16 | °C |  | WO | 1 | → |  |  | Unmapped
765 | Inverter Parameters (Setup) | 0xAD7A | 44410 | Humidity 1 | U16 | %RH |  | WO | 1 | → |  |  | Unmapped
766 | Inverter Parameters (Setup) | 0xAFC8 | 45000 | Restorefactorysettings. | U16 |  |  | WO | 1 | → | DER_POWER_FACTOR_SET |  | Ref(57%)
767 | Inverter Parameters (Setup) | 0xAFC9 | 45001 | Clearingactivealarms | string |  |  | WO | 2 | → |  |  | Unmapped
768 | Inverter Parameters (Setup) | 0xAFCB | 45003 | Alarmsetting | string |  |  | WO | 2 | → |  |  | Unmapped
769 | Inverter Parameters (Setup) | 0xAFCD | 45005 | Alarmclearance | U16 |  |  | WO | 1 | → |  |  | Unmapped
770 | Inverter Parameters (Setup) | 0xAFCE | 45006 | Alarmmasking | U16 |  |  | WO | 1 | → |  |  | Unmapped
771 | Inverter Parameters (Setup) | 0xAFCF | 45007 | AFCI self- checkstart | U16 |  |  | WO | 1 | → |  |  | Unmapped
772 | Inverter Parameters (Setup) | 0xAFD0 | 45008 | Accumulatedenergyyieldcorrection | U32 | kWh |  | WO | 2 | → | ACCUMULATED_ENERGY |  | Ref(68%)
773 | Inverter Parameters (Setup) | 0xAFD2 | 45010 | Clearhistoricalbatterylevel. | U16 |  |  | WO | 1 | → |  |  | Unmapped
774 | Inverter Parameters (Setup) | 0xAFD3 | 45011 | Cleartherunningtimeinformation. | U16 |  |  | WO | 1 | → |  |  | Unmapped
775 | Inverter Parameters (Setup) | 0xAFD4 | 45012 | Spot Check | U16 |  |  | WO | 1 | → |  |  | Unmapped
776 | Inverter Parameters (Setup) | 0xAFD6 | 45014 | Cleartheflashmemory. | U16 |  |  | WO | 1 | → |  |  | Unmapped
777 | Inverter Parameters (Setup) | 0xAFD7 | 45015 | ESN validationcommand | U16 |  |  | WO | 1 | → | IV_SCAN_COMMAND |  | Ref(56%)
778 | Inverter Parameters (Setup) | 0xAFD8 | 45016 | Restorethedefaultpassword . | string |  |  | WO | 10 | → |  |  | Unmapped
779 | Inverter Parameters (Setup) | 0xAFE2 | 45026 | [STA ] Startscanningtheavailable WLA N list. | U16 |  |  | WO | 1 | → |  |  | Unmapped
780 | Inverter Parameters (Setup) | 0xAFE3 | 45027 | [License Interface] License Deregistration | string |  |  | WO | 10 | → |  |  | Unmapped
781 | Inverter Parameters (Setup) | 0xAFED | 45037 | Alarmportself- checkstart | U16 |  |  | WO | 1 | → |  |  | Unmapped
782 | Inverter Parameters (Setup) | 0xAFF0 | 45040 | Audibleandvisualalarmconfirmation | U16 |  |  | WO | 1 | → |  |  | Unmapped
783 | Inverter Parameters (Setup) | 0xB799 | 47001 | Box- typetransformernumber | U16 |  |  | RW | 1 | → |  |  | Unmapped
784 | Inverter Parameters (Setup) | 0xB79A | 47002 | Winding No. | U16 |  |  | RW | 1 | → |  |  | Unmapped
785 | Inverter Parameters (Setup) | 0xB79B | 47003 | Mac Ofsfet | U16 |  |  | RW | 1 | → | AC_POWER |  | Ref(56%)
786 | Inverter Parameters (Setup) | 0xB79C | 47004 | Operatingmode | U16 |  |  | RW | 1 | → | OPERATION_MODE |  | Ref(89%)
787 | Inverter Parameters (Setup) | 0xB7E7 | 47079 | Powerlimitforgrid- tiedsites | S32 | W |  | RW | 2 | → |  |  | Unmapped
788 | Inverter Parameters (Setup) | 0xB810 | 47120 | Optimizer | U16 |  |  | RW | 1 | → |  |  | Unmapped
789 | Inverter Parameters (Setup) | 0xB816 | 47126 | Single Optimizer Data Query | U16 |  |  | RW | 1 | → |  |  | Unmapped
790 | Inverter Parameters (Setup) | 0xB819 | 47129 | Alias Settings | string |  |  | WO | 11 | → |  |  | Unmapped
791 | Inverter Parameters (Setup) | 0xB824 | 47140 | Physicallocation | U16 |  |  | WO | 1 | → |  |  | Unmapped
792 | Inverter Parameters (Setup) | 0xB825 | 47141 | Importing Logs | U16 |  |  | WO | 1 | → |  |  | Unmapped
793 | Inverter Parameters (Setup) | 0xB827 | 47143 | Brokenlinedetection | U16 |  |  | WO | 1 | → |  |  | Unmapped
794 | Inverter Parameters (Setup) | 0xB828 | 47144 | Exportcompletelogs. | U16 |  |  | WO | 1 | → |  |  | Unmapped
795 | Inverter Parameters (Setup) | 0xB829 | 47145 | Settingthe Accumulated Energy Yield | MULTIDATA | 1 |  | WO | 3 | → | ACCUMULATED_ENERGY |  | Ref(68%)
796 | Inverter Parameters (Setup) | 0xB82E | 47150 | Baud Rate | U16 |  |  | RW | 1 | → |  |  | Unmapped
797 | Inverter Parameters (Setup) | 0xB82F | 47151 | Anti- crosstalk | U16 |  |  | RW | 1 | → |  |  | Unmapped
798 | Inverter Parameters (Setup) | 0xB830 | 47152 | Networkfrequencyband | U16 |  |  | RW | 1 | → | R_FREQUENCY |  | Ref(65%)
799 | Inverter Parameters (Setup) | 0xB831 | 47153 | Networking | U16 |  |  | RW | 1 | → | WORKING_MODE |  | Ref(64%)
800 | Inverter Parameters (Setup) | 0xB832 | 47154 | Packetlossratetest | U16 |  |  | RW | 1 | → |  |  | Unmapped
801 | Inverter Parameters (Setup) | 0xB834 | 47156 | Securitymode | U16 |  |  | RW | 1 | → | INVERTER_MODE |  | Ref(56%)
802 | Inverter Parameters (Setup) | 0xB835 | 47157 | Fastpower- downenable | U16 |  |  | RW | 1 | → | S_POWER_LOW |  | Ref(58%)
803 | Inverter Parameters (Setup) | 0xB836 | 47158 | Fast Shutdown Self- Test | U16 |  |  | WO | 1 | → |  |  | Unmapped
804 | Inverter Parameters (Setup) | 0xB8C4 | 47300 | Forwardpower | U16 |  |  | RW | 1 | → | AC_POWER |  | Ref(60%)
805 | Inverter Parameters (Setup) | 0xB8C5 | 47301 | Cableconnectionposition | U16 |  |  | RW | 1 | → |  |  | Unmapped
806 | Inverter Parameters (Setup) | 0xB8C6 | 47302 | CT ratedcurrent | U16 | A |  | RW | 1 | → | T_CURRENT |  | Ref(75%)
807 | Inverter Parameters (Setup) | 0xB8C7 | 47303 | Metermodel | U16 |  |  | RW | 1 | → | INVERTER_MODE |  | Ref(70%)
808 | Inverter Parameters (Setup) | 0xB8C8 | 47304 | Meteraddress | U16 |  |  | RW | 1 | → |  |  | Unmapped
809 | Inverter Parameters (Setup) | 0xB8C9 | 47305 | Metername | string |  |  | RW | 15 | → |  |  | Unmapped
810 | Inverter Parameters (Setup) | 0xB928 | 47400 | Enableautomaticaddressallocation. | U16 |  |  | RW | 1 | → |  |  | Unmapped
811 | Inverter Parameters (Setup) | 0xB929 | 47401 | Startaddressforautomaticaddressassignment | U16 |  |  | RW | 1 | → |  |  | Unmapped
812 | Inverter Parameters (Setup) | 0xB936 | 47414 | Communicationmoduleaddress | U16 |  |  | RW | 1 | → |  |  | Unmapped
813 | Inverter Parameters (Setup) | 0xB937 | 47415 | Activepowercontrolmode | U16 |  |  | RW | 1 | → | ACTIVE_POWER_PCT |  | Ref(68%)
814 | Inverter Parameters (Setup) | 0xB938 | 47416 | Maximumpowerfedtothegrid (kW) | S32 | kW |  | RW | 2 | → |  |  | Unmapped
815 | Inverter Parameters (Setup) | 0xB93A | 47418 | Maximum Feed Grid Power (%) | S16 | % |  | RW | 1 | → | GRID_R_POWER |  | Ref(57%)
816 | Inverter Parameters (Setup) | 0xB93B | 47419 | Restrictionmode | U16 |  |  | RW | 1 | → | ACTION_MODE |  | Ref(69%)
817 | Inverter Parameters (Setup) | 0xB93C | 47420 | Powerdecreaseadjustmentperiod | U16 | s |  | RW | 1 | → |  |  | Unmapped
818 | Inverter Parameters (Setup) | 0xB93D | 47421 | Maximumprotectiontime | U16 | s |  | RW | 1 | → |  |  | Unmapped
819 | Inverter Parameters (Setup) | 0xB93E | 47422 | Power Increase Threshold | U32 | kW |  | RW | 2 | → | POWER_FACTOR_SET |  | Ref(55%)
820 | Inverter Parameters (Setup) | 0xB940 | 47424 | Activepowerlimitforfailprotection [%] [lowprecision] | S16 | % |  | RW | 1 | → |  |  | Unmapped
821 | Inverter Parameters (Setup) | 0xB941 | 47425 | reactivepowercontrolmode | U16 |  |  | RW | 1 | → | REACTIVE_POWER_PCT |  | Ref(71%)
822 | Inverter Parameters (Setup) | 0xB942 | 47426 | Reactivefixedvalue | S32 | kVar |  | RW | 2 | → | REACTIVE_POWER |  | Ref(56%)
823 | Inverter Parameters (Setup) | 0xB944 | 47428 | targetpowerfactor | S16 |  |  | RW | 1 | → | POWER_FACTOR |  | Ref(76%)
824 | Inverter Parameters (Setup) | 0xB945 | 47429 | Reactivepoweradjustmentperiod | U16 | s |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(64%)
825 | Inverter Parameters (Setup) | 0xB946 | 47430 | Adjusting Dead Zone | U16 |  |  | RW | 1 | → |  |  | Unmapped
826 | Inverter Parameters (Setup) | 0xB947 | 47431 | Compensatingdelay | U16 | s |  | RW | 1 | → | OPERATION_MODE |  | Ref(58%)
827 | Inverter Parameters (Setup) | 0xB948 | 47432 | Failureprotectionreactivepowerlimit [PF] | S16 |  |  | RW | 1 | → |  |  | Unmapped
828 | Inverter Parameters (Setup) | 0xB949 | 47433 | Plantcapacity | U32 | kW |  | RW | 2 | → |  |  | Unmapped
829 | Inverter Parameters (Setup) | 0xB94B | 47435 | Powerplant DC capacity | U32 | kW |  | RW | 2 | → |  |  | Unmapped
830 | Inverter Parameters (Setup) | 0xB94D | 47437 | [Remote Output] Certificate | U16 |  |  | RW | 1 | → |  |  | Unmapped
831 | Inverter Parameters (Setup) | 0xB94E | 47438 | [Remoteoutput] PV plant ID | string |  |  | RW | 13 | → |  |  | Unmapped
832 | Inverter Parameters (Setup) | 0xB95B | 47451 | [Remoteoutput] Remoteoutputcontrolserver | string |  |  | RW | 30 | → |  |  | Unmapped
833 | Inverter Parameters (Setup) | 0xB979 | 47481 | [Remote Output] Remote Output Control Time | U16 | min |  | RW | 1 | → |  |  | Unmapped
834 | Inverter Parameters (Setup) | 0xB97A | 47482 | [Remoteoutput] Connectingtothedispatchserver | U16 |  |  | WO | 1 | → |  |  | Unmapped
835 | Inverter Parameters (Setup) | 0xB97B | 47483 | closedloopcontroller | U16 |  |  | RW | 1 | → |  |  | Unmapped
836 | Inverter Parameters (Setup) | 0xB9EA | 47594 | [Local Access] Link Enabled | U16 |  |  | RW | 1 | → |  |  | Unmapped
837 | Inverter Parameters (Setup) | 0xB9EB | 47595 | [Localaccess] Client 1 IP address | IPv4 |  |  | RW | 2 | → |  |  | Unmapped
838 | Inverter Parameters (Setup) | 0xBA3A | 47674 | Schedule Task | U16 |  |  | RW | 1 | → |  |  | Unmapped
839 | Inverter Parameters (Setup) | 0xBA3B | 47675 | Maximum Feed Grid Power Default | S32 | kW |  | RW | 2 | → |  |  | Unmapped
840 | Inverter Parameters (Setup) | 0xBA3D | 47677 | Defaultactivepowerchangegradient | U32 | %/s |  | RW | 2 | → | DEA_REACTIVE_POWER_HIGH |  | Ref(58%)
841 | Inverter Parameters (Setup) | 0xBB4E | 47950 | Feedingpowerover- thresholdprotectionshutdown | U16 | 1 |  | RW | 1 | → |  |  | Unmapped
842 | Inverter Parameters (Setup) | 0xBB4F | 47951 | Feedthreshold - crossingprotectionshutdownthreshold | S32 | 1000 |  | RW | 2 | → |  |  | Unmapped
843 | Inverter Parameters (Setup) | 0xBB51 | 47953 | Feedthreshold - crossingprotectionshutdowntime | U16 | 1 |  | RW | 1 | → |  |  | Unmapped
844 | Inverter Parameters (Setup) | 0xBB95 | 48021 | [Management System - 1] Management System Access | U16 | N/A |  | RW | 1 | → |  |  | Unmapped
845 | Inverter Parameters (Setup) | 0xBBD7 | 48087 | [Management System- 1] Protocol Type | U16 |  |  | RW | 1 | → |  |  | Unmapped
846 | Inverter Parameters (Setup) | 0xBBDA | 48090 | Groundshortcircuitprotection | U16 |  |  | RW | 1 | → |  |  | Unmapped
Mode: AI ¦ Match stats: Auto/Ref=239, Unmapped=607 ¦ Edit "Solarize_Name" for Unmapped rows (red = needs review).

## Status_Mapping
Raw_Code | Raw_Name | InverterMode_State | Solarize_Code | Notes
61 | [Re | Unknown |  | Review - could not auto-match
62 | [Re | Unknown |  | Review - could not auto-match
63 | [Re | Unknown |  | Review - could not auto-match
2 | 0: offline | Unknown |  | Review - could not auto-match
1 | standby | STANDBY | 1
NOTE: Edit "InverterMode_State" column: INITIAL/STANDBY/ON_GRID/FAULT/SHUTDOWN

## DER_AVM_Control
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x07D0 | 2000 | DER_POWER_FACTOR_SET | S16 | FC06 | 1 |  | 0.001 | RW | Power factor setpoint [-1000,-800],[800,1000]
0x07D1 | 2001 | DER_ACTION_MODE | U16 | FC06 | 1 |  | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
0x07D2 | 2002 | DER_REACTIVE_POWER_PCT | S16 | FC06 | 1 | % | 0.1 | RW | Reactive power % [-484,484]
0x07D3 | 2003 | DER_ACTIVE_POWER_PCT | U16 | FC06 | 1 | % | 0.1 | RW | Active power % [0,1100]
0x0834 | 2100 | INVERTER_ON_OFF | U16 | FC06 | 1 |  | 1 | RW | On/Off control: 0=ON, 1=OFF
0x0835 | 2101 | CLEAR_PV_INSULATION_WARNING | U16 | FC06 | 1 |  | 1 | WO | Clear PV insulation warning: 1=Clear
0x6001 | 24577 | INVERTER_CONTROL | U16 | FC06 | 1 |  | 1 | WO | Inverter control: 0=Power on, 1=Shut down
0x600D | 24589 | IV_CURVE_SCAN | U16 | FC06 | 1 |  | 1 | RW | IV curve scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
0x600F | 24591 | POWER_FACTOR_DYNAMIC | S16 | FC06 | 1 |  | 0.001 | RW | Dynamic power factor control
0x6010 | 24592 | REACTIVE_POWER_DYNAMIC | S16 | FC06 | 1 | % | 0.01 | RW | Dynamic reactive power control (%)
0x3005 | 12293 | POWER_DERATING_PCT | U16 | FC06 | 1 | % | 1 | RW | Active power derating [0-110]%
NOTE: DER-AVM control registers (always included). Do not modify addresses.

## DEA_AVM_Monitor
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x03E8 | 1000 | DEA_L1_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L1 current (low word)
0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 current (high word)
0x03EA | 1002 | DEA_L2_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L2 current (low word)
0x03EB | 1003 | DEA_L2_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 current (high word)
0x03EC | 1004 | DEA_L3_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L3 current (low word)
0x03ED | 1005 | DEA_L3_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 current (high word)
0x03EE | 1006 | DEA_L1_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L1 voltage (low word)
0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 voltage (high word)
0x03F0 | 1008 | DEA_L2_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L2 voltage (low word)
0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 voltage (high word)
0x03F2 | 1010 | DEA_L3_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L3 voltage (low word)
0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 voltage (high word)
0x03F4 | 1012 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | FC03 | 2 | kW | 0.1 | RO | DEA total active power (low word)
0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total active power (high word)
0x03F6 | 1014 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | FC03 | 2 | Var | 1 | RO | DEA total reactive power (low word)
0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total reactive power (high word)
0x03F8 | 1016 | DEA_POWER_FACTOR_LOW | S32 | FC03 | 2 |  | 0.001 | RO | DEA power factor (low word)
0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | S32 | FC03 | 1 |  |  | RO | DEA power factor (high word)
0x03FA | 1018 | DEA_FREQUENCY_LOW | S32 | FC03 | 2 | Hz | 0.1 | RO | DEA frequency (low word)
0x03FB | 1019 | DEA_FREQUENCY_HIGH | S32 | FC03 | 1 |  |  | RO | DEA frequency (high word)
0x03FC | 1020 | DEA_STATUS_FLAG_LOW | S32 | FC03 | 2 |  | 1 | RO | DEA status flag (low word)
0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | S32 | FC03 | 1 |  |  | RO | DEA status flag (high word)
NOTE: DEA-AVM monitoring registers (always included). Do not modify addresses.