## Registers
No | Section | Address_Hex | Address_Dec | Definition | Data_Type | FC_Code | Registers | Unit | Scale_Factor | R/W | Description
--- DEA-AVM Realtime Data ---
1 | DEA-AVM Realtime Data | 0x03E8 | 1000 | L1 Current |  | FC03 | 1 |  |  | RO
2 | DEA-AVM Realtime Data | 0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | U16 | FC03 | 1 |  |  | RO
3 | DEA-AVM Realtime Data | 0x03EA | 1002 | L2 Current | S32 | FC03 | 2 | 0.1A | 0.1 | RO | 2 ¦ RO
4 | DEA-AVM Realtime Data | 0x03EA | 1002 | L2 Current | S32 | FC03 | 2 | 0.1A | 0.1 | RO
5 | DEA-AVM Realtime Data | 0x03EB | 1003 | DEA_L2_CURRENT_HIGH | U16 | FC03 | 1 |  |  | RO
6 | DEA-AVM Realtime Data | 0x03EC | 1004 | L3 Current |  | FC03 | 1 |  |  | RO
7 | DEA-AVM Realtime Data | 0x03ED | 1005 | DEA_L3_CURRENT_HIGH | U16 | FC03 | 1 |  |  | RO
8 | DEA-AVM Realtime Data | 0x03EE | 1006 | L1 Voltage |  | FC03 | 1 |  |  | RO
9 | DEA-AVM Realtime Data | 0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | U16 | FC03 | 1 |  |  | RO
10 | DEA-AVM Realtime Data | 0x03F0 | 1008 | L2 Voltage |  | FC03 | 1 |  |  | RO
11 | DEA-AVM Realtime Data | 0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | U16 | FC03 | 1 |  |  | RO
12 | DEA-AVM Realtime Data | 0x03F2 | 1010 | L3 Voltage |  | FC03 | 1 |  |  | RO
13 | DEA-AVM Realtime Data | 0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | U16 | FC03 | 1 |  |  | RO
14 | DEA-AVM Realtime Data | 0x03F4 | 1012 | Grid total Active Power |  | FC03 | 1 |  |  | RO
15 | DEA-AVM Realtime Data | 0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
16 | DEA-AVM Realtime Data | 0x03F6 | 1014 | Grid total Reactive Power |  | FC03 | 1 |  |  | RO
17 | DEA-AVM Realtime Data | 0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
18 | DEA-AVM Realtime Data | 0x03F8 | 1016 | Power Factor |  | FC03 | 1 |  |  | RO
19 | DEA-AVM Realtime Data | 0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | U16 | FC03 | 1 |  |  | RO
20 | DEA-AVM Realtime Data | 0x03FA | 1018 | Frequency |  | FC03 | 1 |  |  | RO
21 | DEA-AVM Realtime Data | 0x03FB | 1019 | DEA_FREQUENCY_HIGH | U16 | FC03 | 1 |  |  | RO
22 | DEA-AVM Realtime Data | 0x03FC | 1020 | Status Flag 1 |  | FC03 | 1 |  |  | RO
--- DER-AVM Parameters ---
23 | DER-AVM Parameters | 0x03FC | 1020 | PV8 fuse open check mask, [0,1] |  | FC03 | 1 |  |  | RO | 0:Enable , 1: Disable ¦ Reference document ¦ APD PV inverter Modbus communication protocol V4.25.xlsx ¦ Bit ¦ Description
--- DEA-AVM Realtime Data ---
24 | DEA-AVM Realtime Data | 0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | U16 | FC03 | 1 |  |  | RO
--- DER-AVM Parameters ---
25 | DER-AVM Parameters | 0x07D0 | 2000 | Power factor setting | S16 | FC03/FC06 | 1 | 0.001 |  | RW | [-1000, -800], [800, ¦ 1000] ¦ Default 1000
26 | DER-AVM Parameters | 0x07D1 | 2001 | Action mode |  | FC03 | 1 |  |  | RO
27 | DER-AVM Parameters | 0x07D2 | 2002 | Reactive power percent |  | FC03 | 1 |  |  | RO | setting
28 | DER-AVM Parameters | 0x07D3 | 2003 | Active power percent setting |  | FC03 | 1 |  |  | RO
29 | DER-AVM Parameters | 0x0834 | 2100 | Inverter off |  | FC03 | 1 |  |  | RO
30 | DER-AVM Parameters | 0x0835 | 2101 | Clear PV insulation warning |  | FC03 | 1 |  |  | RO
--- Inverter Realtime Data ---
31 | Inverter Realtime Data | 0x1001 | 4097 | L1 Voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
32 | Inverter Realtime Data | 0x1002 | 4098 | L1 Current |  | FC03 | 1 |  |  | RO
33 | Inverter Realtime Data | 0x1003 | 4099 | L1 Power |  | FC03 | 1 |  |  | RO
34 | Inverter Realtime Data | 0x1004 | 4100 | L1_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
35 | Inverter Realtime Data | 0x1005 | 4101 | L1 Frequency |  | FC03 | 1 |  |  | RO
36 | Inverter Realtime Data | 0x1006 | 4102 | L2 Voltage |  | FC03 | 1 |  |  | RO
37 | Inverter Realtime Data | 0x1007 | 4103 | L2 Current |  | FC03 | 1 |  |  | RO
38 | Inverter Realtime Data | 0x1008 | 4104 | L2 Power |  | FC03 | 1 |  |  | RO
39 | Inverter Realtime Data | 0x1009 | 4105 | L2_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
40 | Inverter Realtime Data | 0x100A | 4106 | L2 Frequency |  | FC03 | 1 |  |  | RO
41 | Inverter Realtime Data | 0x100B | 4107 | L3 Voltage |  | FC03 | 1 |  |  | RO
42 | Inverter Realtime Data | 0x100C | 4108 | L3 Current |  | FC03 | 1 |  |  | RO
43 | Inverter Realtime Data | 0x100D | 4109 | L3 Power |  | FC03 | 1 |  |  | RO
44 | Inverter Realtime Data | 0x100E | 4110 | L3_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
45 | Inverter Realtime Data | 0x100F | 4111 | L3 Frequency |  | FC03 | 1 |  |  | RO
46 | Inverter Realtime Data | 0x1010 | 4112 | MPPT1 Voltage |  | FC03 | 1 |  |  | RO
47 | Inverter Realtime Data | 0x1011 | 4113 | MPPT1 Current |  | FC03 | 1 |  |  | RO
48 | Inverter Realtime Data | 0x1012 | 4114 | MPPT1 Power |  | FC03 | 1 |  |  | RO
49 | Inverter Realtime Data | 0x1013 | 4115 | MPPT1_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
50 | Inverter Realtime Data | 0x1014 | 4116 | MPPT2 Voltage |  | FC03 | 1 |  |  | RO
51 | Inverter Realtime Data | 0x1015 | 4117 | MPPT2 Current |  | FC03 | 1 |  |  | RO
52 | Inverter Realtime Data | 0x1016 | 4118 | MPPT2 Power |  | FC03 | 1 |  |  | RO
53 | Inverter Realtime Data | 0x1017 | 4119 | MPPT2_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
54 | Inverter Realtime Data | 0x1018 | 4120 | MPPT3 Voltage |  | FC03 | 1 |  |  | RO
55 | Inverter Realtime Data | 0x1019 | 4121 | MPPT3 Current |  | FC03 | 1 |  |  | RO
56 | Inverter Realtime Data | 0x101A | 4122 | MPPT3 Power |  | FC03 | 1 |  |  | RO
57 | Inverter Realtime Data | 0x101B | 4123 | MPPT3_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
58 | Inverter Realtime Data | 0x101C | 4124 | Inner Temperature |  | FC03 | 1 |  |  | RO
59 | Inverter Realtime Data | 0x101D | 4125 | Inverter Mode |  | FC03 | 1 |  |  | RO
--- DER-AVM Parameters ---
60 | DER-AVM Parameters | 0x101D | 4125 | PV8 fuse open data, [0,1] |  | FC03 | 1 |  |  | RO | 0:normal , 1: Fuse open ¦ No. ¦ Description ¦ 0x00 ¦ Initial mode ¦ 0x01 ¦ Standby mode ¦ 0x03 ¦ On-Grid mode ¦ 0x04 ¦ Off-Grid mode ¦ 0x05 ¦ Fault mode
--- Inverter Realtime Data ---
61 | Inverter Realtime Data | 0x101E | 4126 | Error Code1 |  | FC03 | 1 |  |  | RO
62 | Inverter Realtime Data | 0x101F | 4127 | Error Code2 |  | FC03 | 1 |  |  | RO
--- DER-AVM Parameters ---
63 | DER-AVM Parameters | 0x101F | 4127 | Boost abnormal |  | FC03 | 1 |  |  | RO | Bit ¦ No ¦ Description
--- Inverter Realtime Data ---
64 | Inverter Realtime Data | 0x1020 | 4128 | Error Code3 |  | FC03 | 1 |  |  | RO
--- DER-AVM Parameters ---
65 | DER-AVM Parameters | 0x1020 | 4128 | AC moving average voltage high |  | FC03 | 15 |  |  | RO | Bit ¦ No ¦ Description
66 | DER-AVM Parameters | 0x1020 | 4128 | AC moving average voltage high |  | FC03 | 1 |  |  | RO | Bit ¦ No ¦ Description
--- Inverter Realtime Data ---
67 | Inverter Realtime Data | 0x1021 | 4129 | Total Energy |  | FC03 | 1 |  |  | RO
68 | Inverter Realtime Data | 0x1021 | 4129 | energy is 220.836kWh, | U16 | FC03 | 1 | Wh |  | RO | then 0x104C is 836Wh
69 | Inverter Realtime Data | 0x1022 | 4130 | TOTAL_ENERGY_HIGH | U16 | FC03 | 1 |  |  | RO
70 | Inverter Realtime Data | 0x1023 | 4131 | Total generation time |  | FC03 | 1 |  |  | RO
71 | Inverter Realtime Data | 0x1024 | 4132 | TOTAL_GENERATION_TIME_HIGH | U16 | FC03 | 1 |  |  | RO
72 | Inverter Realtime Data | 0x1027 | 4135 | Today Energy |  | FC03 | 1 |  |  | RO
73 | Inverter Realtime Data | 0x1028 | 4136 | TODAY_ENERGY_HIGH | U16 | FC03 | 1 |  |  | RO
74 | Inverter Realtime Data | 0x1034 | 4148 | Fuse open data |  | FC03 | 1 |  |  | RO
75 | Inverter Realtime Data | 0x1037 | 4151 | Grid total Active Power |  | FC03 | 1 |  |  | RO
76 | Inverter Realtime Data | 0x1038 | 4152 | GRID_TOTAL_ACTIVE_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
77 | Inverter Realtime Data | 0x1039 | 4153 | Grid total Reactive Power |  | FC03 | 1 |  |  | RO
78 | Inverter Realtime Data | 0x103A | 4154 | GRID_TOTAL_REACTIVE_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
79 | Inverter Realtime Data | 0x103B | 4155 | PV Today Peak Power |  | FC03 | 1 |  |  | RO
80 | Inverter Realtime Data | 0x103D | 4157 | Power Factor |  | FC03 | 1 |  |  | RO
81 | Inverter Realtime Data | 0x103E | 4158 | MPPT4 Voltage |  | FC03 | 1 |  |  | RO
82 | Inverter Realtime Data | 0x103F | 4159 | MPPT4 Current |  | FC03 | 1 |  |  | RO
83 | Inverter Realtime Data | 0x1040 | 4160 | MPPT4 Power |  | FC03 | 1 |  |  | RO
84 | Inverter Realtime Data | 0x1041 | 4161 | MPPT4_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
85 | Inverter Realtime Data | 0x1048 | 4168 | PV total input power |  | FC03 | 1 |  |  | RO
86 | Inverter Realtime Data | 0x1049 | 4169 | PV_TOTAL_INPUT_POWER_HIGH | U16 | FC03 | 1 |  |  | RO
87 | Inverter Realtime Data | 0x104C | 4172 | Decimals of total energy |  | FC03 | 1 |  |  | RO
88 | Inverter Realtime Data | 0x1050 | 4176 | String1 input voltage |  | FC03 | 1 |  |  | RO
89 | Inverter Realtime Data | 0x1051 | 4177 | String1 input current |  | FC03 | 1 |  |  | RO
90 | Inverter Realtime Data | 0x1052 | 4178 | String2 input voltage |  | FC03 | 1 |  |  | RO
91 | Inverter Realtime Data | 0x1053 | 4179 | String2 input current |  | FC03 | 1 |  |  | RO
92 | Inverter Realtime Data | 0x1054 | 4180 | String3 input voltage |  | FC03 | 1 |  |  | RO
93 | Inverter Realtime Data | 0x1055 | 4181 | String3 input current |  | FC03 | 1 |  |  | RO
94 | Inverter Realtime Data | 0x1056 | 4182 | String4 input voltage |  | FC03 | 1 |  |  | RO
95 | Inverter Realtime Data | 0x1057 | 4183 | String4 input current |  | FC03 | 1 |  |  | RO
96 | Inverter Realtime Data | 0x1058 | 4184 | String5 input voltage |  | FC03 | 1 |  |  | RO
97 | Inverter Realtime Data | 0x1059 | 4185 | String5 input current |  | FC03 | 1 |  |  | RO
98 | Inverter Realtime Data | 0x105A | 4186 | String6 input voltage |  | FC03 | 1 |  |  | RO
99 | Inverter Realtime Data | 0x105B | 4187 | String6 input current |  | FC03 | 1 |  |  | RO
100 | Inverter Realtime Data | 0x105C | 4188 | String7 input voltage |  | FC03 | 1 |  |  | RO
101 | Inverter Realtime Data | 0x105D | 4189 | String7 input current |  | FC03 | 1 |  |  | RO
102 | Inverter Realtime Data | 0x105E | 4190 | String8 input voltage |  | FC03 | 1 |  |  | RO
103 | Inverter Realtime Data | 0x105F | 4191 | String8 input current |  | FC03 | 1 |  |  | RO
104 | Inverter Realtime Data | 0x1060 | 4192 | String9 input voltage |  | FC03 | 1 |  |  | RO
105 | Inverter Realtime Data | 0x1061 | 4193 | String9 input current |  | FC03 | 1 |  |  | RO
106 | Inverter Realtime Data | 0x1062 | 4194 | String10 input voltage |  | FC03 | 1 |  |  | RO
107 | Inverter Realtime Data | 0x1063 | 4195 | String10 input current |  | FC03 | 1 |  |  | RO
108 | Inverter Realtime Data | 0x1064 | 4196 | String11 input voltage |  | FC03 | 1 |  |  | RO
109 | Inverter Realtime Data | 0x1065 | 4197 | String11 input current |  | FC03 | 1 |  |  | RO
110 | Inverter Realtime Data | 0x1066 | 4198 | String12 input voltage |  | FC03 | 1 |  |  | RO
111 | Inverter Realtime Data | 0x1067 | 4199 | String12 input current |  | FC03 | 1 |  |  | RO
112 | Inverter Realtime Data | 0x1068 | 4200 | String13 input voltage |  | FC03 | 1 |  |  | RO
113 | Inverter Realtime Data | 0x1069 | 4201 | String13 input current |  | FC03 | 1 |  |  | RO
114 | Inverter Realtime Data | 0x106A | 4202 | String14 input voltage |  | FC03 | 1 |  |  | RO
115 | Inverter Realtime Data | 0x106B | 4203 | String14 input current |  | FC03 | 1 |  |  | RO
116 | Inverter Realtime Data | 0x106C | 4204 | String15 input voltage |  | FC03 | 1 |  |  | RO
117 | Inverter Realtime Data | 0x106D | 4205 | String15 input current |  | FC03 | 1 |  |  | RO
118 | Inverter Realtime Data | 0x106E | 4206 | String16 input voltage |  | FC03 | 1 |  |  | RO
119 | Inverter Realtime Data | 0x106F | 4207 | String16 input current |  | FC03 | 1 |  |  | RO
120 | Inverter Realtime Data | 0x1070 | 4208 | String17 input voltage |  | FC03 | 1 |  |  | RO
121 | Inverter Realtime Data | 0x1071 | 4209 | String17 input current |  | FC03 | 1 |  |  | RO
122 | Inverter Realtime Data | 0x1072 | 4210 | String18 input voltage |  | FC03 | 1 |  |  | RO
123 | Inverter Realtime Data | 0x1073 | 4211 | String18 input current |  | FC03 | 1 |  |  | RO
124 | Inverter Realtime Data | 0x1074 | 4212 | String19 input voltage |  | FC03 | 1 |  |  | RO
125 | Inverter Realtime Data | 0x1075 | 4213 | String19 input current |  | FC03 | 1 |  |  | RO
126 | Inverter Realtime Data | 0x1076 | 4214 | String20 input voltage |  | FC03 | 1 |  |  | RO
127 | Inverter Realtime Data | 0x1077 | 4215 | String20 input current |  | FC03 | 1 |  |  | RO
128 | Inverter Realtime Data | 0x1078 | 4216 | String21 input voltage |  | FC03 | 1 |  |  | RO
129 | Inverter Realtime Data | 0x1079 | 4217 | String21 input current |  | FC03 | 1 |  |  | RO
130 | Inverter Realtime Data | 0x107A | 4218 | String22 input voltage |  | FC03 | 1 |  |  | RO
131 | Inverter Realtime Data | 0x107B | 4219 | String22 input current |  | FC03 | 1 |  |  | RO
132 | Inverter Realtime Data | 0x107C | 4220 | String23 input voltage |  | FC03 | 1 |  |  | RO
133 | Inverter Realtime Data | 0x107D | 4221 | String23 input current |  | FC03 | 1 |  |  | RO
134 | Inverter Realtime Data | 0x107E | 4222 | String24 input voltage |  | FC03 | 1 |  |  | RO
135 | Inverter Realtime Data | 0x107F | 4223 | String24 input current |  | FC03 | 1 |  |  | RO
136 | Inverter Realtime Data | 0x1080 | 4224 | MPPT5 Voltage |  | FC03 | 1 |  |  | RO
137 | Inverter Realtime Data | 0x1081 | 4225 | MPPT5 Current |  | FC03 | 1 |  |  | RO
138 | Inverter Realtime Data | 0x1082 | 4226 | MPPT5 Power |  | FC03 | 1 |  |  | RO
139 | Inverter Realtime Data | 0x1084 | 4228 | MPPT6 Voltage |  | FC03 | 1 |  |  | RO
140 | Inverter Realtime Data | 0x1085 | 4229 | MPPT6 Current |  | FC03 | 1 |  |  | RO
141 | Inverter Realtime Data | 0x1086 | 4230 | MPPT6 Power |  | FC03 | 1 |  |  | RO
142 | Inverter Realtime Data | 0x1088 | 4232 | MPPT7 Voltage |  | FC03 | 1 |  |  | RO
143 | Inverter Realtime Data | 0x1089 | 4233 | MPPT7 Current |  | FC03 | 1 |  |  | RO
144 | Inverter Realtime Data | 0x108A | 4234 | MPPT7 Power |  | FC03 | 1 |  |  | RO
145 | Inverter Realtime Data | 0x108C | 4236 | MPPT8 Voltage |  | FC03 | 1 |  |  | RO
146 | Inverter Realtime Data | 0x108D | 4237 | MPPT8 Current |  | FC03 | 1 |  |  | RO
147 | Inverter Realtime Data | 0x108E | 4238 | MPPT8 Power |  | FC03 | 1 |  |  | RO
148 | Inverter Realtime Data | 0x1090 | 4240 | MPPT9 Voltage |  | FC03 | 1 |  |  | RO
149 | Inverter Realtime Data | 0x1091 | 4241 | MPPT9 Current |  | FC03 | 1 |  |  | RO
150 | Inverter Realtime Data | 0x1092 | 4242 | MPPT9 Power |  | FC03 | 1 |  |  | RO
151 | Inverter Realtime Data | 0x120C | 4620 | External fan speed duty |  | FC03 | 1 |  |  | RO | percentage
152 | Inverter Realtime Data | 0x1210 | 4624 | DER_AVM_METER_STATUS | U16 | FC03 | 1 |  |  | RO | U16, 0=disconnected, 1=connected
--- Inverter Parameters ---
153 | Inverter Parameters | 0x1211 | 4625 | DER_AVM_MODE | U16 | FC03/FC06 | 1 |  |  | RW | U16, 0=self control, 1=DER-AVM control
--- Inverter Realtime Data ---
154 | Inverter Realtime Data | 0x1226 | 4646 | Q (Reference Output reactive |  | FC03 | 1 |  |  | RO | power)
--- Inverter Parameters ---
155 | Inverter Parameters | 0x1240 | 4672 | RS485-2 Modbus address |  | FC03 | 1 |  |  | RO
156 | Inverter Parameters | 0x1241 | 4673 | RS485-2 UART baud rate |  | FC03 | 1 |  |  | RO
157 | Inverter Parameters | 0x1242 | 4674 | RS485-2 terminal resistance |  | FC03 | 1 |  |  | RO | control
158 | Inverter Parameters | 0x1243 | 4675 | RS485-3 Modbus address |  | FC03 | 1 |  |  | RO
159 | Inverter Parameters | 0x1244 | 4676 | RS485-3 UART baud rate |  | FC03 | 1 |  |  | RO
160 | Inverter Parameters | 0x1245 | 4677 | RS485-3 terminal resistance |  | FC03 | 1 |  |  | RO | control
--- Inverter Realtime Data ---
161 | Inverter Realtime Data | 0x1300 | 4864 | L1 watt of grid |  | FC03 | 1 |  |  | RO
162 | Inverter Realtime Data | 0x1302 | 4866 | L2 watt of grid |  | FC03 | 1 |  |  | RO
163 | Inverter Realtime Data | 0x1304 | 4868 | L3 watt of grid |  | FC03 | 1 |  |  | RO
164 | Inverter Realtime Data | 0x1306 | 4870 | Accumulated energy of |  | FC03 | 1 |  |  | RO | import
165 | Inverter Realtime Data | 0x1308 | 4872 | Accumulated energy of |  | FC03 | 1 |  |  | RO | export
166 | Inverter Realtime Data | 0x130A | 4874 | L1 watt of load |  | FC03 | 1 |  |  | RO
167 | Inverter Realtime Data | 0x130C | 4876 | L2 watt of load |  | FC03 | 1 |  |  | RO
168 | Inverter Realtime Data | 0x130E | 4878 | L3 watt of load |  | FC03 | 1 |  |  | RO
169 | Inverter Realtime Data | 0x1310 | 4880 | Accumulated energy of load |  | FC03 | 1 |  |  | RO
170 | Inverter Realtime Data | 0x131A | 4890 | L1-N phase voltage of grid |  | FC03 | 1 |  |  | RO
171 | Inverter Realtime Data | 0x131B | 4891 | L2-N phase voltage of grid |  | FC03 | 1 |  |  | RO
172 | Inverter Realtime Data | 0x131C | 4892 | L3-N phase voltage of grid |  | FC03 | 1 |  |  | RO
173 | Inverter Realtime Data | 0x131D | 4893 | L1 current of grid |  | FC03 | 1 |  |  | RO
174 | Inverter Realtime Data | 0x131F | 4895 | L2 current of grid |  | FC03 | 1 |  |  | RO
175 | Inverter Realtime Data | 0x1321 | 4897 | L3 current of grid |  | FC03 | 1 |  |  | RO
176 | Inverter Realtime Data | 0x1323 | 4899 | L1-N phase voltage of load |  | FC03 | 1 |  |  | RO
177 | Inverter Realtime Data | 0x1324 | 4900 | L2-N phase voltage of load |  | FC03 | 1 |  |  | RO
178 | Inverter Realtime Data | 0x1325 | 4901 | L3-N phase voltage of load |  | FC03 | 1 |  |  | RO
179 | Inverter Realtime Data | 0x1326 | 4902 | L1 current of load |  | FC03 | 1 |  |  | RO
180 | Inverter Realtime Data | 0x1328 | 4904 | L2 current of load |  | FC03 | 1 |  |  | RO
181 | Inverter Realtime Data | 0x132A | 4906 | L3 current of load |  | FC03 | 1 |  |  | RO
182 | Inverter Realtime Data | 0x1332 | 4914 | Today import Energy |  | FC03 | 1 |  |  | RO
183 | Inverter Realtime Data | 0x1334 | 4916 | Today export Energy |  | FC03 | 1 |  |  | RO
184 | Inverter Realtime Data | 0x1336 | 4918 | Today load Energy |  | FC03 | 1 |  |  | RO
185 | Inverter Realtime Data | 0x1338 | 4920 | Frequency of grid |  | FC03 | 1 |  |  | RO
--- Device Information ---
186 | Device Information | 0x1A00 | 6656 | Device Model name |  | FC03 | 1 |  |  | RO
187 | Device Information | 0x1A10 | 6672 | Device Serial number |  | FC03 | 1 |  |  | RO
188 | Device Information | 0x1A1C | 6684 | Master firmware version |  | FC03 | 3 | ASCII |  | RO | string Ex.：123456
189 | Device Information | 0x1A26 | 6694 | Slave firmware version |  | FC03 | 1 |  |  | RO
190 | Device Information | 0x1A3B | 6715 | MPPT Number |  | FC03 | 1 |  |  | RO
191 | Device Information | 0x1A44 | 6724 | Nominal Voltage |  | FC03 | 1 |  |  | RO
--- Inverter Parameters ---
192 | Inverter Parameters | 0x1A44 | 6724 | Nominal voltage |  | FC03 | 1 |  |  | RO
--- Device Information ---
193 | Device Information | 0x1A45 | 6725 | Nominal Frequency |  | FC03 | 1 |  |  | RO
194 | Device Information | 0x1A46 | 6726 | Nominal Active Power |  | FC03 | 1 |  |  | RO | (Low word)
195 | Device Information | 0x1A48 | 6728 | Grid Phase Number |  | FC03 | 1 |  |  | RO
196 | Device Information | 0x1A4E | 6734 | Nominal Active Power |  | FC03 | 1 |  |  | RO | (High word)
197 | Device Information | 0x1A60 | 6752 | EMS Firmware Version |  | FC03 | 1 |  |  | RO
198 | Device Information | 0x1A8E | 6798 | LCD firmware version |  | FC03 | 1 |  |  | RO
--- Inverter Parameters ---
199 | Inverter Parameters | 0x3000 | 12288 | Date：Year |  | FC03 | 1 |  |  | RO
200 | Inverter Parameters | 0x3001 | 12289 | Date：Month + Day |  | FC03 | 1 |  |  | RO
201 | Inverter Parameters | 0x3002 | 12290 | Date：Hour + Minute |  | FC03 | 1 |  |  | RO
202 | Inverter Parameters | 0x3003 | 12291 | Date：Second + 0 |  | FC03 | 1 |  |  | RO
203 | Inverter Parameters | 0x3005 | 12293 | Power derating percent by |  | FC03 | 1 |  |  | RO
204 | Inverter Parameters | 0x303E | 12350 | RS485-1 Modbus Address |  | FC03 | 1 |  |  | RO
205 | Inverter Parameters | 0x304C | 12364 | RS485-1 baud rate |  | FC03 | 1 |  |  | RO
206 | Inverter Parameters | 0x3060 | 12384 | WIFI STA SSID | string | FC03/FC06 | 16 | ASCII |  | RW
207 | Inverter Parameters | 0x3070 | 12400 | WIFI STA password |  | FC03 | 1 |  |  | RO
208 | Inverter Parameters | 0x30B0 | 12464 | Digital meter Modbus address |  | FC03 | 1 |  |  | RO
209 | Inverter Parameters | 0x30B1 | 12465 | Digital meter Type |  | FC03 | 1 |  |  | RO
210 | Inverter Parameters | 0x30B2 | 12466 | Power flow direction |  | FC03 | 1 |  |  | RO
211 | Inverter Parameters | 0x30B3 | 12467 | Power limit function |  | FC03 | 1 |  |  | RO
212 | Inverter Parameters | 0x30B4 | 12468 | Power limit CT ratio |  | FC03 | 1 |  |  | RO
213 | Inverter Parameters | 0x30B5 | 12469 | Meter location |  | FC03 | 1 |  |  | RO
214 | Inverter Parameters | 0x30B9 | 12473 | Maximum feed in grid power |  | FC03 | 1 |  |  | RO
215 | Inverter Parameters | 0x5000 | 20480 | First connect start time |  | FC03 | 1 |  |  | RO
216 | Inverter Parameters | 0x5001 | 20481 | Reconnect time |  | FC03 | 1 |  |  | RO
217 | Inverter Parameters | 0x5002 | 20482 | Grid frequency high loss level |  | FC03 | 1 |  |  | RO | 1 limit
218 | Inverter Parameters | 0x5003 | 20483 | Grid frequency low loss level 1 |  | FC03 | 1 |  |  | RO | limit
219 | Inverter Parameters | 0x5004 | 20484 | Grid voltage high loss level 1 |  | FC03 | 1 |  |  | RO | limit
220 | Inverter Parameters | 0x5005 | 20485 | Grid voltage low loss level 1 |  | FC03 | 1 |  |  | RO | limit
221 | Inverter Parameters | 0x5006 | 20486 | Grid frequency high loss level |  | FC03 | 1 |  |  | RO | 1 trip time
222 | Inverter Parameters | 0x5007 | 20487 | Grid frequency low loss level 1 |  | FC03 | 1 |  |  | RO | trip time
223 | Inverter Parameters | 0x5008 | 20488 | Grid voltage high loss level 1 |  | FC03 | 1 |  |  | RO | trip time
224 | Inverter Parameters | 0x5009 | 20489 | Grid voltage low loss level 1 |  | FC03 | 1 |  |  | RO | trip time
225 | Inverter Parameters | 0x500A | 20490 | Grid frequency high loss level |  | FC03 | 1 |  |  | RO | 2 limit
226 | Inverter Parameters | 0x500B | 20491 | Grid frequency low loss level 2 |  | FC03 | 1 |  |  | RO | limit
227 | Inverter Parameters | 0x500C | 20492 | Grid voltage high loss level 2 |  | FC03 | 1 |  |  | RO | limit
228 | Inverter Parameters | 0x500D | 20493 | Grid voltage low loss level 2 |  | FC03 | 1 |  |  | RO | limit
229 | Inverter Parameters | 0x500E | 20494 | Grid frequency high loss level |  | FC03 | 1 |  |  | RO | 2 trip time
230 | Inverter Parameters | 0x500F | 20495 | Grid frequency low loss level 2 |  | FC03 | 1 |  |  | RO | trip time
231 | Inverter Parameters | 0x5010 | 20496 | Grid voltage high loss level 2 |  | FC03 | 1 |  |  | RO | trip time
232 | Inverter Parameters | 0x5011 | 20497 | Grid voltage low loss level 2 |  | FC03 | 1 |  |  | RO | trip time
233 | Inverter Parameters | 0x5012 | 20498 | Grid Frequency High Level 1 |  | FC03 | 1 |  |  | RO | back
234 | Inverter Parameters | 0x5013 | 20499 | Grid Frequency Low Level 1 |  | FC03 | 1 |  |  | RO | back
235 | Inverter Parameters | 0x5018 | 20504 | 10 min average sustained |  | FC03 | 1 |  |  | RO | voltage
236 | Inverter Parameters | 0x5019 | 20505 | Reconnect soft output power |  | FC03 | 1 |  |  | RO | percent
237 | Inverter Parameters | 0x501A | 20506 | Over frequency power |  | FC03 | 1 |  |  | RO | reduction droop
238 | Inverter Parameters | 0x501B | 20507 | Insulation resistance active |  | FC03 | 1 |  |  | RO | limit
239 | Inverter Parameters | 0x501E | 20510 | Grid over voltage de-rating |  | FC03 | 1 |  |  | RO | point
240 | Inverter Parameters | 0x501E | 20510 | [0, 1] | U16 | FC03/FC06 | 1 |  |  | RW | 0: disable,1: enable
241 | Inverter Parameters | 0x501F | 20511 | Grid frequency high Level 1 |  | FC03 | 1 |  |  | RO | trip time (High word)
242 | Inverter Parameters | 0x5020 | 20512 | Grid frequency low Level 1 trip |  | FC03 | 1 |  |  | RO | time (High word)
243 | Inverter Parameters | 0x5021 | 20513 | Grid over frequency de-rating |  | FC03 | 1 |  |  | RO | start point
244 | Inverter Parameters | 0x5022 | 20514 | Grid over frequency de-rating |  | FC03 | 1 |  |  | RO | end point
245 | Inverter Parameters | 0x5025 | 20517 | Grid Voltage High Level 1 trip |  | FC03 | 1 |  |  | RO | time (High word)
246 | Inverter Parameters | 0x5026 | 20518 | Grid Voltage Low Level 1 trip |  | FC03 | 1 |  |  | RO | time (High word)
247 | Inverter Parameters | 0x5027 | 20519 | Grid Voltage High Level 1 |  | FC03 | 1 |  |  | RO
248 | Inverter Parameters | 0x5028 | 20520 | Grid Voltage Low Level 1 back |  | FC03 | 1 |  |  | RO
249 | Inverter Parameters | 0x5029 | 20521 | First connect soft start output |  | FC03 | 1 |  |  | RO | power percent
250 | Inverter Parameters | 0x5030 | 20528 | Output reactive power mode |  | FC03 | 1 |  |  | RO
251 | Inverter Parameters | 0x5031 | 20529 | [0,9] | U16 | FC03/FC06 | 1 |  |  | RW | 0: Pure active power ¦ 1: cosφ = const. relation ¦ 2: Q = const. relation with ¦ [0x5032] ¦ [0x5114] ¦ 3: cosφ(P), relation with ¦ [0x5034~0x503B], ¦ [0x5045,0x5046 CEI-021 ¦ only] ¦ 4: Q(U), relation with ¦ [0x503C~0x5044], ¦ [0x5047,0x5048 CEI-021
252 | Inverter Parameters | 0x5031 | 20529 | Power factor setting |  | FC03 | 1 |  |  | RO
253 | Inverter Parameters | 0x5033 | 20531 | Reactive control response |  | FC03 | 1 |  |  | RO | time
254 | Inverter Parameters | 0x503C | 20540 | Q(U) curve node1 |  | FC03 | 1 |  |  | RO | percent(U/Un)
255 | Inverter Parameters | 0x503D | 20541 | Q(U) curve node2 |  | FC03 | 1 |  |  | RO | percent(U/Un)
256 | Inverter Parameters | 0x503E | 20542 | Q(U) curve node3 |  | FC03 | 1 |  |  | RO | percent(U/Un)
257 | Inverter Parameters | 0x503F | 20543 | Q(U) curve node4 |  | FC03 | 1 |  |  | RO | percent(U/Un)
258 | Inverter Parameters | 0x5040 | 20544 | Q(U) curve node1 value |  | FC03 | 1 |  |  | RO | setting (Q/S)
259 | Inverter Parameters | 0x5041 | 20545 | Q(U) curve node2 value |  | FC03 | 1 |  |  | RO | setting (Q/S)
260 | Inverter Parameters | 0x5042 | 20546 | Q(U) curve node3 value |  | FC03 | 1 |  |  | RO | setting (Q/S)
261 | Inverter Parameters | 0x5043 | 20547 | Q(U) curve node4 value |  | FC03 | 1 |  |  | RO | setting (Q/S)
262 | Inverter Parameters | 0x504B | 20555 | Volt-Watt node1 voltage for |  | FC03 | 1 |  |  | RO | output power derating
263 | Inverter Parameters | 0x504C | 20556 | Volt-Watt node2 voltage for |  | FC03 | 1 |  |  | RO | output power derating
264 | Inverter Parameters | 0x504F | 20559 | Volt-Watt node1 output |  | FC03 | 1 |  |  | RO | power percent
265 | Inverter Parameters | 0x5050 | 20560 | Volt-Watt node2 output |  | FC03 | 1 |  |  | RO | power percent
266 | Inverter Parameters | 0x505A | 20570 | Q(P) curve node 1 percentage |  | FC03 | 1 |  |  | RO | setting (P/Pn)
267 | Inverter Parameters | 0x505B | 20571 | Q(P) curve node 2 percentage |  | FC03 | 1 |  |  | RO | setting (P/Pn)
268 | Inverter Parameters | 0x505C | 20572 | Q(P) curve node 3 percentage |  | FC03 | 1 |  |  | RO | setting (P/Pn)
269 | Inverter Parameters | 0x505D | 20573 | Q(P) curve node 4 percentage |  | FC03 | 1 |  |  | RO | setting (P/Pn)
270 | Inverter Parameters | 0x505E | 20574 | Q(P) curve node 1 value |  | FC03 | 1 |  |  | RO | setting (Q/Pn)
271 | Inverter Parameters | 0x505F | 20575 | Q(P) curve node 2 value |  | FC03 | 1 |  |  | RO | setting (Q/Pn)
272 | Inverter Parameters | 0x5060 | 20576 | Q(P) curve node 3 value |  | FC03 | 1 |  |  | RO | setting (Q/Pn)
273 | Inverter Parameters | 0x5061 | 20577 | Q(P) curve node 4 value |  | FC03 | 1 |  |  | RO | setting (Q/Pn)
274 | Inverter Parameters | 0x5063 | 20579 | LVRT Triggering voltage |  | FC03 | 1 |  |  | RO
275 | Inverter Parameters | 0x5064 | 20580 | HVRT Triggering voltage |  | FC03 | 1 |  |  | RO
276 | Inverter Parameters | 0x5065 | 20581 | FRT Mode |  | FC03 | 1 |  |  | RO
277 | Inverter Parameters | 0x5066 | 20582 | FRT |  | FC03 | 1 |  |  | RO | Zero ¦ current ¦ mode ¦ triggering threshold
278 | Inverter Parameters | 0x5067 | 20583 | FRT |  | FC03 | 1 |  |  | RO | grid ¦ voltage ¦ jump ¦ triggering threshold
279 | Inverter Parameters | 0x506C | 20588 | Grid frequency high Level 2 |  | FC03 | 1 |  |  | RO | trip time (High word)
280 | Inverter Parameters | 0x506D | 20589 | Grid frequency low Level 2 trip |  | FC03 | 1 |  |  | RO | time (High word)
281 | Inverter Parameters | 0x5070 | 20592 | Grid frequency high level 3 |  | FC03 | 1 |  |  | RO | limit
282 | Inverter Parameters | 0x5071 | 20593 | Grid frequency low level 3 |  | FC03 | 1 |  |  | RO | limit
283 | Inverter Parameters | 0x5072 | 20594 | Grid voltage high level 3 limit |  | FC03 | 1 |  |  | RO
284 | Inverter Parameters | 0x5073 | 20595 | Grid voltage low level 3 limit |  | FC03 | 1 |  |  | RO
285 | Inverter Parameters | 0x5074 | 20596 | Grid Frequency High Level 3 |  | FC03 | 1 |  |  | RO | trip time
286 | Inverter Parameters | 0x5075 | 20597 | Grid Frequency Low Level 3 |  | FC03 | 1 |  |  | RO | trip time
287 | Inverter Parameters | 0x5076 | 20598 | Grid Voltage High Level 3 trip |  | FC03 | 1 |  |  | RO | time
288 | Inverter Parameters | 0x5077 | 20599 | Grid Voltage Low Level 3 trip |  | FC03 | 1 |  |  | RO | time
289 | Inverter Parameters | 0x507F | 20607 | Over frequency derating |  | FC03 | 1 |  |  | RO | reference power
290 | Inverter Parameters | 0x5081 | 20609 | Grid under frequency rise |  | FC03 | 1 |  |  | RO | power start point
291 | Inverter Parameters | 0x5082 | 20610 | Grid under frequency rise |  | FC03 | 1 |  |  | RO | power stop point
292 | Inverter Parameters | 0x5083 | 20611 | Under frequency rise power |  | FC03 | 1 |  |  | RO | droop
293 | Inverter Parameters | 0x5084 | 20612 | Under frequency rise power |  | FC03 | 1 |  |  | RO | reference
294 | Inverter Parameters | 0x5101 | 20737 | Regulation code |  | FC03 | 1 |  |  | RO
--- IV Scan ---
295 | IV Scan | 0x5101 | 20737 | [0, 65535] | S16 | FC03/FC06 | 1 | 0.01% | 0.01 | RW | (+) Positive: over-excited ¦ (lag, inductive) ¦ (-) Negative: under-excited ¦ (lead, capacitive) ¦ Dynamic reactive ¦ power regulation. ¦ Note: ¦ 1ms. ¦ 2. Only support for 3 phase model, means 0x1A48 = 3. ¦ 3. 0x5000/0x5100 write parameter to EEPROM, write more frequently will reduce the EEPROM life, so forbid
--- DER-AVM Parameters ---
296 | DER-AVM Parameters | 0x5101 | 20737 | Reserved |  | FC03 | 1 |  |  | RO | No. ¦ Regulation code
--- Inverter Parameters ---
297 | Inverter Parameters | 0x5104 | 20740 | Derating Watt Percent |  | FC03 | 1 |  |  | RO
298 | Inverter Parameters | 0x5106 | 20742 | Mppt shadow manage |  | FC03 | 1 |  |  | RO
299 | Inverter Parameters | 0x5107 | 20743 | Mppt shadow manage interval |  | FC03 | 1 |  |  | RO | time
300 | Inverter Parameters | 0x510E | 20750 | Islanding detection |  | FC03 | 1 |  |  | RO
301 | Inverter Parameters | 0x5110 | 20752 | Ground current limit |  | FC03 | 1 |  |  | RO
302 | Inverter Parameters | 0x5112 | 20754 | Low voltage through |  | FC03 | 1 |  |  | RO | detection
303 | Inverter Parameters | 0x5114 | 20756 | Reactive Power Percent |  | FC03 | 1 |  |  | RO
304 | Inverter Parameters | 0x5115 | 20757 | RS485-1 terminal resistance |  | FC03 | 1 |  |  | RO | control
305 | Inverter Parameters | 0x5117 | 20759 | Insulation Resistor Detection |  | FC03 | 1 |  |  | RO
306 | Inverter Parameters | 0x5118 | 20760 | Ground Current Detection |  | FC03 | 1 |  |  | RO
307 | Inverter Parameters | 0x511D | 20765 | Grid high voltage load |  | FC03 | 1 |  |  | RO | de-rating function
308 | Inverter Parameters | 0x5121 | 20769 | Reactive Power Percent |  | FC03 | 1 |  |  | RO
309 | Inverter Parameters | 0x513D | 20797 | Fuse open Check Mask |  | FC03 | 1 |  |  | RO
--- DER-AVM Parameters ---
310 | DER-AVM Parameters | 0x513D | 20797 | Indicate that read or write register value is out of limit or |  | FC03 | 1 |  |  | RO | the register is forbidden to write ¦ Bit ¦ Description
--- Inverter Parameters ---
311 | Inverter Parameters | 0x6001 | 24577 | Inverter control |  | FC03 | 1 |  |  | RO
312 | Inverter Parameters | 0x6006 | 24582 | EEPROM default |  | FC03 | 1 |  |  | RO
313 | Inverter Parameters | 0x6009 | 24585 | Clear the EEPROM history |  | FC03 | 1 |  |  | RO | energy record
314 | Inverter Parameters | 0x600D | 24589 | I-V curve scan |  | FC03 | 1 |  |  | RO
--- IV Scan ---
315 | IV Scan | 0x600F | 24591 | P.F (cosφ) |  | FC03 | 1 |  |  | RO
316 | IV Scan | 0x6010 | 24592 | Reactive Power Percent |  | FC03 | 1 |  |  | RO
--- Inverter Realtime Data ---
317 | Inverter Realtime Data | 0x8000 | 32768 | Tracker 1 voltage |  | FC03 | 1 |  |  | RO
318 | Inverter Realtime Data | 0x8040 | 32832 | String 1-1 current |  | FC03 | 1 |  |  | RO
319 | Inverter Realtime Data | 0x8080 | 32896 | String 1-2 current |  | FC03 | 1 |  |  | RO
320 | Inverter Realtime Data | 0x80C0 | 32960 | String 1-3 current |  | FC03 | 1 |  |  | RO
321 | Inverter Realtime Data | 0x8100 | 33024 | String 1-4 current |  | FC03 | 1 |  |  | RO
322 | Inverter Realtime Data | 0x8140 | 33088 | Tracker 2 voltage |  | FC03 | 1 |  |  | RO
323 | Inverter Realtime Data | 0x8180 | 33152 | String 2-1 current |  | FC03 | 1 |  |  | RO
324 | Inverter Realtime Data | 0x81C0 | 33216 | String 2-2 current |  | FC03 | 1 |  |  | RO
325 | Inverter Realtime Data | 0x8200 | 33280 | String 2-3 current |  | FC03 | 1 |  |  | RO
326 | Inverter Realtime Data | 0x8240 | 33344 | String 2-4 current |  | FC03 | 1 |  |  | RO
327 | Inverter Realtime Data | 0x8280 | 33408 | Tracker 3 voltage |  | FC03 | 1 |  |  | RO
328 | Inverter Realtime Data | 0x82C0 | 33472 | String 3-1 current |  | FC03 | 1 |  |  | RO
329 | Inverter Realtime Data | 0x8300 | 33536 | String 3-2 current |  | FC03 | 1 |  |  | RO
330 | Inverter Realtime Data | 0x8340 | 33600 | String 3-3 current |  | FC03 | 1 |  |  | RO
331 | Inverter Realtime Data | 0x8380 | 33664 | String 3-4 current |  | FC03 | 1 |  |  | RO
332 | Inverter Realtime Data | 0x83C0 | 33728 | Tracker 4 voltage |  | FC03 | 1 |  |  | RO
333 | Inverter Realtime Data | 0x8400 | 33792 | String 4-1 current |  | FC03 | 1 |  |  | RO
334 | Inverter Realtime Data | 0x8440 | 33856 | String 4-2 current |  | FC03 | 1 |  |  | RO
335 | Inverter Realtime Data | 0x8480 | 33920 | String 4-3 current |  | FC03 | 1 |  |  | RO
336 | Inverter Realtime Data | 0x84C0 | 33984 | String 4-4 current |  | FC03 | 1 |  |  | RO
337 | Inverter Realtime Data | 0x8500 | 34048 | Tracker 5 voltage |  | FC03 | 1 |  |  | RO
338 | Inverter Realtime Data | 0x8540 | 34112 | String 5-1 current |  | FC03 | 1 |  |  | RO
339 | Inverter Realtime Data | 0x8580 | 34176 | String 5-2 current |  | FC03 | 1 |  |  | RO
340 | Inverter Realtime Data | 0x85C0 | 34240 | String 5-3 current |  | FC03 | 1 |  |  | RO
341 | Inverter Realtime Data | 0x8600 | 34304 | String 5-4 current |  | FC03 | 1 |  |  | RO
342 | Inverter Realtime Data | 0x8640 | 34368 | Tracker 6 voltage |  | FC03 | 1 |  |  | RO
343 | Inverter Realtime Data | 0x8680 | 34432 | String 6-1 current |  | FC03 | 1 |  |  | RO
344 | Inverter Realtime Data | 0x86C0 | 34496 | String 6-2 current |  | FC03 | 1 |  |  | RO
345 | Inverter Realtime Data | 0x8700 | 34560 | String 6-3 current |  | FC03 | 1 |  |  | RO
346 | Inverter Realtime Data | 0x8740 | 34624 | String 6-4 current |  | FC03 | 1 |  |  | RO
347 | Inverter Realtime Data | 0x8780 | 34688 | Tracker 7 voltage |  | FC03 | 1 |  |  | RO
348 | Inverter Realtime Data | 0x87C0 | 34752 | String 7-1 current |  | FC03 | 1 |  |  | RO
349 | Inverter Realtime Data | 0x8800 | 34816 | String 7-2 current |  | FC03 | 1 |  |  | RO
350 | Inverter Realtime Data | 0x8840 | 34880 | String 7-3 current |  | FC03 | 1 |  |  | RO
351 | Inverter Realtime Data | 0x8880 | 34944 | String 7-4 current |  | FC03 | 1 |  |  | RO
352 | Inverter Realtime Data | 0x88C0 | 35008 | Tracker 8 voltage |  | FC03 | 1 |  |  | RO
353 | Inverter Realtime Data | 0x8900 | 35072 | String 8-1 current |  | FC03 | 1 |  |  | RO
354 | Inverter Realtime Data | 0x8940 | 35136 | String 8-2 current |  | FC03 | 1 |  |  | RO
355 | Inverter Realtime Data | 0x8980 | 35200 | String 8-3 current |  | FC03 | 1 |  |  | RO
356 | Inverter Realtime Data | 0x89C0 | 35264 | String 8-4 current |  | FC03 | 1 |  |  | RO
357 | Inverter Realtime Data | 0x8A00 | 35328 | Tracker 9 voltage |  | FC03 | 1 |  |  | RO
358 | Inverter Realtime Data | 0x8A40 | 35392 | String 9-1 current |  | FC03 | 1 |  |  | RO
359 | Inverter Realtime Data | 0x8A80 | 35456 | String 9-2 current |  | FC03 | 1 |  |  | RO
360 | Inverter Realtime Data | 0x8AC0 | 35520 | String 9-3 current |  | FC03 | 1 |  |  | RO
361 | Inverter Realtime Data | 0x8B00 | 35584 | String 9-4 current |  | FC03 | 1 |  |  | RO
362 | Inverter Realtime Data | 0xB600 | 46592 | history log 0 |  | FC03 | 1 |  |  | RO
363 | Inverter Realtime Data | 0xB600 | 46592 | Note: | S16 | FC03 | 1 | 0.01A | 0.01 | RO | 1. L1/L2/L3 Voltage/Current/Power register address for all model even single phase or split phase model. ¦ 2. MPPT1~4 Voltage/Current/Power register address for all model. ¦ 3. MPPT5~9 Voltage/Current/Power register address depend on model. ¦ 4. Example： ¦ (1) Query history 1: 01 03 B6 00 00 03 23 83 ¦ (2) Reply history 1: 01 03 06 06 B3 A4 97 00 05 76 16 ¦ (3) Parsing： ¦ Year=0b000001=1(add 2020); Month=0b1010=10; Second=0b110011=51 ¦ - Register 0xB601 =0xA497= 0b10100 10010 010111 ¦ Day=0b10100=20; Hour=0b10010=18; Minute=0b010111=23
364 | Inverter Realtime Data | 0xB77D | 46973 | history log 127 |  | FC03 | 1 |  |  | RO
--- DER-AVM Parameters ---
365 | DER-AVM Parameters | 0xFFFF | 65535 |  |  | FC03 | 1 |  |  | RO

## Status_Definitions
Code | Name | Description | Bit_Definition
0 | Initial mode | Initial mode
1 | Standby mode | Standby mode
3 | On-Grid mode | On-Grid mode
4 | Off-Grid mode | Off-Grid mode
5 | Fault mode | Fault mode
9 | Shutdown mode | Shutdown mode
NOTE: Add/edit status codes. Descriptions used in Stage 2 InverterMode mapping.

## Error_Fault_Codes
Register | Bit | Error_No | Description | Notes
0X101E | 0 | 16 | Inverter over dc-bias current
0X101E | 1 | 17 | Inverter relay abnormal
0X101E | 2 | 18 | Remote off
0X101E | 3 | 19 | Inverter over temperature
0X101E | 4 | 20 | GFCI abnormal
0X101E | 5 | 21 | PV string reverse
0X101E | 6 | 22 | System type error
0X101E | 7 | 23 | Fan abnormal
0X101E | 8 | 24 | Dc-link unbalance or under voltage
0X101E | 9 | 25 | Dc-link over voltage
0X101E | 10 | 26 | Internal communication error
0X101E | 11 | 27 | Software incompatibility
0X101E | 12 | 28 | Internal storage error
0X101E | 13 | 29 | Data inconsistency
0X101E | 14 | 30 | Inverter abnormal
0X101E | 15 | 31 | Boost abnormal
0X101F | 0 | 0 | Grid over voltage
0X101F | 1 | 1 | Grid under voltage
0X101F | 2 | 2 | Grid absent
0X101F | 3 | 3 | Grid over frequency
0X101F | 4 | 4 | Grid under frequency
0X101F | 5 | 5 | PV over voltage
0X101F | 6 | 6 | PV insulation abnormal
0X101F | 7 | 7 | Leakage current abnormal
0X101F | 8 | 8 | Inverter in power limit state
0X101F | 9 | 9 | Internal power supply abnormal
0X101F | 10 | 10 | PV string abnormal
0X101F | 11 | 11 | PV under voltage
0X101F | 12 | 12 | PV irradiation weak
0X101F | 13 | 13 | Grid abnormal
0X101F | 14 | 14 | Arc fault detection
0X101F | 15 | 15 | AC moving average voltage high
0X1020 | 0 | 32 | Reserved
0X1020 | 1 | 33 | Logger/E-Display EEPROM fail
0X1020 | 2 | 34 | Reserved
0X1020 | 3 | 35 | Single tracker detect warning (PID device
0X1020 | 4 | 36 | AFCI lost
0X1020 | 5 | 37 | Data logger lost
0X1020 | 6 | 38 | Meter lost
0X1020 | 7 | 39 | Inverter lost
0X1020 | 8 | 40 | Grid N abnormal
0X1020 | 9 | 41 | Surge Protection Devices (SPD) defective
0X1020 | 10 | 42 | Parallel ID warning
0X1020 | 11 | 43 | Parallel SYN signal warning
0X1020 | 12 | 44 | Parallel BAT abnormal
0X1020 | 13 | 45 | Parallel GRID abnormal
0X1020 | 14 | 46 | Generator voltage abnormal
0X1020 | 15 | 47 | Reserved

## Grid_Codes
Code_Hex | Description
0XFFFF | UNKNOWN
0X0001 | AU (?? AS/NZS 4777.2 Region B)
0X0002 | DE (?? VDE 0126-1-1/A1)
0X0003 | TW (?? TW GRID)
0X0004 | DE (?? VDE-AR-N 4105:2011)
0X0005 | JP (?? JETGR0002-1-2.0)
0X0006 | IT (??? CEI 0-21)
0X0007 | SE (?? EIFS-2)
0X0008 | UK (?? G98)
0X0009 | UL (?? UL)
0X000A | TH(?? PEA)
0X000B | SE (?? SWEDEN GRID) 2007
0X000C | NL (?? EN50549-1 2019)
0X000D | TH (?? MEA)
0X000E | CN (?? NB/T 32004)
0X000F | IN (?? IEC61727)
0X0010 | AU (?? AS/NZS 4777.2 Region A)
0X0011 | NZ (?? AS/NZS 4777.2 New Zealand)
0X0012 | US (?? IEEE1547)
0X0013 | UA (??? VDE-AR-N 4105.)
0X0014 | TW (?? CNS 15382:2018)
0X0015 | DE (?? VDE0126-1-1/08.13)
0X0016 | BR (?? ABNT NBR16149 2013)
0X0017 | CZ (?? Czech EN 50160)
0X0018 | UK (?? G99 Type A)
0X0019 | PT (??? EN50549-1)
0X001A | ES (??? Spain RD1699 / RD413)
0X001B | ES (??? Spain RD661 / PO12.2)
0X001C | IT (??? CEI 0-21 ACEA)
0X001D | DE (?? VDE-AR-N 4105:2018)
0X001E | BR (?? IEC61727)
0X001F | EU (?? EN50549-1:2019)
0X0020 | BE (??? C10/11 LV)
0X0021 | PL (?? EN50438 2013)
0X0022 | DE (?? VDE4110:2018)
0X0023 | EU (?? EN50549-2:2019)
0X0024 | IT (??? CEI 0-16)
0X0025 | ZA (?? NRS097-2-1)
0X0026 | GR (?? VDE0126_Continent)
0X0027 | GR (?? VDE0126_Islands)
0X0028 | JO (?? IRR-DCC MV 2015)
0X0029 | ES (???Spain UNE206007 / UNE206006)
0X002A | AU (?? AS/NZS 4777.2 Region C)
0X002B | UK (?? G99 Type B)
0X002C | JO (?? IRR-TIC 2015)
0X002D | CZ (?? Czech EN50549-1)
0X002E | AT (??? TOR TypeA)
0X002F | CY (???? Cyprus 2019)
0X0030 | MX (??? IEEE1547 : 2014)
0X0031 | CL (?? Chile BT)
0X0032 | FR (?? UTE C15-712-1)
0X0033 | CH (?? NA/EEA A2)
0X0034 | CH (?? NA/EEA B2)
0X0035 | FR (?? UTE C15-712-1 Island 50Hz)
0X0036 | FR (?? UTE C15-712-1 Island 60Hz)
0X0037 | FI (?? VJV Type A)
0X0038 | FI (?? VJV Type B)
0X0039 | NO (?? EN50549-1)
0X003A | PL (?? NC RFG Type A)
0X003B | PL (?? NC RFG Type B)
0X003C | BE (??? C10/11 MV)
0X003D | AT (??? TOR Type B)
0X003E | IL (??? IS 4777)
0X003F | DK1 (??? Type A & B LV)
0X0040 | DK1 (??? Type B MV)
0X0041 | DK2 (??? Type A & B LV)
0X0042 | DK2 (??? Type B MV)
0X0043 | CL (?? Chile MT HD)
0X0044 | CL (?? Chile MT LD)
0X0045 | ES (???NTs-A/UNE217002/RD647)
0X0046 | ES (???NTs-B/UNE217002/RD647)
0X0047 | AU (?? AS/NZS 4777.2 Vector)
0X0048 | IRL (??? EN50549-1?Ireland)
NOTE: Register 0x5101 - Grid regulation/country code setting

## Fuse_Open_Data
Bit | Description | Value_Definition
1 | PV1 fuse open data, [0,1] | 0:normal , 1: Fuse open
2 | PV2 fuse open data, [0,1] | 0:normal , 1: Fuse open
3 | PV3 fuse open data, [0,1] | 0:normal , 1: Fuse open
4 | PV4 fuse open data, [0,1] | 0:normal , 1: Fuse open
5 | PV5 fuse open data, [0,1] | 0:normal , 1: Fuse open
6 | PV6 fuse open data, [0,1] | 0:normal , 1: Fuse open
7 | PV7 fuse open data, [0,1] | 0:normal , 1: Fuse open
8 | PV8 fuse open data, [0,1] | 0:normal , 1: Fuse open
NOTE: Registers 0x1034~0x1035 — PV string fuse open status bits

## Status_Bits_03FC
Bit | Description | Value_Definition
1 | Inverter action state, [0,1] | 0:Run , 1: Fail
2 | Inverter CB action state, [0,1] | 0: Run, 1: Fail
3 | Run state, [0,1] | 0: DER-AVM control, 1: Self control
4 | Active power control(communication), [0,1] In DER-AVM, the data is switched to 1 after a successful acceptance and to 0 after the next read
5 | Inverter action control(communication), [0,1] In DER-AVM, the data is switched to 1 after a successful acceptance and to 0 after the next read
NOTE: Registers 0x03FC~03FD — DEA-AVM inverter action/run-state bits

## Fuse_Check_Mask
Bit | Description | Value_Definition
1 | PV1 fuse open check mask, [0,1] | 0:Enable , 1: Disable
2 | PV2 fuse open check mask, [0,1] | 0:Enable , 1: Disable
3 | PV3 fuse open check mask, [0,1] | 0:Enable , 1: Disable
4 | PV4 fuse open check mask, [0,1] | 0:Enable , 1: Disable
5 | PV5 fuse open check mask, [0,1] | 0:Enable , 1: Disable
6 | PV6 fuse open check mask, [0,1] | 0:Enable , 1: Disable
7 | PV7 fuse open check mask, [0,1] | 0:Enable , 1: Disable
8 | PV8 fuse open check mask, [0,1] | 0:Enable , 1: Disable
NOTE: Registers 0x513D~0x513E — PV string fuse check enable/disable mask

## REMS_Error_Bits
Bit | Description | Value_Definition
0 | Inverter action state, [0,1] | 0: inverter running, 1: inverter stop
1 | Solar battery over voltage, [0,1] | 0: normal, 1: over voltage
2 | Solar battery under voltage, [0,1] | 0: normal, 1: under voltage
3 | Solar battery over current, [0,1] | 0: normal, 1: over current
4 | Inverter IGBT error, [0,1] | 0: normal, 1: error
5 | Inverter over temperature, [0,1] | 0: normal, 1: over temperature
6 | Grid over voltage, [0,1] | 0: normal, 1: over voltage
7 | Grid under voltage, [0,1] | 0: normal, 1: under voltage
8 | Grid over current, [0,1] | 0: normal, 1: over current
9 | Grid over frequency, [0,1] | 0: normal, 1: over frequency
10 | Grid under frequency, [0,1] | 0: normal, 1: under frequency
11 | Self control(outage), [0,1] | 0: normal, 1: outage
12 | Leakage current abnormal, [0,1] | 0: normal, 1: abnormal
NOTE: REMS Error Code register — bit-field inverter alarm flags

## REMS_Registers
No | Description | Length_Bytes | Unit
1 | PV average voltage | 2 | V
2 | PV total current | 2 | A
3 | PV totally input power | 4 | W
4 | L1 Voltage | 2 | V
5 | L2 Voltage | 2 | V
6 | L3 Voltage | 2 | V
7 | L1 Current | 2 | A
8 | L2 Current | 2 | A
9 | L3 Current | 2 | A
10 | Totally active power | 4 | W
11 | Power Factor | 2 | 0.1%
12 | Frequency | 2 | 0.1Hz
13 | Total Energy | 8 | Wh
NOTE: REMS protocol register layout (function code 0x7E)