## Register_Mapping
No | Section | Source_Addr_Hex | Source_Addr_Dec | Source_Name | Source_Type | Source_Unit | Source_Scale | Source_RW | Source_Regs | → | Solarize_Name | Solarize_Addr_Hex | Match_Type | Notes
Mode: OFFLINE ¦ Match stats: Auto/Ref=0, Unmapped=0 ¦ Edit "Solarize_Name" for Unmapped rows (red = needs review).

## Status_Mapping
Raw_Code | Raw_Name | InverterMode_State | Solarize_Code | Notes
0 | INITIAL | INITIAL | 0
1 | STANDBY | STANDBY | 1
3 | ON_GRID | ON_GRID | 3
4 | OFF_GRID | ON_GRID | 3
5 | FAULT | FAULT | 5
9 | SHUTDOWN | SHUTDOWN | 9
NOTE: Edit "InverterMode_State" column: INITIAL/STANDBY/ON_GRID/FAULT/SHUTDOWN

## DER_AVM_Control
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x07D0 | 2000 | DER_POWER_FACTOR_SET | S16 | FC06 | 1 |  | 0.001 | RW | Power factor setpoint [-1000,-800],[800,1000]
0x07D1 | 2001 | DER_ACTION_MODE | U16 | FC06 | 1 |  | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
0x07D2 | 2002 | DER_REACTIVE_POWER_PCT | S16 | FC06 | 1 | % | 0.1 | RW | Reactive power % [-484,484]
0x07D3 | 2003 | DER_ACTIVE_POWER_PCT | U16 | FC06 | 1 | % | 0.1 | RW | Active power % [0,1100]
0x0834 | 2100 | INVERTER_ON_OFF | U16 | FC06 | 1 |  | 1 | RW | On/Off control: 0=ON, 1=OFF
0x0835 | 2101 | CLEAR_PV_INSULATION_WARNING | U16 | FC06 | 1 |  | 1 | WO | Clear PV insulation warning: 1=Clear
0x6001 | 24577 | INVERTER_CONTROL | U16 | FC06 | 1 |  | 1 | WO | Inverter control: 0=Power on, 1=Shut down
0x600D | 24589 | IV_CURVE_SCAN | U16 | FC06 | 1 |  | 1 | RW | IV curve scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
0x600F | 24591 | POWER_FACTOR_DYNAMIC | S16 | FC06 | 1 |  | 0.001 | RW | Dynamic power factor control
0x6010 | 24592 | REACTIVE_POWER_DYNAMIC | S16 | FC06 | 1 | % | 0.01 | RW | Dynamic reactive power control (%)
0x3005 | 12293 | POWER_DERATING_PCT | U16 | FC06 | 1 | % | 1 | RW | Active power derating [0-110]%
NOTE: DER-AVM control registers (always included). Do not modify addresses.

## DEA_AVM_Monitor
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x03E8 | 1000 | DEA_L1_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L1 current (low word)
0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 current (high word)
0x03EA | 1002 | DEA_L2_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L2 current (low word)
0x03EB | 1003 | DEA_L2_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 current (high word)
0x03EC | 1004 | DEA_L3_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L3 current (low word)
0x03ED | 1005 | DEA_L3_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 current (high word)
0x03EE | 1006 | DEA_L1_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L1 voltage (low word)
0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 voltage (high word)
0x03F0 | 1008 | DEA_L2_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L2 voltage (low word)
0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 voltage (high word)
0x03F2 | 1010 | DEA_L3_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L3 voltage (low word)
0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 voltage (high word)
0x03F4 | 1012 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | FC03 | 2 | kW | 0.1 | RO | DEA total active power (low word)
0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total active power (high word)
0x03F6 | 1014 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | FC03 | 2 | Var | 1 | RO | DEA total reactive power (low word)
0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total reactive power (high word)
0x03F8 | 1016 | DEA_POWER_FACTOR_LOW | S32 | FC03 | 2 |  | 0.001 | RO | DEA power factor (low word)
0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | S32 | FC03 | 1 |  |  | RO | DEA power factor (high word)
0x03FA | 1018 | DEA_FREQUENCY_LOW | S32 | FC03 | 2 | Hz | 0.1 | RO | DEA frequency (low word)
0x03FB | 1019 | DEA_FREQUENCY_HIGH | S32 | FC03 | 1 |  |  | RO | DEA frequency (high word)
0x03FC | 1020 | DEA_STATUS_FLAG_LOW | S32 | FC03 | 2 |  | 1 | RO | DEA status flag (low word)
0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | S32 | FC03 | 1 |  |  | RO | DEA status flag (high word)
NOTE: DEA-AVM monitoring registers (always included). Do not modify addresses.