## Registers
No | Section | Address_Hex | Address_Dec | Definition | Data_Type | FC_Code | Registers | Unit | Scale_Factor | R/W | Description
--- Device Information (System Info) ---
1 | Device Information (System Info) | 0x7530 | 30000 | Model | string | FC03 | 15 |  |  | RO | Nameplate name of the machine, original "model name"
2 | Device Information (System Info) | 0x753F | 30015 | SN | string | FC03 | 10 |  |  | RO | Device SN, which is obtained from the electronic label of the entire system.
3 | Device Information (System Info) | 0x7549 | 30025 | PN | string | FC03 | 10 |  |  | RO | Product Code
4 | Device Information (System Info) | 0x7553 | 30035 | Firmware Version | string | FC03 | 15 |  |  | RO | Character string reporting: initial version VX00R00X (default VR version) VX00R00XD01, VX00R00XD02... (D0X is provided b
5 | Device Information (System Info) | 0x7562 | 30050 | Softwareversion | string | FC03 | 15 |  |  | RO | In V800R021C10SPCXXX, the offering name and software version are displayed on the display page.
6 | Device Information (System Info) | 0x7574 | 30068 | Protocolversion [Modbus ] | U32 | FC03 | 2 |  |  | RO | high-character: main version; Upgrade on Incompatible Changes low-letter: revision; Compatible upgrade The baseline vers
7 | Device Information (System Info) | 0x7576 | 30070 | Model ID | U16 | FC03 | 1 |  |  | RO | Model ID. For details, see the Inverter Model Defni ition.xlsm.
8 | Device Information (System Info) | 0x7577 | 30071 | Numberof PV strings | U16 | FC03 | 1 |  |  | RO
9 | Device Information (System Info) | 0x7578 | 30072 | Numberof MPP Ts | U16 | FC03 | 1 |  |  | RO
10 | Device Information (System Info) | 0x7579 | 30073 | Ratedpower | U32 | FC03 | 2 | kW |  | RO | Pn
11 | Device Information (System Info) | 0x757B | 30075 | Maximumactivepower (Pmax) | U32 | FC03 | 2 | kW |  | RO | Read-only interface to 42027
12 | Device Information (System Info) | 0x757D | 30077 | Maximumapparent (Smax) | U32 | FC03 | 2 | kVA |  | RO | Read-only interface to 42025
13 | Device Information (System Info) | 0x757F | 30079 | Real - timemaximumreactivepower (Qmax, fedtothepowergrid) | S32 | FC03 | 2 | kVar |  | RO | Reported to the monitoring, indicating the reactive power adjustment range. Feature data is updated when the power grid
14 | Device Information (System Info) | 0x7581 | 30081 | Real - timemaximumreactivepower (- Qmax, absorbedfromthepowergrid) | S32 | FC03 | 2 | kVar |  | RO | Reported to the monitoring, indicating the reactive power adjustment range. Feature data is updated when the power grid
15 | Device Information (System Info) | 0x7583 | 30083 | Maximumactivepower (Pmaxr _ eal) | U32 | FC03 | 2 | kW |  | RO | The default maximum active power capacity is fixed on the nameplate of the machine, and the maximum active power capacit
16 | Device Information (System Info) | 0x7585 | 30085 | Maximumapparentcapability (Smaxr _ eal) | U32 | FC03 | 2 | kVA |  | RO | The default apparent maximum capacity value is fixed on the machine nameplate, and one machine will not change. as a set
17 | Device Information (System Info) | 0x7599 | 30105 | Productsalesarea | string | FC03 | 2 |  |  | RO | XX: Two uppercase letters, indicating the sales area or application area of the product, mainly related to the AC power
18 | Device Information (System Info) | 0x759B | 30107 | Productsoftware ID | U16 | FC03 | 1 |  |  | RO | Unique ID of the software publishing entity. Used for processing the compatibility of the power grid standard code.
19 | Device Information (System Info) | 0x759C | 30108 | Product Software Version Number | U16 | FC03 | 1 |  |  | RO | Software release entity specifci release version sequence number Used to process the compatibility of the power grid sta
20 | Device Information (System Info) | 0x759D | 30109 | Power Grid Standard Code Protocol Version | U16 | FC03 | 1 |  |  | RO | Protocol loading and verifciation is similar to CAN1.0 and CAN2.0.
21 | Device Information (System Info) | 0x759E | 30110 | Unique ID ofthesoftware . | U16 | FC03 | 1 |  |  | RO | Unique ID of a software version. Upgrade packages with different IDs cannot be upgraded to each other. (Broadcast Upgrad
22 | Device Information (System Info) | 0x759F | 30111 | Numberofupgradepackages | U16 | FC03 | 1 |  |  | RO | The number of upgrade packages must be sufcfiient because more and more devices need to be upgraded.
23 | Device Information (System Info) | 0x75A0 | 30112 | Informationaboutsubpackage 1 | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
24 | Device Information (System Info) | 0x75A2 | 30114 | Subpackage 2 information | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
25 | Device Information (System Info) | 0x75A4 | 30116 | Informationaboutsubpackage 3 | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
26 | Device Information (System Info) | 0x75A6 | 30118 | Subpackage 4 information | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
27 | Device Information (System Info) | 0x75A8 | 30120 | Subpackage 5 information | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
28 | Device Information (System Info) | 0x75AA | 30122 | Informationaboutsubpackage 6 | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
29 | Device Information (System Info) | 0x75AC | 30124 | Subpackage 7 information | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
30 | Device Information (System Info) | 0x75AE | 30126 | Subpackage 8 information | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
31 | Device Information (System Info) | 0x75B0 | 30128 | Subpackage 9 information | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
32 | Device Information (System Info) | 0x75B2 | 30130 | Informationaboutsubpackage 10 | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
33 | Device Information (System Info) | 0x75EF | 30191 | [Third- partylabeling] SN | string | FC03 | 10 |  |  | RO | Serial number of third-party OEM equipment, customized by third-party manufacturers
34 | Device Information (System Info) | 0x75F9 | 30201 | [Third- partylabel ] Manufacturermodel | U16 | FC03 | 1 |  |  | RO | Model of third-party OEM equipment manufacturer
35 | Device Information (System Info) | 0x75FF | 30207 | Subdevice Support ID | U32 | FC03 | 2 |  |  | RO
36 | Device Information (System Info) | 0x7601 | 30209 | Subdevicepresenceflag. | U32 | FC03 | 2 |  |  | RO
37 | Device Information (System Info) | 0x7724 | 30500 | Numberofuniquesouthboundsoftware IDs | U16 | FC03 | 1 |  |  | RO | Total number of southbound components that have independent upgrade packages. Note: This flag corresponds to the EquipCh
38 | Device Information (System Info) | 0x7725 | 30501 | Unique ID 1 ofthesouthboundsoftware . | U16 | FC03 | 1 |  |  | RO
39 | Device Information (System Info) | 0x7726 | 30502 | Unique ID 2 ofthesouthboundsoftware | U16 | FC03 | 1 |  |  | RO
40 | Device Information (System Info) | 0x772A | 30506 | Numberofupgradepackagesforsouthbounddevice 1 | U16 | FC03 | 1 |  |  | RO
41 | Device Information (System Info) | 0x772B | 30507 | Informationaboutsubpackage 1 ofsouthbounddevice 1 | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
42 | Device Information (System Info) | 0x772D | 30509 | Informationaboutsubpackage 2 ofsouthbounddevice 1 | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
43 | Device Information (System Info) | 0x772F | 30511 | Informationaboutsubpackage 3 ofsouthbounddevice 1 | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
44 | Device Information (System Info) | 0x7735 | 30517 | Numberofupgradepackagesforsouthbounddevice 2 | U16 | FC03 | 1 |  |  | RO
45 | Device Information (System Info) | 0x7736 | 30518 | Informationaboutsubpackage 1 ofsouthbounddevice 2 | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
46 | Device Information (System Info) | 0x7738 | 30520 | Informationaboutsubpackage 2 ofsouthbounddevice 2 | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
47 | Device Information (System Info) | 0x773A | 30522 | Informationaboutsubpackage 3 ofsouthbounddevice 2 | U32 | FC03 | 2 |  |  | RO | high-character: file type ID; Low character: device type ID.
48 | Device Information (System Info) | 0x773C | 30524 | Informationaboutsubpackage 4 ofsouthbounddevice 2 | U32 | FC03 | 2 |  |  | RO | high-character: flie type ID; Low character: device type ID.
49 | Device Information (System Info) | 0x7761 | 30561 | Ofefringnameofsouthbounddevice 1 | string | FC03 | 15 |  |  | RO | Distributed inverter southbound device identification: Southbound device 1: optimizer
50 | Device Information (System Info) | 0x7770 | 30576 | Offeringnameofsouthbounddevice 2 | string | FC03 | 15 |  |  | RO | Distributed inverter southbound device identifciation: Southbound device 2: DC- MBUS
51 | Device Information (System Info) | 0x777F | 30591 | Ofefringnameofsouthbounddevice 3. | string | FC03 | 15 |  |  | RO | Distributed inverter southbound device identifciation: Southbound device 3: LUNA2000 1.0
52 | Device Information (System Info) | 0x7918 | 31000 | Hardwareversion | string | FC03 | 15 |  |  | RO
53 | Device Information (System Info) | 0x7927 | 31015 | Monitoring Board SN | string | FC03 | 10 |  |  | RO | From the electronic label of the monitoring board
54 | Device Information (System Info) | 0x7931 | 31025 | Monitoringsoftwareversion | string | FC03 | 15 |  |  | RO | MCU1 version
55 | Device Information (System Info) | 0x7940 | 31040 | Main DSP version | string | FC03 | 15 |  |  | RO | MCU2 version
56 | Device Information (System Info) | 0x795E | 31070 | CPL D versionnumber | string | FC03 | 15 |  |  | RO | MCU4 version
57 | Device Information (System Info) | 0x796D | 31085 | AFCI versionnumber | string | FC03 | 15 |  |  | RO | MCU5 version
58 | Device Information (System Info) | 0x798B | 31115 | DC- MBU S versionnumber | string | FC03 | 15 |  |  | RO | MCU7 version
59 | Device Information (System Info) | 0x79E0 | 31200 | Registrationcode | string | FC03 | 10 |  |  | RO
--- Inverter Realtime Data ---
60 | Inverter Realtime Data | 0x7D00 | 32000 | [Remotecommunication] Single- noderemotecommunication | U16 | FC03 | 1 |  |  | RO | Reported by IEC104, which indicates the merged PCS running status.
61 | Inverter Realtime Data | 0x7D02 | 32002 | [Remotesignal] Runningstatus (monitoring) | U16 | FC03 | 1 |  |  | RO
62 | Inverter Realtime Data | 0x7D03 | 32003 | [Remotesignal] Runningstatus (powerprocessing) | U32 | FC03 | 2 |  |  | RO
63 | Inverter Realtime Data | 0x7D08 | 32008 | [Remotesignal] Alarm 1 | U16 | FC03 | 1 |  |  | RO | For details, see the Alarm Mapping sheet.
64 | Inverter Realtime Data | 0x7D09 | 32009 | [Remotesignal] Alarm 2 | U16 | FC03 | 1 |  |  | RO | For details, see the Alarm Mapping sheet.
65 | Inverter Realtime Data | 0x7D0A | 32010 | [Remotesignal] Alarm 3 | U16 | FC03 | 1 |  |  | RO | For details, see the Alarm Mapping sheet.
66 | Inverter Realtime Data | 0x7D0B | 32011 | [Remotesignal] Alarm 4 | U16 | FC03 | 1 |  |  | RO | For details, see the Alarm Mapping sheet.
67 | Inverter Realtime Data | 0x7D0C | 32012 | [Remotesignal] Alarm 5 | U16 | FC03 | 1 |  |  | RO | For details, see the Alarm Mapping sheet.
68 | Inverter Realtime Data | 0x7D0D | 32013 | [Remotesignal] Alarm 6 | U16 | FC03 | 1 |  |  | RO | For details, see the Alarm Mapping sheet.
69 | Inverter Realtime Data | 0x7D0F | 32015 | Device SN featurecode | U16 | FC03 | 1 |  |  | RO | Indicates the CRC16 value of the SN, which is the key data ID. Used to prevent incorrect energy yield from being modifie
70 | Inverter Realtime Data | 0x7D10 | 32016 | PV1 voltage | S16 | FC03 | 1 | V |  | RO | When bit 9 of power parameter mask 14 is 0, the signal name is PV1 voltage. When bit 9 of the power parameter mask 14 is
71 | Inverter Realtime Data | 0x7D11 | 32017 | PV1 current | S16 | FC03 | 1 | A |  | RO | When bit 9 of power parameter mask 14 is 0, the signal name is PV1 current. When bit 9 of power parameter mask 14 is 1,
72 | Inverter Realtime Data | 0x7D12 | 32018 | PV2 Voltage | S16 | FC03 | 1 | V |  | RO | When bit 9 of power parameter mask 14 is 0, the signal name is PV2 voltage. When bit 9 of the power parameter mask 14 is
73 | Inverter Realtime Data | 0x7D13 | 32019 | PV2 current | S16 | FC03 | 1 | A |  | RO | When bit 9 of power parameter mask 14 is 0, the signal name is PV2 current. When bit 9 of the power parameter mask 14 is
74 | Inverter Realtime Data | 0x7D14 | 32020 | PV3 Voltage | S16 | FC03 | 1 | V |  | RO
75 | Inverter Realtime Data | 0x7D15 | 32021 | PV3 current | S16 | FC03 | 1 | A |  | RO
76 | Inverter Realtime Data | 0x7D16 | 32022 | PV4 Voltage | S16 | FC03 | 1 | V |  | RO
77 | Inverter Realtime Data | 0x7D17 | 32023 | PV4 current | S16 | FC03 | 1 | A |  | RO
78 | Inverter Realtime Data | 0x7D18 | 32024 | PV5 voltage | S16 | FC03 | 1 | V |  | RO
79 | Inverter Realtime Data | 0x7D19 | 32025 | PV5 current | S16 | FC03 | 1 | A |  | RO
80 | Inverter Realtime Data | 0x7D1A | 32026 | PV6 voltage | S16 | FC03 | 1 | V |  | RO
81 | Inverter Realtime Data | 0x7D1B | 32027 | PV6 current | S16 | FC03 | 1 | A |  | RO
82 | Inverter Realtime Data | 0x7D1C | 32028 | PV7 Voltage | S16 | FC03 | 1 | V |  | RO
83 | Inverter Realtime Data | 0x7D1D | 32029 | PV7 current | S16 | FC03 | 1 | A |  | RO
84 | Inverter Realtime Data | 0x7D1E | 32030 | PV8 Voltage | S16 | FC03 | 1 | V |  | RO
85 | Inverter Realtime Data | 0x7D1F | 32031 | PV8 current | S16 | FC03 | 1 | A |  | RO
86 | Inverter Realtime Data | 0x7D40 | 32064 | DC power | S32 | FC03 | 2 | kW |  | RO
87 | Inverter Realtime Data | 0x7D42 | 32066 | Powergridline A and B voltage | U16 | FC03 | 1 | V |  | RO | When the output mode is L/N, the signal name is Grid Voltage. When Output Mode is set to L1/L2/N or L1/L2, the signal na
88 | Inverter Realtime Data | 0x7D43 | 32067 | Powergrid B/C linevoltage | U16 | FC03 | 1 | V |  | RO | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
89 | Inverter Realtime Data | 0x7D44 | 32068 | Powergrid CA linevoltage | U16 | FC03 | 1 | V |  | RO | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
90 | Inverter Realtime Data | 0x7D45 | 32069 | Powergridphase A voltage | U16 | FC03 | 1 | V |  | RO | This parameter is invalid when the output mode is L/N. When Output Mode is set to L1/L2/N or L1/L2, the signal name is U
91 | Inverter Realtime Data | 0x7D46 | 32070 | Powergridphase B voltage | U16 | FC03 | 1 | V |  | RO | This parameter is invalid when the output mode is L/N. When Output Mode is set to L1/L2/N or L1/L2, the signal name is W
92 | Inverter Realtime Data | 0x7D47 | 32071 | Powergridphase C voltage | U16 | FC03 | 1 | V |  | RO | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
93 | Inverter Realtime Data | 0x7D48 | 32072 | Powergridphase A current | S32 | FC03 | 2 | A |  | RO | When the output mode is L/N, L1/L2/N, or L1/L2, the signal name is Grid Current.
94 | Inverter Realtime Data | 0x7D4A | 32074 | Powergridphase B current | S32 | FC03 | 2 | A |  | RO | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
95 | Inverter Realtime Data | 0x7D4C | 32076 | Powergridphase C current | S32 | FC03 | 2 | A |  | RO | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
96 | Inverter Realtime Data | 0x7D4E | 32078 | Peakactivepowerofthecurrentday | S32 | FC03 | 2 | kW |  | RO
97 | Inverter Realtime Data | 0x7D50 | 32080 | Activepower | S32 | FC03 | 2 | kW |  | RO
98 | Inverter Realtime Data | 0x7D52 | 32082 | reactivepower | S32 | FC03 | 2 | kVar |  | RO
99 | Inverter Realtime Data | 0x7D54 | 32084 | Powerfactor | S16 | FC03 | 1 |  |  | RO
100 | Inverter Realtime Data | 0x7D55 | 32085 | Gridfrequency | U16 | FC03 | 1 | Hz |  | RO
101 | Inverter Realtime Data | 0x7D56 | 32086 | Inverterefficiency | U16 | FC03 | 1 | % |  | RO | When PCS is used to generate power, it indicates the power generation efficiency. When PCS is used to absorb, it indicat
102 | Inverter Realtime Data | 0x7D57 | 32087 | Internaltemperature | S16 | FC03 | 1 | °C |  | RO
103 | Inverter Realtime Data | 0x7D58 | 32088 | Insulationimpedance | U16 | FC03 | 1 | MΩ |  | RO
104 | Inverter Realtime Data | 0x7D59 | 32089 | Device Status | U16 | FC03 | 1 |  |  | RO | 0x0000 Standby: initializing 0x0001 Standby: detecting insulation resistance 0x0002 Standby: detecting irradiation 0x000
105 | Inverter Realtime Data | 0x7D5A | 32090 | Fault Code | U16 | FC03 | 1 |  |  | RO | Fault code corresponding to the alarm with the highest priority. For details, see the Alarm Description sheet.
106 | Inverter Realtime Data | 0x7D5B | 32091 | Start -uptime | EpochSecond | FC03 | 2 | s |  | RO | Monitoring Calculation
107 | Inverter Realtime Data | 0x7D5D | 32093 | Shutdowntime | EpochSecond | FC03 | 2 | s |  | RO | Monitoring Calculation
108 | Inverter Realtime Data | 0x7D5F | 32095 | Activepower [fast ] | S32 | FC03 | 2 | kW |  | RO | Fast reporting interface, which is not filtered and used for scheduling energy storage.
109 | Inverter Realtime Data | 0x7D6A | 32106 | Accumulatedpowergeneration | U32 | FC03 | 2 | kWh |  | RO
110 | Inverter Realtime Data | 0x7D6C | 32108 | Total DC Input Power | U32 | FC03 | 2 | kWh |  | RO
111 | Inverter Realtime Data | 0x7D6E | 32110 | Statisticaltimeofthecurrentenergyyield . | EpochSecond | FC03 | 2 | s |  | RO
112 | Inverter Realtime Data | 0x7D70 | 32112 | Current Hour Electricity | U32 | FC03 | 2 | kWh |  | RO
113 | Inverter Realtime Data | 0x7D72 | 32114 | Current- daypowergeneration | U32 | FC03 | 2 | kWh |  | RO
114 | Inverter Realtime Data | 0x7D74 | 32116 | Electricitygeneratedinthecurrentmonth | U32 | FC03 | 2 | kWh |  | RO
115 | Inverter Realtime Data | 0x7D76 | 32118 | Electricitygeneratedinthecurrentyear | U32 | FC03 | 2 | kWh |  | RO
116 | Inverter Realtime Data | 0x7D97 | 32151 | Numberofcriticalalarms | U16 | FC03 | 1 |  |  | RO
117 | Inverter Realtime Data | 0x7D98 | 32152 | Numberofmajoralarms | U16 | FC03 | 1 |  |  | RO
118 | Inverter Realtime Data | 0x7D99 | 32153 | Numberof Minor Alarms | U16 | FC03 | 1 |  |  | RO
119 | Inverter Realtime Data | 0x7D9A | 32154 | Numberof Warning Alarms | U16 | FC03 | 1 |  |  | RO
120 | Inverter Realtime Data | 0x7D9B | 32155 | Alarmclearance SN | U16 | FC03 | 1 |  |  | RO | After the alarm is cleared, the serial number increases by 1. After the alarm is reversed, the serial number starts from
121 | Inverter Realtime Data | 0x7D9C | 32156 | Last Hour Power Statistics Time | EpochSecond | FC03 | 2 | s |  | RO | include generate/absorbed power
122 | Inverter Realtime Data | 0x7D9E | 32158 | Electricitygeneratedintheprevioushour | U32 | FC03 | 2 | kWh |  | RO
123 | Inverter Realtime Data | 0x7DA0 | 32160 | Electricitystatisticstimeofthepreviousday | EpochSecond | FC03 | 2 | s |  | RO | include generate/absorbed power
124 | Inverter Realtime Data | 0x7DA2 | 32162 | Electricitygeneratedinthepreviousday | U32 | FC03 | 2 | kWh |  | RO
125 | Inverter Realtime Data | 0x7DA4 | 32164 | Statisticaltimeofthepreviousmonth. | EpochSecond | FC03 | 2 | s |  | RO | include generate/absorbed power
126 | Inverter Realtime Data | 0x7DA6 | 32166 | Electricitygeneratedinthepreviousmonth | U32 | FC03 | 2 | kWh |  | RO
127 | Inverter Realtime Data | 0x7DA8 | 32168 | Electricitystatisticstimeofthepreviousyear | EpochSecond | FC03 | 2 | s |  | RO | include generate/absorbed power
128 | Inverter Realtime Data | 0x7DAA | 32170 | Electricitygeneratedinthepreviousyear | U32 | FC03 | 2 | kWh |  | RO
129 | Inverter Realtime Data | 0x7DAC | 32172 | Serialnumberofthelatestactivealarm. | U32 | FC03 | 2 |  |  | RO | When a new active alarm is generated, the serial number increases by 1.
130 | Inverter Realtime Data | 0x7DAE | 32174 | Latest Historical Alarm Serial Number | U32 | FC03 | 2 |  |  | RO | When an active alarm is transferred to the historical alarm, the serial number of the historical alarm is the same as th
131 | Inverter Realtime Data | 0x7DB0 | 32176 | Totalbusvoltage | S16 | FC03 | 1 | V |  | RO | Data reported by PID, used in single-level scenarios
132 | Inverter Realtime Data | 0x7DB1 | 32177 | Maximum PV voltage | S16 | FC03 | 1 | V |  | RO | Data reported by PID, used in single-level scenarios
133 | Inverter Realtime Data | 0x7DB2 | 32178 | Minimum PV voltage | S16 | FC03 | 1 | V |  | RO | Data reported by PID, used in single-level scenarios
134 | Inverter Realtime Data | 0x7DB3 | 32179 | Average PV negative- to- groundvoltage | S16 | FC03 | 1 | V |  | RO | Data reported by PID, used in single-level scenarios
135 | Inverter Realtime Data | 0x7DB4 | 32180 | Maximum PV positive- to- groundvoltage | S16 | FC03 | 1 | V |  | RO | Data reported by PID, used in single-level scenarios
136 | Inverter Realtime Data | 0x7DB5 | 32181 | Minimum PV negative- to- groundvoltage | S16 | FC03 | 1 | V |  | RO | Data reported by PID, used in single-level scenarios
137 | Inverter Realtime Data | 0x7DB6 | 32182 | Inverter- to- PE withstandvoltage | U16 | FC03 | 1 | V |  | RO | Data reported by PID, used in single-level scenarios To be compatible with PID 2.0, the PCS reports 1502. 0:100 V or 110
138 | Inverter Realtime Data | 0x7DB7 | 32183 | ISO featureinformation | U16 | FC03 | 1 |  |  | RO | Data reported by PID, used in single-level scenarios
139 | Inverter Realtime Data | 0x7DBE | 32190 | Built -in PID runningstatus | U16 | FC03 | 1 |  |  | RO
140 | Inverter Realtime Data | 0x7DBF | 32191 | PV negative- to- groundvoltage | S16 | FC03 | 1 | V |  | RO
141 | Inverter Realtime Data | 0x7DC0 | 32192 | Directionofthebuilt -in PID compensation | U16 | FC03 | 1 |  |  | RO
142 | Inverter Realtime Data | 0x7DD4 | 32212 | Total DC energyyieldof MPP T1 | U32 | FC03 | 2 | kWh |  | RO | TD Tech NMS GUI Display [5/4]
143 | Inverter Realtime Data | 0x7DD6 | 32214 | Total DC energyyieldof MPP T2 | U32 | FC03 | 2 | kWh |  | RO | TD Tech NMS GUI Display [5/4]
144 | Inverter Realtime Data | 0x7DD8 | 32216 | MPP T3 DC Total Energy Yield | U32 | FC03 | 2 | kWh |  | RO | TD Tech NMS GUI Display [5/4]
145 | Inverter Realtime Data | 0x7DDA | 32218 | MPP T4 DC Accumulated Energy Yield | U32 | FC03 | 2 | kWh |  | RO | TD Tech NMS GUI Display [5/4]
146 | Inverter Realtime Data | 0x7DFC | 32252 | Monitoringalarm 1 | U16 | FC03 | 1 |  |  | RO | GroupID:0xFF00
147 | Inverter Realtime Data | 0x7DFD | 32253 | Monitoringalarm 2 | U16 | FC03 | 1 |  |  | RO | GroupID:0xFF01
148 | Inverter Realtime Data | 0x7DFE | 32254 | Monitoralarm 3 | U16 | FC03 | 1 |  |  | RO | GroupID:0xFF02
149 | Inverter Realtime Data | 0x7DFF | 32255 | [External] Poweralarm 1 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0000
150 | Inverter Realtime Data | 0x7E00 | 32256 | [External] Poweralarm 2 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0001
151 | Inverter Realtime Data | 0x7E01 | 32257 | [External] Poweralarm 3 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0002
152 | Inverter Realtime Data | 0x7E02 | 32258 | [External] Poweralarm 4 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0003
153 | Inverter Realtime Data | 0x7E03 | 32259 | [External] Poweralarm 5 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0004
154 | Inverter Realtime Data | 0x7E04 | 32260 | [External] Poweralarm 6 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0005
155 | Inverter Realtime Data | 0x7E05 | 32261 | [External] Poweralarm 7 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0006
156 | Inverter Realtime Data | 0x7E06 | 32262 | [External] Poweralarm 8 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0007
157 | Inverter Realtime Data | 0x7E07 | 32263 | [External] Poweralarm 9 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0008
158 | Inverter Realtime Data | 0x7E08 | 32264 | [External] Poweralarm 10 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0009
159 | Inverter Realtime Data | 0x7E09 | 32265 | [External] Poweralarm 11 | U16 | FC03 | 1 |  |  | RO | GroupID:0x000A
160 | Inverter Realtime Data | 0x7E0A | 32266 | [External] Poweralarm 12 | U16 | FC03 | 1 |  |  | RO | GroupID:0x000B
161 | Inverter Realtime Data | 0x7E0B | 32267 | [External] Poweralarm 13 | U16 | FC03 | 1 |  |  | RO | GroupID:0x000C
162 | Inverter Realtime Data | 0x7E0C | 32268 | [External] Poweralarm 14 | U16 | FC03 | 1 |  |  | RO | GroupID:0x000D
163 | Inverter Realtime Data | 0x7E0D | 32269 | [External] Poweralarm 15 | U16 | FC03 | 1 |  |  | RO | GroupID:0x000E
164 | Inverter Realtime Data | 0x7E0E | 32270 | [External] Poweralarm 16 | U16 | FC03 | 1 |  |  | RO | GroupID:0x000F
165 | Inverter Realtime Data | 0x7E0F | 32271 | Monitoralarm 4 | U16 | FC03 | 1 |  |  | RO | GroupID:0xFF03
166 | Inverter Realtime Data | 0x7E10 | 32272 | Monitoralarm 5 | U16 | FC03 | 1 |  |  | RO | GroupID:0xFF04
167 | Inverter Realtime Data | 0x7E11 | 32273 | [External] Poweralarm 17 | U16 | FC03 | 1 |  |  | RO | GroupID:0x0010
168 | Inverter Realtime Data | 0x7E2C | 32300 | String 1 accessstatus | U16 | FC03 | 1 |  |  | RO
169 | Inverter Realtime Data | 0x7E2D | 32301 | String 2 accessstatus | U16 | FC03 | 1 |  |  | RO
170 | Inverter Realtime Data | 0x7E2E | 32302 | String 3 accessstatus | U16 | FC03 | 1 |  |  | RO
171 | Inverter Realtime Data | 0x7E2F | 32303 | String 4 accessstatus | U16 | FC03 | 1 |  |  | RO
172 | Inverter Realtime Data | 0x7E30 | 32304 | String 5 accessstatus | U16 | FC03 | 1 |  |  | RO
173 | Inverter Realtime Data | 0x7E31 | 32305 | Connectionstatusofstring 6 | U16 | FC03 | 1 |  |  | RO
174 | Inverter Realtime Data | 0x7E32 | 32306 | String 7 accessstatus | U16 | FC03 | 1 |  |  | RO
175 | Inverter Realtime Data | 0x7E33 | 32307 | String 8 accessstatus | U16 | FC03 | 1 |  |  | RO
176 | Inverter Realtime Data | 0x84D0 | 34000 | Stent System Status | U32 | FC03 | 2 |  |  | RO | BIT0–BIT15: state of support system 1–16; BIT16–BIT31: reserved for future expansion.
177 | Inverter Realtime Data | 0x84D2 | 34002 | Tiltangle 1 sampling | S16 | FC03 | 1 | ° |  | RO
178 | Inverter Realtime Data | 0x84D3 | 34003 | Azimuth 1 sampling | S16 | FC03 | 1 | ° |  | RO
179 | Inverter Realtime Data | 0x84D4 | 34004 | Tiltangle 2 sampling | S16 | FC03 | 1 | ° |  | RO
180 | Inverter Realtime Data | 0x84D5 | 34005 | Azimuth 2 sampling | S16 | FC03 | 1 | ° |  | RO
181 | Inverter Realtime Data | 0x84D6 | 34006 | Tiltangle 3 sampling | S16 | FC03 | 1 | ° |  | RO
182 | Inverter Realtime Data | 0x84D7 | 34007 | Azimuth 3 sampling | S16 | FC03 | 1 | ° |  | RO
183 | Inverter Realtime Data | 0x84D8 | 34008 | Tiltangle 4 sampling | S16 | FC03 | 1 | ° |  | RO
184 | Inverter Realtime Data | 0x84D9 | 34009 | Azimuth 4 sampling | S16 | FC03 | 1 | ° |  | RO
185 | Inverter Realtime Data | 0x84DA | 34010 | Tiltangle 5 sampling | S16 | FC03 | 1 | ° |  | RO
186 | Inverter Realtime Data | 0x84DB | 34011 | Azimuth 5 sampling | S16 | FC03 | 1 | ° |  | RO
187 | Inverter Realtime Data | 0x84DC | 34012 | Tiltangle 6 sampling | S16 | FC03 | 1 | ° |  | RO
188 | Inverter Realtime Data | 0x84DD | 34013 | Azimuth 6 sampling | S16 | FC03 | 1 | ° |  | RO
189 | Inverter Realtime Data | 0x84DE | 34014 | Tiltangle 7 sampling | S16 | FC03 | 1 | ° |  | RO
190 | Inverter Realtime Data | 0x84DF | 34015 | Azimuth 7 sampling | S16 | FC03 | 1 | ° |  | RO
191 | Inverter Realtime Data | 0x84E0 | 34016 | Tiltangle 8 sampling | S16 | FC03 | 1 | ° |  | RO
192 | Inverter Realtime Data | 0x84E1 | 34017 | Azimuth 8 sampling | S16 | FC03 | 1 | ° |  | RO
193 | Inverter Realtime Data | 0x84E2 | 34018 | Tiltangle 9 sampling | S16 | FC03 | 1 | ° |  | RO
194 | Inverter Realtime Data | 0x84E3 | 34019 | Azimuth 9 sampling | S16 | FC03 | 1 | ° |  | RO
195 | Inverter Realtime Data | 0x84E4 | 34020 | Tiltangle 10 sampling | S16 | FC03 | 1 | ° |  | RO
196 | Inverter Realtime Data | 0x84E5 | 34021 | Azimuth 10 sampling | S16 | FC03 | 1 | ° |  | RO
197 | Inverter Realtime Data | 0x84E6 | 34022 | Tiltangle 11 sampling | S16 | FC03 | 1 | ° |  | RO
198 | Inverter Realtime Data | 0x84E7 | 34023 | Azimuth 11 sampling | S16 | FC03 | 1 | ° |  | RO
199 | Inverter Realtime Data | 0x84E8 | 34024 | Tiltangle 12 sampling | S16 | FC03 | 1 | ° |  | RO
200 | Inverter Realtime Data | 0x84E9 | 34025 | Azimuth 12 sampling | S16 | FC03 | 1 | ° |  | RO
201 | Inverter Realtime Data | 0x84EA | 34026 | Tiltangle 13 sampling | S16 | FC03 | 1 | ° |  | RO
202 | Inverter Realtime Data | 0x84EB | 34027 | Bearing 13 sampling | S16 | FC03 | 1 | ° |  | RO
203 | Inverter Realtime Data | 0x84EC | 34028 | Tiltangle 14 sampling | S16 | FC03 | 1 | ° |  | RO
204 | Inverter Realtime Data | 0x84ED | 34029 | Azimuth 14 sampling | S16 | FC03 | 1 | ° |  | RO
205 | Inverter Realtime Data | 0x84EE | 34030 | Tiltangle 15 sampling | S16 | FC03 | 1 | ° |  | RO
206 | Inverter Realtime Data | 0x84EF | 34031 | Bearingangle 15 sampling | S16 | FC03 | 1 | ° |  | RO
207 | Inverter Realtime Data | 0x84F0 | 34032 | Tiltangle 16 sampling | S16 | FC03 | 1 | ° |  | RO
208 | Inverter Realtime Data | 0x84F1 | 34033 | Bearing 16 sampling | S16 | FC03 | 1 | ° |  | RO
209 | Inverter Realtime Data | 0x84F2 | 34034 | Trackingsystemcontroller | U16 | FC03 | 1 |  |  | RO
210 | Inverter Realtime Data | 0x84F3 | 34035 | Support System Type | U16 | FC03 | 1 |  |  | RO | If the vendor does not support a support type, the system returns the 03 error code.
211 | Inverter Realtime Data | 0x84F4 | 34036 | Operatingmode | U16 | FC03 | 1 |  |  | RO
212 | Inverter Realtime Data | 0x84F5 | 34037 | Totalnumberofstents | U16 | FC03 | 1 |  |  | RO | For dual-axis control, the maximum number of supports is 8.
213 | Inverter Realtime Data | 0x84F6 | 34038 | Supportaccessstatus | U32 | FC03 | 2 |  |  | RO | BIT0–BIT15: access status of support system 1–16; BIT16–BIT31: reserved for future expansion.
214 | Inverter Realtime Data | 0x84F8 | 34040 | Workingmodemask | U32 | FC03 | 2 |  |  | RO | Each bit indicates whether a working mode is supported.
215 | Inverter Realtime Data | 0x851B | 34075 | Support 1 General Fault Status | U16 | FC03 | 1 |  |  | RO | Data reported by the SmartLogger to the management system
216 | Inverter Realtime Data | 0x851C | 34076 | Support 1 user- definedfaultstatus | U16 | FC03 | 1 |  |  | RO | For details about the controller scenario definition, see the corresponding document. Data reported by the SmartLogger t
217 | Inverter Realtime Data | 0x851D | 34077 | Support 2 General Fault Status | U16 | FC03 | 1 |  |  | RO
218 | Inverter Realtime Data | 0x851E | 34078 | Support 2 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
219 | Inverter Realtime Data | 0x851F | 34079 | Support 3 General Fault Status | U16 | FC03 | 1 |  |  | RO
220 | Inverter Realtime Data | 0x8520 | 34080 | Support 3 user- definedfaultstatus | U16 | FC03 | 1 |  |  | RO
221 | Inverter Realtime Data | 0x8521 | 34081 | Support 4 General Fault Status | U16 | FC03 | 1 |  |  | RO
222 | Inverter Realtime Data | 0x8522 | 34082 | Support 4 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
223 | Inverter Realtime Data | 0x8523 | 34083 | Support 5 General Fault Status | U16 | FC03 | 1 |  |  | RO
224 | Inverter Realtime Data | 0x8524 | 34084 | Support 5 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
225 | Inverter Realtime Data | 0x8525 | 34085 | Support 6 General Fault Status | U16 | FC03 | 1 |  |  | RO
226 | Inverter Realtime Data | 0x8526 | 34086 | Support 6 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
227 | Inverter Realtime Data | 0x8527 | 34087 | Support 7 General Fault Status | U16 | FC03 | 1 |  |  | RO
228 | Inverter Realtime Data | 0x8528 | 34088 | Support 7 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
229 | Inverter Realtime Data | 0x8529 | 34089 | Support 8 General Fault Status | U16 | FC03 | 1 |  |  | RO
230 | Inverter Realtime Data | 0x852A | 34090 | Support 8 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
231 | Inverter Realtime Data | 0x852B | 34091 | Support 9 General Fault Status | U16 | FC03 | 1 |  |  | RO
232 | Inverter Realtime Data | 0x852C | 34092 | Support 9 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
233 | Inverter Realtime Data | 0x852D | 34093 | Support 10 General Fault Status | U16 | FC03 | 1 |  |  | RO
234 | Inverter Realtime Data | 0x852E | 34094 | Support 10 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
235 | Inverter Realtime Data | 0x852F | 34095 | Support 11 General Fault Status | U16 | FC03 | 1 |  |  | RO
236 | Inverter Realtime Data | 0x8530 | 34096 | Support 11 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
237 | Inverter Realtime Data | 0x8531 | 34097 | Support 12 General Fault Status | U16 | FC03 | 1 |  |  | RO
238 | Inverter Realtime Data | 0x8532 | 34098 | Support 12 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
239 | Inverter Realtime Data | 0x8533 | 34099 | Support 13 General Fault Status | U16 | FC03 | 1 |  |  | RO
240 | Inverter Realtime Data | 0x8534 | 34100 | Support 13 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
241 | Inverter Realtime Data | 0x8535 | 34101 | Support 14 General Fault Status | U16 | FC03 | 1 |  |  | RO
242 | Inverter Realtime Data | 0x8536 | 34102 | Support 14 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
243 | Inverter Realtime Data | 0x8537 | 34103 | Support 15 General Fault Status | U16 | FC03 | 1 |  |  | RO
244 | Inverter Realtime Data | 0x8538 | 34104 | Support 15 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
245 | Inverter Realtime Data | 0x8539 | 34105 | Support 16 General Fault Status | U16 | FC03 | 1 |  |  | RO
246 | Inverter Realtime Data | 0x853A | 34106 | Support 16 Custom Fault Status | U16 | FC03 | 1 |  |  | RO
247 | Inverter Realtime Data | 0x88B8 | 35000 | Runningtimeofcapacitorbank | U32 | FC03 | 2 | hour |  | RO | Used to inspect data.
248 | Inverter Realtime Data | 0x88BA | 35002 | Internalfan 1 runningtime | U32 | FC03 | 2 | hour |  | RO | Used to inspect data.
249 | Inverter Realtime Data | 0x88C2 | 35010 | Internalalarm | U16 | FC03 | 1 | V |  | RO | Used for R&D data storage.
250 | Inverter Realtime Data | 0x88CD | 35021 | Internal Temperature 1 | S16 | FC03 | 1 | °C |  | RO | Temperature of INV module A Used for R&D 5-minute data recording.
251 | Inverter Realtime Data | 0x88CE | 35022 | Internal Temperature 2 | S16 | FC03 | 1 | °C |  | RO | Temperature of INV module B Used for R&D 5-minute data recording.
252 | Inverter Realtime Data | 0x88CF | 35023 | Internal Temperature 3 | S16 | FC03 | 1 | °C |  | RO | INV module C temperature Used for R&D 5-minute data recording.
253 | Inverter Realtime Data | 0x88D0 | 35024 | Internal Temperature 4 | S16 | FC03 | 1 | °C |  | RO | Temperature sampling of anti-reverse module 1 Used for R&D 5-minute data recording.
254 | Inverter Realtime Data | 0x88D1 | 35025 | Internal Temperature 5 | S16 | FC03 | 1 | °C |  | RO | Output board relay, ambient temperature - maximum temperature Used for R&D 5-minute data recording.
255 | Inverter Realtime Data | 0x88D2 | 35026 | Internal Temperature 6 | S16 | FC03 | 1 | °C |  | RO | Output board, power board input, and power board inverter temperature sampling - maximum temperature Used for R&D 5-minu
256 | Inverter Realtime Data | 0x88D3 | 35027 | Internaltemperature 7 | S16 | FC03 | 1 | °C |  | RO | Temperature sampling of anti-reverse module 2 Used for R&D 5-minute data recording.
257 | Inverter Realtime Data | 0x88D4 | 35028 | Internaltemperature 8 | S16 | FC03 | 1 | °C |  | RO | DC terminal temperature 1 / 2 - maximum temperature Used for R&D 5-minute data recording.
258 | Inverter Realtime Data | 0x88D5 | 35029 | Internaltemperature 9 | S16 | FC03 | 1 | °C |  | RO | AC Terminal Temperature 1 / 2 / 3 - Maximum Temperature Used for R&D 5-minute data recording.
259 | Inverter Realtime Data | 0x88D6 | 35030 | Internaltemperature 10 | S16 | FC03 | 1 | °C |  | RO | Used for R&D data storage.
260 | Inverter Realtime Data | 0x88D7 | 35031 | Internaltemperature 11 | S16 | FC03 | 1 | °C |  | RO | Used for R&D data storage.
261 | Inverter Realtime Data | 0x88D8 | 35032 | Internaltemperature 12 | S16 | FC03 | 1 | °C |  | RO | Used for R&D data storage.
262 | Inverter Realtime Data | 0x88DE | 35038 | Phase A DC component DCI | S16 | FC03 | 1 | A |  | RO | Used for R&D 5-minute data recording.
263 | Inverter Realtime Data | 0x88DF | 35039 | Phase B DC component DCI | S16 | FC03 | 1 | A |  | RO | Used for R&D 5-minute data recording.
264 | Inverter Realtime Data | 0x88E0 | 35040 | Phase C DC component DCI | S16 | FC03 | 1 | A |  | RO | Used for R&D 5-minute data recording.
265 | Inverter Realtime Data | 0x88E1 | 35041 | Leakagecurrent RCD | S16 | FC03 | 1 | mA |  | RO | Used for R&D 5-minute data recording.
266 | Inverter Realtime Data | 0x88E2 | 35042 | Positivebusvoltage | S16 | FC03 | 1 | V |  | RO | Used for R&D 5-minute data recording.
267 | Inverter Realtime Data | 0x88E3 | 35043 | Negativebusvoltage | S16 | FC03 | 1 | V |  | RO | Used for R&D 5-minute data recording.
268 | Inverter Realtime Data | 0x88E4 | 35044 | BUS negativevoltagetoground | S16 | FC03 | 1 | V |  | RO | Used for R&D 5-minute data recording.
269 | Inverter Realtime Data | 0x8916 | 35094 | I-V scanstatus | U16 | FC03 | 1 |  |  | RO
270 | Inverter Realtime Data | 0x8917 | 35095 | I-V scanningcapability | U16 | FC03 | 1 |  |  | RO
271 | Inverter Realtime Data | 0x891E | 35102 | [Management System] NMS IP address | U32 | FC03 | 2 |  |  | RO | Indicates whether the NMS is successfully connected. After the NMS is connected, flil in the NMS IP address. If there is
272 | Inverter Realtime Data | 0x8920 | 35104 | [STA ] Wireless Routing Access Signal Strength | U16 | FC03 | 1 |  |  | RO | The FE status enumeration is used by the mobile app to effectively identify the current network conditions, switch icons
273 | Inverter Realtime Data | 0x8921 | 35105 | [STA ] WLA N listscanningstatus | U16 | FC03 | 1 |  |  | RO
274 | Inverter Realtime Data | 0x8922 | 35106 | Wifi- Mac | string | FC03 | 3 |  |  | RO
275 | Inverter Realtime Data | 0x8928 | 35112 | [NTP ] Last NTP synchronizationstatus. | U16 | FC03 | 1 |  |  | RO | 0: normal 1: abnormal
276 | Inverter Realtime Data | 0x8929 | 35113 | [NTP ] NTP Last Synchronization Time | U32 | FC03 | 2 |  |  | RO | Epoch Second
277 | Inverter Realtime Data | 0x892B | 35115 | Deferredactivationstate | U16 | FC03 | 1 |  |  | RO
278 | Inverter Realtime Data | 0x892C | 35116 | [4G] Monthlyusedtraffic | U32 | FC03 | 2 | MB |  | RO
279 | Inverter Realtime Data | 0x892E | 35118 | [4G] Monthly Remaining Traffic | U32 | FC03 | 2 | MB |  | RO
280 | Inverter Realtime Data | 0x8930 | 35120 | [4G] Averagedailytrafficusage | U32 | FC03 | 2 | MB |  | RO
281 | Inverter Realtime Data | 0x8932 | 35122 | [4G] Trafficstatus | U16 | FC03 | 1 |  |  | RO
282 | Inverter Realtime Data | 0x8934 | 35124 | [STA ] Routerconnectiontime | U16 | FC03 | 1 | s |  | RO | This parameter indicates the performance indicators for connecting the inverter or dongle to the router, and the duratio
283 | Inverter Realtime Data | 0x8935 | 35125 | [STA ] Routerconnectionstatus | U16 | FC03 | 1 |  |  | RO | Note: 3: Connection failure indicates that the route can be discovered normally and the password is correct but the resu
284 | Inverter Realtime Data | 0x8936 | 35126 | [FE] Connectionstatus | U16 | FC03 | 1 |  |  | RO | 0: not connected 1: being connected 2: successful connection 3: connection failure
285 | Inverter Realtime Data | 0x8940 | 35136 | [Smart I- V-V- Diagnosis ] Authorization Function | U32 | FC03 | 2 |  |  | RO | 2019-02-19 SEG of the Monitoring Development Dept: The original LicC does not support the scenario where different featu
286 | Inverter Realtime Data | 0x8942 | 35138 | Smart I- V-V- Diagnosis (License) Status | U16 | FC03 | 1 |  |  | RO
287 | Inverter Realtime Data | 0x8943 | 35139 | [Smart I- V-V- Diagnosis ] Licenseexpirationdate | EpochSecond | FC03 | 2 | s |  | RO | Epoch second 0XF2A52380 (2099-1-1) is reported, indicating that the setting takes effect permanently. If there is no lic
288 | Inverter Realtime Data | 0x8945 | 35141 | Licenseloadingtime | EpochSecond | FC03 | 2 | s |  | RO | Epoch Second
289 | Inverter Realtime Data | 0x8947 | 35143 | License Deregistration Time | EpochSecond | FC03 | 2 | s |  | RO | Epoch second 0XFFFFFFFF is reported when the status is not deregistered.
290 | Inverter Realtime Data | 0x8949 | 35145 | License SN | string | FC03 | 10 |  |  | RO
291 | Inverter Realtime Data | 0x8953 | 35155 | Invalidationcode . | string | FC03 | 64 |  |  | RO
292 | Inverter Realtime Data | 0x8993 | 35219 | Authorization Feature Signature | U16 | FC03 | 2 |  |  | RO | 1. If bit is set to 1, the function is licensed. 2. If the bit is cleared, the function does not need to be licensed on
293 | Inverter Realtime Data | 0x8995 | 35221 | [Stringmonitoring] Licensestatus | U16 | FC03 | 1 |  |  | RO | 0: no license; 1: normal; 2: grace period; 3: deregistered; 4: The SN does not match. 5: expired;
294 | Inverter Realtime Data | 0x8996 | 35222 | [String Monitoring] License Expiration Time | EpochSecond | FC03 | 2 | s |  | RO | Epoch Second If the feature status is normal, 0XF2A52380(2099-1-1) is reported, indicating that the feature takes effect
295 | Inverter Realtime Data | 0x89B1 | 35249 | [4G] Modulestatus | U16 | FC03 | 1 |  |  | RO
296 | Inverter Realtime Data | 0x89B2 | 35250 | [4G] IP address | U32 | FC03 | 2 |  |  | RO
297 | Inverter Realtime Data | 0x89B4 | 35252 | [4G] Subnet Mask | U32 | FC03 | 2 |  |  | RO
298 | Inverter Realtime Data | 0x89B6 | 35254 | [4G] IMEI | string | FC03 | 10 |  |  | RO
299 | Inverter Realtime Data | 0x89C0 | 35264 | [4G] signalstrength | U16 | FC03 | 1 |  |  | RO | 0 = No signal
300 | Inverter Realtime Data | 0x89C1 | 35265 | [4G] PIN numberinputtimes | U16 | FC03 | 1 |  |  | RO
301 | Inverter Realtime Data | 0x89C2 | 35266 | [4G] PIN checkstatus | U16 | FC03 | 1 |  |  | RO
302 | Inverter Realtime Data | 0x89E4 | 35300 | Activepoweradjustmentstatus | string | FC03 | 4 |  |  | RO
303 | Inverter Realtime Data | 0x89E8 | 35304 | Reactivepoweradjustmentstatus | string | FC03 | 4 |  |  | RO
304 | Inverter Realtime Data | 0x8CC1 | 36033 | Upgradestatus ID. | U16 | FC03 | 1 |  |  | RO | The flag is cleared each time the system is powered on. After the upgrade is successful, the flag is set to 1, indicatin
305 | Inverter Realtime Data | 0x9088 | 37000 | [Module 1] Runningstatusofthebattery | U16 | FC03 | 1 |  |  | RO
306 | Inverter Realtime Data | 0x90EC | 37100 | Meter Status | U16 | FC03 | 1 |  |  | RO
307 | Inverter Realtime Data | 0x90ED | 37101 | Gridvoltage (phase A voltage) | S32 | FC03 | 2 | V |  | RO
308 | Inverter Realtime Data | 0x90EF | 37103 | Phase B voltage | S32 | FC03 | 2 | V |  | RO
309 | Inverter Realtime Data | 0x90F1 | 37105 | Phase C voltage | S32 | FC03 | 2 | V |  | RO
310 | Inverter Realtime Data | 0x90F3 | 37107 | Gridcurrent (phase A current) | S32 | FC03 | 2 | A |  | RO
311 | Inverter Realtime Data | 0x90F5 | 37109 | Phase B current | S32 | FC03 | 2 | A |  | RO
312 | Inverter Realtime Data | 0x90F7 | 37111 | Phase C current | S32 | FC03 | 2 | A |  | RO
313 | Inverter Realtime Data | 0x90F9 | 37113 | Activepower | S32 | FC03 | 2 | W |  | RO | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
314 | Inverter Realtime Data | 0x90FB | 37115 | reactivepower | S32 | FC03 | 2 | Var |  | RO
315 | Inverter Realtime Data | 0x90FD | 37117 | Powerfactor | S16 | FC03 | 1 |  |  | RO
316 | Inverter Realtime Data | 0x90FE | 37118 | Gridfrequency | S16 | FC03 | 1 | Hz |  | RO
317 | Inverter Realtime Data | 0x90FF | 37119 | Positiveactivepower | S32 | FC03 | 2 | kWh |  | RO | Inverter power fed to the grid
318 | Inverter Realtime Data | 0x9101 | 37121 | Reverseactivepower | S32 | FC03 | 2 | kWh |  | RO | Electricity absorbed by the distributed system from the grid
319 | Inverter Realtime Data | 0x9103 | 37123 | Accumulatedreactivepower | S32 | FC03 | 2 | kVarh |  | RO
320 | Inverter Realtime Data | 0x9105 | 37125 | Meter Type | U16 | FC03 | 1 |  |  | RO
321 | Inverter Realtime Data | 0x9106 | 37126 | A-B linevoltage | S32 | FC03 | 2 | V |  | RO
322 | Inverter Realtime Data | 0x9108 | 37128 | BC linevoltage | S32 | FC03 | 2 | V |  | RO
323 | Inverter Realtime Data | 0x910A | 37130 | CA linevoltage | S32 | FC03 | 2 | V |  | RO
324 | Inverter Realtime Data | 0x910C | 37132 | Phase A activepower | S32 | FC03 | 2 | W |  | RO | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
325 | Inverter Realtime Data | 0x910E | 37134 | Phase B activepower | S32 | FC03 | 2 | W |  | RO | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
326 | Inverter Realtime Data | 0x9110 | 37136 | Phase C activepower | S32 | FC03 | 2 | W |  | RO | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
327 | Inverter Realtime Data | 0x9112 | 37138 | Meter Model Check Result | U16 | FC03 | 1 |  |  | RO
328 | Inverter Realtime Data | 0x9150 | 37200 | Totalnumberofoptimizers | U16 | FC03 | 1 |  |  | RO
329 | Inverter Realtime Data | 0x9151 | 37201 | Numberofonlineoptimizers | U16 | FC03 | 1 |  |  | RO
330 | Inverter Realtime Data | 0x9152 | 37202 | Featuredatasequencenumber | U16 | FC03 | 1 |  |  | RO
331 | Inverter Realtime Data | 0x9153 | 37203 | Physical Location Locating Progress | U16 | FC03 | 1 |  |  | RO
332 | Inverter Realtime Data | 0x9154 | 37204 | Logexportprogress | U16 | FC03 | 1 |  |  | RO
333 | Inverter Realtime Data | 0x9155 | 37205 | Real - timedataqueryprogress | U16 | FC03 | 1 |  |  | RO
334 | Inverter Realtime Data | 0x9156 | 37206 | Currentstatusofthephysicallocation | U16 | FC03 | 1 |  |  | RO
335 | Inverter Realtime Data | 0x9157 | 37207 | Numberof Searched Optimizers | U16 | FC03 | 1 |  |  | RO
336 | Inverter Realtime Data | 0x9158 | 37208 | Relative Positioning Status | U16 | FC03 | 1 |  |  | RO | The previous result needs to be solidified and retained after a power failure.
337 | Inverter Realtime Data | 0x9159 | 37209 | Layout File Storage Progress | U16 | FC03 | 1 | % |  | RO | 0xff : indicates that saving the data fails.
338 | Inverter Realtime Data | 0x915A | 37210 | Layout File Change SN | U16 | FC03 | 1 |  |  | RO
339 | Inverter Realtime Data | 0x915B | 37211 | Disconnectiondetectionprogress | U16 | FC03 | 1 | % |  | RO | Other values are error codes. Error code definitions are as follows: 0xfe02: Off-grid running, operation forbidden 0xfe0
340 | Inverter Realtime Data | 0x915C | 37212 | Disconnectedstatus | U16 | FC03 | 1 |  |  | RO
341 | Inverter Realtime Data | 0x9182 | 37250 | [DC- MBU S] Networkingstatus | U16 | FC03 | 1 |  |  | RO
342 | Inverter Realtime Data | 0x9183 | 37251 | Numberof Networked Networks | U16 | FC03 | 1 |  |  | RO
343 | Inverter Realtime Data | 0x9184 | 37252 | Numberofneighboringnetworks | U16 | FC03 | 1 |  |  | RO
344 | Inverter Realtime Data | 0x9185 | 37253 | Fast Shutdown Self Test Status | U16 | FC03 | 1 |  |  | RO | 0: not executed, indicating that the system life cycle has never been executed. The previous result needs to be solidifi
345 | Inverter Realtime Data | 0x9186 | 37254 | Runningstatus | U16 | FC03 | 1 |  |  | RO
346 | Inverter Realtime Data | 0x9187 | 37255 | SN | string | FC03 | 10 |  |  | RO
347 | Inverter Realtime Data | 0x9218 | 37400 | SN | string | FC03 | 10 |  |  | RO
348 | Inverter Realtime Data | 0x9222 | 37410 | Type | U16 | FC03 | 1 |  |  | RO
349 | Inverter Realtime Data | 0x9235 | 37429 | Maximumnumberofconnecteddevices | U16 | FC03 | 1 |  |  | RO
350 | Inverter Realtime Data | 0x9236 | 37430 | RAT | string | FC03 | 10 |  |  | RO
351 | Inverter Realtime Data | 0x9240 | 37440 | Carriers | string | FC03 | 15 |  |  | RO | The default value is reported when no query is found.
352 | Inverter Realtime Data | 0x925E | 37470 | Totalratedcapacityofgrid- tiedinverters | U32 | FC03 | 2 | kW |  | RO | Difference from plant capacity: refers only to the total capacity of online grid- tied inverters.
353 | Inverter Realtime Data | 0x9260 | 37472 | Conversionfactor | U32 | FC03 | 2 |  |  | RO | Percentage of current control/percentage of control delivered by the electric power company
354 | Inverter Realtime Data | 0x9262 | 37474 | Current Percentage | U16 | FC03 | 1 | % |  | RO
355 | Inverter Realtime Data | 0x9263 | 37475 | [Scheduleserver] Communicationstatus | U16 | FC03 | 1 |  |  | RO | Dongle and Japan Electric Power Huawei server communication status (only for third-party NMSs in Japan): Dispatching ser
356 | Inverter Realtime Data | 0x9264 | 37476 | [Scheduleserver] Latestconnectionstatus | U16 | FC03 | 1 |  |  | RO
357 | Inverter Realtime Data | 0x9265 | 37477 | [Scheduleserver] Latestconnectiontime | U32 | FC03 | 2 |  |  | RO
358 | Inverter Realtime Data | 0x9267 | 37479 | Softwareversion | string | FC03 | 15 |  |  | RO | Dongle firmware version
359 | Inverter Realtime Data | 0x9276 | 37494 | Numberofconnecteddevices | U16 | FC03 | 1 |  |  | RO
360 | Inverter Realtime Data | 0x9278 | 37496 | Silenceflag | U16 | FC03 | 1 |  |  | RO | Note: This API is used only to synchronize dongle silence between the mobile app and inverter. Wait for the dongle to ex
361 | Inverter Realtime Data | 0x9279 | 37497 | Upgrade Status | U16 | FC03 | 1 |  |  | RO
362 | Inverter Realtime Data | 0x928E | 37518 | Invertercomprehensivestatus | U16 | FC03 | 1 |  |  | RO
363 | Inverter Realtime Data | 0x928F | 37519 | Inverterintegratedstatussupportflag | U16 | FC03 | 1 |  |  | RO
--- Inverter Parameters (Setup) ---
364 | Inverter Parameters (Setup) | 0x9C40 | 40000 | Systemtime (localtime ) | EpochSecond | FC03/FC06 | 2 | s |  | RW | The data is in the epoch second format, that is, the local time.
365 | Inverter Parameters (Setup) | 0x9C65 | 40037 | Q-U characteristiccurvemode | U16 | FC03/FC06 | 1 |  |  | RW
366 | Inverter Parameters (Setup) | 0x9C66 | 40038 | Q-U Scheduling Trigger Power Percentage | S16 | FC03/FC06 | 1 | % |  | RW
367 | Inverter Parameters (Setup) | 0x9CB8 | 40120 | Activepowerisderatedbyafixedvalue. | U16 | FC03/FC06 | 1 | kW |  | RW
368 | Inverter Parameters (Setup) | 0x9CBA | 40122 | Powerfactor | S16 | FC03/FC06 | 1 |  |  | RW
369 | Inverter Parameters (Setup) | 0x9CBB | 40123 | Reactivepowercompensation (Q/S ) [lowprecision] | S16 | FC03/FC06 | 1 |  |  | RW | The equipment end converts the value into a fxied Q value for reactive power control. S is Smax.
370 | Inverter Parameters (Setup) | 0x9CBC | 40124 | Reactivepoweradjustmenttime | U16 | FC03/FC06 | 1 | s |  | RW | Change requirement: The "Reactive power adjustment time" broadcast interface is added to the Q-P characteristic curve an
371 | Inverter Parameters (Setup) | 0x9CBD | 40125 | Activepowerpercentagederating (lowprecision) | S16 | FC03/FC06 | 1 | % |  | RW | Active power fni e adjustment interface
372 | Inverter Parameters (Setup) | 0x9CBE | 40126 | Activepowerisderatedbyafixedvalue. | U32 | FC03/FC06 | 2 | W |  | RW | Value range: [0, Pmax]
373 | Inverter Parameters (Setup) | 0x9CC0 | 40128 | Nightreactivepowercompensation (Q/S ) | S16 | FC03/FC06 | 1 |  |  | RW | The equipment end converts the value into a fixed Q value for reactive power control. S is Smax.
374 | Inverter Parameters (Setup) | 0x9CC1 | 40129 | Fixedvalueofreactivepoweratnight | S32 | FC03/FC06 | 2 | kVar |  | RW
375 | Inverter Parameters (Setup) | 0x9CC5 | 40133 | Cos? - P/Pncharacteristiccurve | string | FC03/FC06 | 21 |  |  | RW
376 | Inverter Parameters (Setup) | 0x9CDA | 40154 | Q-U characteristiccurve | string | FC03/FC06 | 21 |  |  | RW
377 | Inverter Parameters (Setup) | 0x9CEF | 40175 | PF-U characteristiccurve | string | FC03/FC06 | 21 |  |  | RW
378 | Inverter Parameters (Setup) | 0x9D04 | 40196 | [Characteristiccurve] Reactivepoweradjustmenttime | U16 | FC03/FC06 | 1 | s |  | RW | Change requirement: The "Reactive power adjustment time" broadcast interface is added to the Q-P characteristic curve an
379 | Inverter Parameters (Setup) | 0x9D06 | 40198 | Q-U Scheduling Exit Power Percentage | S16 | FC03/FC06 | 1 | % |  | RW
380 | Inverter Parameters (Setup) | 0x9D07 | 40199 | Activepowerpercentagecontrol [lowprecision] | S16 | FC03/FC06 | 1 | % |  | RW | This interface is used in distributed mode. It is used to control the active power percentage. It is issued to the power
381 | Inverter Parameters (Setup) | 0x9D08 | 40200 | Startthesystem. | U16 | FC06 | 1 |  |  | WO
382 | Inverter Parameters (Setup) | 0x9D09 | 40201 | Shutdown. | U16 | FC06 | 1 |  |  | WO
383 | Inverter Parameters (Setup) | 0x9D0A | 40202 | Quickpower- onandpower- off | U16 | FC06 | 1 |  |  | WO | Not affected by shutdown gradient
384 | Inverter Parameters (Setup) | 0x9D0D | 40205 | reset | U16 | FC06 | 1 |  |  | WO | After receiving the command, the DSP responds immediately and then resets. After receiving the command, the inverter mon
385 | Inverter Parameters (Setup) | 0x9D0E | 40206 | Insulationimpedancediagnosis | U16 | FC06 | 1 |  |  | WO | [0, 1], 1 action After receiving the instruction, the inverter restarts and performs insulation impedance detection.
386 | Inverter Parameters (Setup) | 0x9D6C | 40300 | Dry Contact Scheduling Settings | string | FC03/FC06 | 33 |  |  | RW
387 | Inverter Parameters (Setup) | 0x9DA2 | 40354 | Q-P characteristiccurve | string | FC03/FC06 | 21 |  |  | RW
388 | Inverter Parameters (Setup) | 0x9DB7 | 40375 | Q-U characteristiccurveminimum PF limit | U16 | FC03/FC06 | 1 |  |  | RW | This MPI is used to limit the reactive power output by the QU curve by limiting the current PF value. The country code t
389 | Inverter Parameters (Setup) | 0x9DB8 | 40376 | Q-U characteristiccurvevaliditydelaytime | U16 | FC03/FC06 | 1 | s |  | RW | After the QU curve reaches the trigger voltage, the reactive power starts to change after a period of time is delayed. I
390 | Inverter Parameters (Setup) | 0x9E34 | 40500 | System Time (UTC ) | EpochSecond | FC06 | 2 | s |  | WO | The data is in the UTC time format.
391 | Inverter Parameters (Setup) | 0xA410 | 42000 | Powergridstandardcode | U16 | FC03/FC06 | 1 |  |  | RW | CHINA MV800 _ For details about the scope, see the Power Grid Standard Code.
392 | Inverter Parameters (Setup) | 0xA411 | 42001 | Outputmode | U16 | FC03/FC06 | 1 |  |  | RW | On the customer interface, only read signals can be displayed. Currently, only three-phase three-wire signals are suppor
393 | Inverter Parameters (Setup) | 0xA412 | 42002 | Voltagelevel | U16 | FC03/FC06 | 1 | V |  | RW | Vn
394 | Inverter Parameters (Setup) | 0xA413 | 42003 | Frequency Class | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn
395 | Inverter Parameters (Setup) | 0xA41C | 42012 | Replacethetargetmodel. | U16 | FC03/FC06 | 1 |  |  | RW | Enumerated ID of the inverter model. For details, see the Inverter Model Defni ition. The default value is 65535 (0xFFFF
396 | Inverter Parameters (Setup) | 0xA41E | 42014 | Remotepowerscheduling | U16 | FC03/FC06 | 1 |  |  | RW | 0：Disable 1：Enable If this parameter is disabled, the inverter will be locked.
397 | Inverter Parameters (Setup) | 0xA41F | 42015 | reactivepowergradient | U32 | FC03/FC06 | 2 | %/s |  | RW
398 | Inverter Parameters (Setup) | 0xA421 | 42017 | Activepowerchangegradient | U32 | FC03/FC06 | 2 | %/s |  | RW | Limits the speed at which the power changes caused by the power scheduling command
399 | Inverter Parameters (Setup) | 0xA423 | 42019 | Scheduledinstructionholdtime | U32 | FC03/FC06 | 2 | s |  | RW | Permanently valid when the value is 0.
400 | Inverter Parameters (Setup) | 0xA425 | 42021 | Maximumapparentpower | U32 | FC03/FC06 | 2 | kVA |  | RW | ["Maximum active power",Smax]
401 | Inverter Parameters (Setup) | 0xA427 | 42023 | Maximumactivepower | U32 | FC03/FC06 | 2 | kW |  | RW | [0.1,Pmax]
402 | Inverter Parameters (Setup) | 0xA429 | 42025 | apparentpowerreference | U32 | FC03/FC06 | 2 | kVar |  | RW | Sn: upper limit of the maximum active power (PMax), which is used as the reference for reactive power scheduling (Q/S).
403 | Inverter Parameters (Setup) | 0xA42B | 42027 | Activepowerreference | U32 | FC03/FC06 | 2 | kW |  | RW | Set the lower limit of the maximum apparent value (SMax), which is also used as the reference for active power schedulin
404 | Inverter Parameters (Setup) | 0xA42D | 42029 | Plantactivepowergradient | U16 | FC03/FC06 | 1 | min/100% |  | RW | China standards require that the active power change caused by light fluctuation must meet the speed requirements during
405 | Inverter Parameters (Setup) | 0xA42E | 42030 | Plantactiveaveragefilteringtime | U32 | FC03/FC06 | 2 | ms |  | RW
406 | Inverter Parameters (Setup) | 0xA430 | 42032 | Filteringtimefor PF-U voltagedetection | U16 | FC03/FC06 | 1 | s |  | RW
407 | Inverter Parameters (Setup) | 0xA431 | 42033 | Drycontactscheduling | U16 | FC03/FC06 | 1 |  |  | RW
408 | Inverter Parameters (Setup) | 0xA432 | 42034 | Audibleandvisualalarm | U16 | FC03/FC06 | 1 |  |  | RW
409 | Inverter Parameters (Setup) | 0xA438 | 42040 | Frequency Active Power Derating Recovery Delay Time | U16 | FC03/FC06 | 1 | s |  | RW
410 | Inverter Parameters (Setup) | 0xA439 | 42041 | Frequency Active Power Derating Effective Delay Time | U16 | FC03/FC06 | 1 | ms |  | RW
411 | Inverter Parameters (Setup) | 0xA43A | 42042 | Frequencyactivepowerderatinghysteresis | U16 | FC03/FC06 | 1 |  |  | RW
412 | Inverter Parameters (Setup) | 0xA43B | 42043 | Frequencymodulationcontrolresponsedeadband | U16 | FC03/FC06 | 1 | Hz |  | RW
413 | Inverter Parameters (Setup) | 0xA43C | 42044 | Of-fgridswitchovermode | U16 | FC03/FC06 | 1 |  |  | RW
414 | Inverter Parameters (Setup) | 0xA43D | 42045 | Off- gridmode | U16 | FC03/FC06 | 1 |  |  | RW
415 | Inverter Parameters (Setup) | 0xA43E | 42046 | PQ mode | U16 | FC03/FC06 | 1 |  |  | RW
416 | Inverter Parameters (Setup) | 0xA43F | 42047 | PV Panel Type | U16 | FC03/FC06 | 1 |  |  | RW
417 | Inverter Parameters (Setup) | 0xA440 | 42048 | PID compensationdirection | U16 | FC03/FC06 | 1 |  |  | RW
418 | Inverter Parameters (Setup) | 0xA441 | 42049 | Stringconnectionmode | U16 | FC03/FC06 | 1 |  |  | RW
419 | Inverter Parameters (Setup) | 0xA442 | 42050 | Isolation Settings | U16 | FC03/FC06 | 1 |  |  | RW | On the customer interface, only read signals can be displayed. Currently, only the input is not grounded and transformer
420 | Inverter Parameters (Setup) | 0xA443 | 42051 | Frequencymodulationcontrolpowerchangegradient | U16 | FC03/FC06 | 1 | %/min |  | RW
421 | Inverter Parameters (Setup) | 0xA444 | 42052 | Frequencymodulationcontrolpowerchangelimitingamplitude | U16 | FC03/FC06 | 1 | % |  | RW
422 | Inverter Parameters (Setup) | 0xA445 | 42053 | FM controldelayresponsetime | U16 | FC03/FC06 | 1 | ms |  | RW | Polish national requirements, open and configurable Initial delay in the frequency sensitive mode
423 | Inverter Parameters (Setup) | 0xA446 | 42054 | MPP T multimodalscanning | U16 | FC03/FC06 | 1 |  |  | RW
424 | Inverter Parameters (Setup) | 0xA447 | 42055 | MPP T scanninginterval | U16 | FC03/FC06 | 1 | min |  | RW
425 | Inverter Parameters (Setup) | 0xA448 | 42056 | Predicted MPP T power | U32 | FC03 | 2 | kW |  | RO
426 | Inverter Parameters (Setup) | 0xA44D | 42061 | Powergridfaultrecoveryautomaticstartup | U16 | FC03/FC06 | 1 |  |  | RW
427 | Inverter Parameters (Setup) | 0xA44E | 42062 | Powerlimit 0% shutdown | U16 | FC03/FC06 | 1 |  |  | RW
428 | Inverter Parameters (Setup) | 0xA44F | 42063 | Automaticpower- offwhencommunicationisdisconnected | U16 | FC03/FC06 | 1 |  |  | RW | In a parallel system, the system automatically shuts down when the communication link is interrupted by default. The com
429 | Inverter Parameters (Setup) | 0xA450 | 42064 | Automaticpower- onaftercommunicationrecovery | U16 | FC03/FC06 | 1 |  |  | RW
430 | Inverter Parameters (Setup) | 0xA451 | 42065 | Power Quality Optimization Mode | U16 | FC03/FC06 | 1 |  |  | RW
431 | Inverter Parameters (Setup) | 0xA452 | 42066 | RCD Enhancement | U16 | FC03/FC06 | 1 |  |  | RW
432 | Inverter Parameters (Setup) | 0xA453 | 42067 | Nightreactivepower | U16 | FC03/FC06 | 1 |  |  | RW
433 | Inverter Parameters (Setup) | 0xA454 | 42068 | Abnormalgroundingshutdown | U16 | FC03/FC06 | 1 |  |  | RW
434 | Inverter Parameters (Setup) | 0xA455 | 42069 | Night PID protection | U16 | FC03/FC06 | 1 |  |  | RW
435 | Inverter Parameters (Setup) | 0xA456 | 42070 | Nightreactivepowerparameterstakeeffect | U16 | FC03/FC06 | 1 |  |  | RW
436 | Inverter Parameters (Setup) | 0xA458 | 42072 | Communication Disconnection Detection Time | U16 | FC03/FC06 | 1 | s |  | RW | This parameter is displayed when the protection against communication disconnection is enabled.
437 | Inverter Parameters (Setup) | 0xA459 | 42073 | AFCI | U16 | FC03/FC06 | 1 |  |  | RW
438 | Inverter Parameters (Setup) | 0xA45A | 42074 | AFCI detectionadaptationmode | U16 | FC03/FC06 | 1 |  |  | RW
439 | Inverter Parameters (Setup) | 0xA45B | 42075 | Communicationlinkfailureprotection | U16 | FC03/FC06 | 1 |  |  | RW | Used to initiate the security protection function after the communication between the device and the northbound interfac
440 | Inverter Parameters (Setup) | 0xA45C | 42076 | Failureprotectionactivepowermode | U16 | FC03/FC06 | 1 |  |  | RW | This parameter is displayed when the protection against communication disconnection is enabled.
441 | Inverter Parameters (Setup) | 0xA45D | 42077 | Active Power Limitfor Failure Protection [kW] [Low Precision] | U32 | FC03/FC06 | 2 | kW |  | RW | This parameter is displayed only when the communication link failure protection is set to Enable and the active power mo
442 | Inverter Parameters (Setup) | 0xA45F | 42079 | Failureprotectionreactivepowermode | U16 | FC03/FC06 | 1 |  |  | RW | This parameter is displayed when the protection against communication disconnection is enabled.
443 | Inverter Parameters (Setup) | 0xA460 | 42080 | Frequencyrateprotection | U16 | FC03/FC06 | 1 |  |  | RW
444 | Inverter Parameters (Setup) | 0xA461 | 42081 | Frequencychangerateprotectionpoint | U16 | FC03/FC06 | 1 | Hz/s |  | RW
445 | Inverter Parameters (Setup) | 0xA462 | 42082 | Frequencychangerateprotectiontime | U16 | FC03/FC06 | 1 | s |  | RW
446 | Inverter Parameters (Setup) | 0xA463 | 42083 | Reactivepowerlimitforfailureprotection [Q/S ] [lowprecision] | S16 | FC03/FC06 | 1 |  |  | RW | (Deliver Q/S value) This parameter is displayed only when Communication Disconnection Failure Protection is set to Enabl
447 | Inverter Parameters (Setup) | 0xA464 | 42084 | Power- onvoltageupperlimitforgridconnection | U16 | FC03/FC06 | 1 | V |  | RW | Parameters for normal reconnection
448 | Inverter Parameters (Setup) | 0xA465 | 42085 | Power- onvoltagelowerlimitforgridconnection | U16 | FC03/FC06 | 1 | V |  | RW | Parameters for normal reconnection
449 | Inverter Parameters (Setup) | 0xA466 | 42086 | Power- onfrequencyupperlimitforgridconnection | U16 | FC03/FC06 | 1 | Hz |  | RW | Parameters for normal reconnection
450 | Inverter Parameters (Setup) | 0xA467 | 42087 | Power- onfrequencylowerlimitforgridconnection | U16 | FC03/FC06 | 1 | Hz |  | RW | Parameters for normal reconnection
451 | Inverter Parameters (Setup) | 0xA468 | 42088 | Powergridreconnectionvoltageupperlimit | U16 | FC03/FC06 | 1 | V |  | RW | Parameters for reconnection after a fault
452 | Inverter Parameters (Setup) | 0xA469 | 42089 | Power Grid Reconnection Voltage Lower Threshold | U16 | FC03/FC06 | 1 | V |  | RW | Parameters for reconnection after a fault
453 | Inverter Parameters (Setup) | 0xA46A | 42090 | Powergridreconnectionfrequencyupperlimit | U16 | FC03/FC06 | 1 | Hz |  | RW | Parameters for reconnection after a fault
454 | Inverter Parameters (Setup) | 0xA46B | 42091 | Powergridreconnectionfrequencylowerlimit | U16 | FC03/FC06 | 1 | Hz |  | RW | Parameters for reconnection after a fault
455 | Inverter Parameters (Setup) | 0xA46C | 42092 | Automatic Power Grid Reconnection Time | U16 | FC03/FC06 | 1 | s |  | RW
456 | Inverter Parameters (Setup) | 0xA471 | 42097 | Insulationimpedanceprotectionpoint | U16 | FC03/FC06 | 1 | MΩ |  | RW | Value range: [0.02, 1.5] Actual protection is implemented by the inverter based on the DC voltage. 600 V DC inverter: [0
457 | Inverter Parameters (Setup) | 0xA472 | 42098 | Voltageunbalanceprotectionthreshold | U16 | FC03/FC06 | 1 | % |  | RW
458 | Inverter Parameters (Setup) | 0xA473 | 42099 | Phaseprotectionpoint | U16 | FC03/FC06 | 1 | ° |  | RW
459 | Inverter Parameters (Setup) | 0xA474 | 42100 | Power- onsoftstarttimeduetopowergridfaults | U16 | FC03/FC06 | 1 | s |  | RW | Power rise gradient during equipment startup after a power grid fault
460 | Inverter Parameters (Setup) | 0xA475 | 42101 | Cos? - P/Pntriggervoltage | U16 | FC03/FC06 | 1 | % |  | RW
461 | Inverter Parameters (Setup) | 0xA476 | 42102 | Cos? - P/Pnexitvoltage | U16 | FC03/FC06 | 1 | % |  | RW
462 | Inverter Parameters (Setup) | 0xA477 | 42103 | Startupsoftstarttime | U16 | FC03/FC06 | 1 | s |  | RW
463 | Inverter Parameters (Setup) | 0xA478 | 42104 | Powergridfaultrecoverytime | U16 | FC03/FC06 | 1 | s |  | RW
464 | Inverter Parameters (Setup) | 0xA479 | 42105 | Timefordeterminingshort - termpowergridinterruption | U32 | FC03/FC06 | 2 | ms |  | RW | Quick Start After Power Grid Fault is enabled and can be set.
465 | Inverter Parameters (Setup) | 0xA47B | 42107 | Shutdowngradient | U32 | FC03/FC06 | 2 | %/s |  | RW
466 | Inverter Parameters (Setup) | 0xA47D | 42109 | Linelosscompensation | U16 | FC03/FC06 | 1 | % |  | RW
467 | Inverter Parameters (Setup) | 0xA47E | 42110 | Gridfaultzerocurrentmode | U16 | FC03/FC06 | 1 |  |  | RW
468 | Inverter Parameters (Setup) | 0xA47F | 42111 | Gridvoltagejumptriggerthreshold | U16 | FC03/FC06 | 1 | % |  | RW | This parameter can be set only for the VDE4120.
469 | Inverter Parameters (Setup) | 0xA480 | 42112 | HVR T | U16 | FC03/FC06 | 1 |  |  | RW
470 | Inverter Parameters (Setup) | 0xA481 | 42113 | HVR T Trigger Threshold | U16 | FC03/FC06 | 1 | V |  | RW
471 | Inverter Parameters (Setup) | 0xA482 | 42114 | HVR T positivesequencereactivepowercompensationfactor | U16 | FC03/FC06 | 1 |  |  | RW
472 | Inverter Parameters (Setup) | 0xA483 | 42115 | V phasetoground | U16 | FC03/FC06 | 1 |  |  | RW | For the medium-three- phase 20KTL-M3 model in Japan, the phase wire on the side where the transformer is connected to th
473 | Inverter Parameters (Setup) | 0xA484 | 42116 | Short- termpowergridinterruptionandquickstartup | U16 | FC03/FC06 | 1 |  |  | RW | Indicates whether to enable the fast startup function after the power grid recovers from a short-term interruption. If t
474 | Inverter Parameters (Setup) | 0xA486 | 42118 | LVRT activecurrentmaintenancecoefficient | U16 | FC03/FC06 | 1 |  |  | RW
475 | Inverter Parameters (Setup) | 0xA487 | 42119 | LVRT | U16 | FC03/FC06 | 1 |  |  | RW | By default, this function is enabled in the BDEW standard. In other standards, this function is disabled by default.
476 | Inverter Parameters (Setup) | 0xA488 | 42120 | LVRT Trigger Threshold | U16 | FC03/FC06 | 1 | V |  | RW | Sets the threshold for triggering low voltage ride- through. The threshold must comply with the local power grid standar
477 | Inverter Parameters (Setup) | 0xA489 | 42121 | Powergridvoltageprotectionshieldduring VRT | U16 | FC03/FC06 | 1 |  |  | RW | It is used to set whether the voltage protection function needs to be shielded during the voltage ride-through.
478 | Inverter Parameters (Setup) | 0xA48A | 42122 | LVRT positivesequencereactivepowercompensationfactor | U16 | FC03/FC06 | 1 |  |  | RW | During the low voltage ride through (LVRT), the device needs to generate positive- sequence reactive power to support th
479 | Inverter Parameters (Setup) | 0xA48B | 42123 | VRT exithysteresisthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Sets the LVRT/HVRT recovery threshold. LVRT recovery threshold = LVRT trigger threshold + VRT exit hysteresis threshold
480 | Inverter Parameters (Setup) | 0xA48C | 42124 | VRT activecurrentlimitingpercentage | U16 | FC03/FC06 | 1 | % |  | RW
481 | Inverter Parameters (Setup) | 0xA48D | 42125 | VRT activepowerrecoverygradient | U16 | FC03/FC06 | 1 | %/s |  | RW
482 | Inverter Parameters (Setup) | 0xA48E | 42126 | HVR T negativesequencereactivecompensationfactor | U16 | FC03/FC06 | 1 |  |  | RW
483 | Inverter Parameters (Setup) | 0xA48F | 42127 | LVRT negativesequencereactivepowercompensationfactor | U16 | FC03/FC06 | 1 |  |  | RW | During low voltage ride through (LVRT), the device needs to generate negative- sequence reactive power to support the po
484 | Inverter Parameters (Setup) | 0xA490 | 42128 | phaseangledeviationprotection | U16 | FC03/FC06 | 1 |  |  | RW
485 | Inverter Parameters (Setup) | 0xA491 | 42129 | Active Islanding Protection | U16 | FC03/FC06 | 1 |  |  | RW
486 | Inverter Parameters (Setup) | 0xA492 | 42130 | Passive Islanding Protection | U16 | FC03/FC06 | 1 |  |  | RW
487 | Inverter Parameters (Setup) | 0xA493 | 42131 | OVG R Associated Shutdown | U16 | FC03/FC06 | 1 |  |  | RW
488 | Inverter Parameters (Setup) | 0xA494 | 42132 | Drycontactfunction | U16 | FC03/FC06 | 1 |  |  | RW
489 | Inverter Parameters (Setup) | 0xA495 | 42133 | LVRT reactivecurrentlimitingpercentage | U16 | FC03/FC06 | 1 | % |  | RW | During low voltage ride- through, the equipment needs to limit the reactive current emitted by the equipment. For exampl
490 | Inverter Parameters (Setup) | 0xA496 | 42134 | LVRT zerocurrentmodethreshold | U16 | FC03/FC06 | 1 | V |  | RW | If the zero current mode is enabled and the voltage of the grid is less than the zero current mode threshold during LVRT
491 | Inverter Parameters (Setup) | 0xA497 | 42135 | LVRT mode | U16 | FC03/FC06 | 1 |  |  | RW
492 | Inverter Parameters (Setup) | 0xA498 | 42136 | RCD currentlimit | U16 | FC03/FC06 | 1 | mA |  | RW
493 | Inverter Parameters (Setup) | 0xA49A | 42138 | Voltagerisesuppression | U16 | FC03/FC06 | 1 |  |  | RW
494 | Inverter Parameters (Setup) | 0xA49B | 42139 | Voltagerisesuppressionreactivepoweradjustmentpoint | U16 | FC03/FC06 | 1 | % |  | RW | The value of "Voltage Rise Reject Active Derating Point" must be greater than the value of "Voltage Rise Reject Reactive
495 | Inverter Parameters (Setup) | 0xA49C | 42140 | Voltagerisesuppressionactivederatingthreshold | U16 | FC03/FC06 | 1 | % |  | RW | The value of "Voltage Rise Reject Active Derating Point" must be greater than the value of "Voltage Rise Reject Reactive
496 | Inverter Parameters (Setup) | 0xA49D | 42141 | frequencymodulationcontrol | U16 | FC03/FC06 | 1 |  |  | RW | According to the standards of some countries or regions, the power grid frequency changes around the rated value. If the
497 | Inverter Parameters (Setup) | 0xA49E | 42142 | frequencymodulationcontroldifferentialmodulationrate | U16 | FC03/FC06 | 1 | % |  | RW | Frequency sensitive mode (FSM) Droop, which is required by the G99 standard.
498 | Inverter Parameters (Setup) | 0xA49F | 42143 | Overfrequencyderating | U16 | FC03/FC06 | 1 |  |  | RW | If this parameter is set to Enable, the device derates the active power based on a certain gradient when the power grid
499 | Inverter Parameters (Setup) | 0xA4A0 | 42144 | Overfrequencyderatingcutofffrequency | U16 | FC03/FC06 | 1 | Hz |  | RW | Specifeis the cutoff frequency for overfrequency derating.
500 | Inverter Parameters (Setup) | 0xA4A1 | 42145 | Overfrequencyderatingcut- offpower | U16 | FC03/FC06 | 1 | % |  | RW | Indicates the cutoff power point for overfrequency derating.
501 | Inverter Parameters (Setup) | 0xA4A2 | 42146 | Triggeringfrequencyofoverfrequencyderating | U16 | FC03/FC06 | 1 | Hz |  | RW | According to the standards in some countries or regions, the active power output by the device must be derated when the
502 | Inverter Parameters (Setup) | 0xA4A3 | 42147 | Overfrequencyderatingexitfrequency | U16 | FC03/FC06 | 1 | Hz |  | RW | Specifies the exit frequency of overfrequency derating.
503 | Inverter Parameters (Setup) | 0xA4A4 | 42148 | Overfrequencyderatingpowerrecoverygradient | U16 | FC03/FC06 | 1 | %/min |  | RW | Indicates the speed at which the overfrequency derating power recovers.
504 | Inverter Parameters (Setup) | 0xA4A7 | 42151 | Underfrequency Power Increase | U16 | FC03/FC06 | 1 |  |  | RW | According to the standards in some countries or regions, the power grid frequency is lower than the triggering frequency
505 | Inverter Parameters (Setup) | 0xA4A8 | 42152 | Underfrequency Power Increase Recovery Gradient | U16 | FC03/FC06 | 1 | %/min |  | RW | Indicates the speed for recovering the underfrequency power increase.
506 | Inverter Parameters (Setup) | 0xA4AB | 42155 | LVRT characteristiccurve | string | FC03/FC06 | 21 |  |  | RW | Set the low-voltage ride- through capability of the equipment. For details, see the Key Information Description Table. T
507 | Inverter Parameters (Setup) | 0xA4C0 | 42176 | Cutofffrequencyofunderfrequencypowerincrease | U16 | FC03/FC06 | 1 | Hz |  | RW | Indicates the cutoff frequency for underfrequency power increase.
508 | Inverter Parameters (Setup) | 0xA4C1 | 42177 | Cut- offpowerforunderfrequencypowerincrease | U16 | FC03/FC06 | 1 | % |  | RW | Indicates the cutoff power point for underfrequency power increase.
509 | Inverter Parameters (Setup) | 0xA4C2 | 42178 | Underfrequency Power Increase Triggering Frequency | U16 | FC03/FC06 | 1 | Hz |  | RW | Set the triggering frequency for underfrequency power increase.
510 | Inverter Parameters (Setup) | 0xA4C3 | 42179 | Underfrequency Power Increase Exit Frequency | U16 | FC03/FC06 | 1 | Hz |  | RW | Specifies the exit frequency for underfrequency power increase.
511 | Inverter Parameters (Setup) | 0xA4C4 | 42180 | Built -in PID mode | U16 | FC03/FC06 | 1 |  |  | RW
512 | Inverter Parameters (Setup) | 0xA4C5 | 42181 | PID outputvoltage | S16 | FC03/FC06 | 1 | V |  | RW | Fixed output. This interface is reserved. The GUI is closed.
513 | Inverter Parameters (Setup) | 0xA4C6 | 42182 | PID | U16 | FC03/FC06 | 1 |  |  | RW | Currently reserved only for equipment
514 | Inverter Parameters (Setup) | 0xA4C7 | 42183 | Nightoff- gridrepair | U16 | FC03/FC06 | 1 |  |  | RW
515 | Inverter Parameters (Setup) | 0xA4D0 | 42192 | Activepowerchangegradient | U32 | FC03/FC06 | 2 | %/s |  | RW | Dedicated broadcast interface for the SmartLogger, which does not support incremental reporting and is used in the remot
516 | Inverter Parameters (Setup) | 0xA4D8 | 42200 | Q-U curve | string | FC03/FC06 | 21 |  |  | RW
517 | Inverter Parameters (Setup) | 0xA4ED | 42221 | P-U curve | string | FC03/FC06 | 21 |  |  | RW
518 | Inverter Parameters (Setup) | 0xA502 | 42242 | P-U curveadjustmenttime | U16 | FC03/FC06 | 1 | s |  | RW
519 | Inverter Parameters (Setup) | 0xA52F | 42287 | Undervoltageprotectionthresholdfor 10 minutes | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
520 | Inverter Parameters (Setup) | 0xA530 | 42288 | Ten- minuteundervoltageprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
521 | Inverter Parameters (Setup) | 0xA532 | 42290 | Ten- minuteovervoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
522 | Inverter Parameters (Setup) | 0xA533 | 42291 | Ten- minuteovervoltageprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
523 | Inverter Parameters (Setup) | 0xA535 | 42293 | Level-1 overvoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
524 | Inverter Parameters (Setup) | 0xA536 | 42294 | Level-1 overvoltageprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
525 | Inverter Parameters (Setup) | 0xA538 | 42296 | Level-2 overvoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
526 | Inverter Parameters (Setup) | 0xA539 | 42297 | Level 2 Overvoltage Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
527 | Inverter Parameters (Setup) | 0xA53B | 42299 | Level-3 overvoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
528 | Inverter Parameters (Setup) | 0xA53C | 42300 | Level-3 overvoltageprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
529 | Inverter Parameters (Setup) | 0xA53E | 42302 | Level-4 overvoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
530 | Inverter Parameters (Setup) | 0xA53F | 42303 | Level-4 overvoltageprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
531 | Inverter Parameters (Setup) | 0xA541 | 42305 | Level-5 overvoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
532 | Inverter Parameters (Setup) | 0xA542 | 42306 | Level-5 overvoltageprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
533 | Inverter Parameters (Setup) | 0xA544 | 42308 | Level-6 overvoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
534 | Inverter Parameters (Setup) | 0xA545 | 42309 | Level-6 overvoltageprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
535 | Inverter Parameters (Setup) | 0xA547 | 42311 | Level-1 undervoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
536 | Inverter Parameters (Setup) | 0xA548 | 42312 | Level-1 Undervoltage Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
537 | Inverter Parameters (Setup) | 0xA54A | 42314 | Level-2 undervoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
538 | Inverter Parameters (Setup) | 0xA54B | 42315 | Level 2 Undervoltage Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
539 | Inverter Parameters (Setup) | 0xA54D | 42317 | Level-3 undervoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
540 | Inverter Parameters (Setup) | 0xA54E | 42318 | Level-3 Undervoltage Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
541 | Inverter Parameters (Setup) | 0xA550 | 42320 | Level-4 undervoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
542 | Inverter Parameters (Setup) | 0xA551 | 42321 | Level-4 Undervoltage Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
543 | Inverter Parameters (Setup) | 0xA553 | 42323 | Level-5 undervoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
544 | Inverter Parameters (Setup) | 0xA554 | 42324 | Level-5 Undervoltage Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
545 | Inverter Parameters (Setup) | 0xA556 | 42326 | Level-6 undervoltageprotectionthreshold | U16 | FC03/FC06 | 1 | V |  | RW | Vn: indicates the voltage level, which is related to the power grid code.
546 | Inverter Parameters (Setup) | 0xA557 | 42327 | Level-6 Undervoltage Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
547 | Inverter Parameters (Setup) | 0xA559 | 42329 | Level-1 overfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
548 | Inverter Parameters (Setup) | 0xA55A | 42330 | Level-1 Overfrequency Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
549 | Inverter Parameters (Setup) | 0xA55C | 42332 | Level-2 overfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
550 | Inverter Parameters (Setup) | 0xA55D | 42333 | Level-2 overfrequencyprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
551 | Inverter Parameters (Setup) | 0xA55F | 42335 | Level-3 overfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
552 | Inverter Parameters (Setup) | 0xA560 | 42336 | Level-3 overfrequencyprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
553 | Inverter Parameters (Setup) | 0xA562 | 42338 | Level-4 overfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
554 | Inverter Parameters (Setup) | 0xA563 | 42339 | Level-4 overfrequencyprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
555 | Inverter Parameters (Setup) | 0xA565 | 42341 | Level-5 overfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
556 | Inverter Parameters (Setup) | 0xA566 | 42342 | Level-5 overfrequencyprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
557 | Inverter Parameters (Setup) | 0xA568 | 42344 | Level-6 overfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
558 | Inverter Parameters (Setup) | 0xA569 | 42345 | Six- leveloverfrequencyprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
559 | Inverter Parameters (Setup) | 0xA56B | 42347 | Level-1 underfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
560 | Inverter Parameters (Setup) | 0xA56C | 42348 | Level-1 Underfrequency Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
561 | Inverter Parameters (Setup) | 0xA56E | 42350 | Level-2 underfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
562 | Inverter Parameters (Setup) | 0xA56F | 42351 | Level-2 underfrequencyprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
563 | Inverter Parameters (Setup) | 0xA571 | 42353 | Level-3 underfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
564 | Inverter Parameters (Setup) | 0xA572 | 42354 | Level-3 underfrequencyprotectiontime | U32 | FC03/FC06 | 2 | ms |  | RW
565 | Inverter Parameters (Setup) | 0xA574 | 42356 | Level-4 underfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
566 | Inverter Parameters (Setup) | 0xA575 | 42357 | Level-4 Underfrequency Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
567 | Inverter Parameters (Setup) | 0xA577 | 42359 | Level-5 underfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
568 | Inverter Parameters (Setup) | 0xA578 | 42360 | Level-5 Underfrequency Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
569 | Inverter Parameters (Setup) | 0xA57A | 42362 | Level-6 underfrequencyprotectionthreshold | U16 | FC03/FC06 | 1 | Hz |  | RW | Fn: indicates the frequency level, which is related to the power grid code.
570 | Inverter Parameters (Setup) | 0xA57B | 42363 | Level-6 Underfrequency Protection Time | U32 | FC03/FC06 | 2 | ms |  | RW
571 | Inverter Parameters (Setup) | 0xA5A0 | 42400 | Emergencystopswitch DI | U16 | FC03/FC06 | 1 |  |  | RW
572 | Inverter Parameters (Setup) | 0xA5A3 | 42403 | Outputimpedanceenhancement | U16 | FC03/FC06 | 1 |  |  | RW | After the output impedance enhancement function is enabled, you can set the output impedance enhancement frequency to in
573 | Inverter Parameters (Setup) | 0xA5A4 | 42404 | Outputimpedanceenhancementfrequencypoint | U16 | FC03/FC06 | 1 | Hz |  | RW | The default values are 1025.0 Hz for Switzerland, 175.0 Hz for France, and 210.0 Hz for Germany.
574 | Inverter Parameters (Setup) | 0xA5A7 | 42407 | Microgridadaptability | U16 | FC03/FC06 | 1 |  |  | RW | The microgrid adaptability interface is added to the inverter (including the PCS current source grid-tied). When the mic
575 | Inverter Parameters (Setup) | 0xA5A9 | 42409 | Operatingmode | U16 | FC03/FC06 | 1 |  |  | RW | The default value is PQ. You need to set the working mode during site deployment. Set the working mode to VSG in the chu
576 | Inverter Parameters (Setup) | 0xA5BD | 42429 | Underfrequency Power Increase Effective Delay Time | U16 | FC03/FC06 | 1 | ms |  | RW | Setting the Underfrequency Power Increase Effective Delay Time
577 | Inverter Parameters (Setup) | 0xA5C0 | 42432 | String-to- groundshortcircuitprotectionautomaticrecovery | U16 | FC03/FC06 | 1 |  |  | RW | Enabled: The string short circuit to ground alarm is automatically cleared when the alarm conditions are not met. Disabl
578 | Inverter Parameters (Setup) | 0xA65E | 42590 | Delayedupgrade | U16 | FC03/FC06 | 1 |  |  | RW
579 | Inverter Parameters (Setup) | 0xA662 | 42594 | Intelligentstringmonitoring | U16 | FC03/FC06 | 1 |  |  | RW
580 | Inverter Parameters (Setup) | 0xA663 | 42595 | Stringdetectionreferenceasymmetrycoefficient | U16 | FC03/FC06 | 1 |  |  | RW
581 | Inverter Parameters (Setup) | 0xA664 | 42596 | Stringdetectionstartpowerpercentage | U16 | FC03/FC06 | 1 | % |  | RW
582 | Inverter Parameters (Setup) | 0xA665 | 42597 | Communication Interruption Time | S16 | FC03/FC06 | 1 | min |  | RW
583 | Inverter Parameters (Setup) | 0xA666 | 42598 | Communications | U16 | FC03/FC06 | 1 |  |  | RW
584 | Inverter Parameters (Setup) | 0xA667 | 42599 | [RS4 85-2 ] Communication | U16 | FC03/FC06 | 1 |  |  | RW
585 | Inverter Parameters (Setup) | 0xA6EA | 42730 | PMI | U16 | FC06 | 1 |  |  | WO | Broadcast command interface Note: The instruction range extension design is made here. The higher eight bits are used to
586 | Inverter Parameters (Setup) | 0xA71B | 42779 | IV Curve Scanning | U16 | FC06 | 1 |  |  | WO | Broadcast command interface
587 | Inverter Parameters (Setup) | 0xA794 | 42900 | Daylight Saving Time | U16 | FC03/FC06 | 1 |  |  | RW
588 | Inverter Parameters (Setup) | 0xA795 | 42901 | [DST ] Offsettime | S16 | FC03/FC06 | 1 | min |  | RW
589 | Inverter Parameters (Setup) | 0xA796 | 42902 | [DST ] Start Month | U16 | FC03/FC06 | 1 |  |  | RW
590 | Inverter Parameters (Setup) | 0xA797 | 42903 | [DST ] Startdate | U16 | FC03/FC06 | 1 |  |  | RW | The number of the day in a week is expressed by the number of weeks. The value 1 indicates Monday and the value 7 indica
591 | Inverter Parameters (Setup) | 0xA798 | 42904 | [DST ] Starttime | U16 | FC03/FC06 | 1 |  |  | RW
592 | Inverter Parameters (Setup) | 0xA799 | 42905 | [DST ] Startminute | U16 | FC03/FC06 | 1 |  |  | RW
593 | Inverter Parameters (Setup) | 0xA79A | 42906 | [DST ] Startsecond | U16 | FC03/FC06 | 1 |  |  | RW
594 | Inverter Parameters (Setup) | 0xA79B | 42907 | [DST ] Endmonth | U16 | FC03/FC06 | 1 |  |  | RW
595 | Inverter Parameters (Setup) | 0xA79C | 42908 | [DST ] Enddate | U16 | FC03/FC06 | 1 |  |  | RW | The number of the day in a week is expressed by the number of weeks. The value 1 indicates Monday and the value 7 indica
596 | Inverter Parameters (Setup) | 0xA79D | 42909 | [Daylight Saving Time ] Ends | U16 | FC03/FC06 | 1 |  |  | RW
597 | Inverter Parameters (Setup) | 0xA79E | 42910 | [DST ] Endminute | U16 | FC03/FC06 | 1 |  |  | RW
598 | Inverter Parameters (Setup) | 0xA79F | 42911 | [DST ] Endsecond | U16 | FC03/FC06 | 1 |  |  | RW
599 | Inverter Parameters (Setup) | 0xA7F8 | 43000 | [System Time ] Year | U16 | FC06 | 1 |  |  | WO
600 | Inverter Parameters (Setup) | 0xA7F9 | 43001 | [System Time ] Month | U16 | FC06 | 1 |  |  | WO
601 | Inverter Parameters (Setup) | 0xA7FA | 43002 | [Systemtime ] day | U16 | FC06 | 1 |  |  | WO
602 | Inverter Parameters (Setup) | 0xA7FB | 43003 | [Systemtime ] hour | U16 | FC06 | 1 |  |  | WO
603 | Inverter Parameters (Setup) | 0xA7FC | 43004 | [System Time ] Min. | U16 | FC06 | 1 |  |  | WO
604 | Inverter Parameters (Setup) | 0xA7FD | 43005 | [System Time ] Second | U16 | FC06 | 1 |  |  | WO
605 | Inverter Parameters (Setup) | 0xA7FE | 43006 | Timezone | S16 | FC03/FC06 | 1 | min |  | RW
606 | Inverter Parameters (Setup) | 0xA7FF | 43007 | Clocksource | U16 | FC03/FC06 | 1 |  |  | RW
607 | Inverter Parameters (Setup) | 0xA800 | 43008 | Citycode | U32 | FC03/FC06 | 2 |  |  | RW | (UTC+08:00) Beijing
608 | Inverter Parameters (Setup) | 0xA806 | 43014 | Inverter Installation Position Longitude | S32 | FC03/FC06 | 2 | ° |  | RW | Set this parameter only on the app. The NMS can read the data.
609 | Inverter Parameters (Setup) | 0xA808 | 43016 | Inverter Installation Position Latitude | S32 | FC03/FC06 | 2 | ° |  | RW | Set this parameter only on the app. The NMS can read the data.
610 | Inverter Parameters (Setup) | 0xA80A | 43018 | [RS4 85-1 ] Protocol Type | U16 | FC03/FC06 | 1 |  |  | RW
611 | Inverter Parameters (Setup) | 0xA80B | 43019 | [RS4 85-1 ] Communicationaddress | U16 | FC03/FC06 | 1 |  |  | RW | 0: broadcast address; 1–247: device address; 248–255: reserved
612 | Inverter Parameters (Setup) | 0xA80C | 43020 | [RS4 85-1 ] Baud Rate | U16 | FC03/FC06 | 1 |  |  | RW | 115200 baud rate, corresponding to bit 26 of feature code 3.
613 | Inverter Parameters (Setup) | 0xA80D | 43021 | [RS4 85-1 ] Verificationmode | U16 | FC03/FC06 | 1 |  |  | RW
614 | Inverter Parameters (Setup) | 0xA80E | 43022 | [RS4 85-1 ] Portmode | U16 | FC03/FC06 | 1 |  |  | RW
615 | Inverter Parameters (Setup) | 0xA80F | 43023 | [RS4 85-1 ] Modbus Protocol Model Version | U16 | FC03/FC06 | 1 |  |  | RW | This parameter is used only when the northbound port is used in the old model replacement scenario.
616 | Inverter Parameters (Setup) | 0xA819 | 43033 | [RS4 85-2 ] Protocol Type | U16 | FC03/FC06 | 1 |  |  | RW
617 | Inverter Parameters (Setup) | 0xA81A | 43034 | [RS4 85-2 ] Communicationaddress | U16 | FC03/FC06 | 1 |  |  | RW | 0: broadcast address 1–247: device address 248–255: reserved
618 | Inverter Parameters (Setup) | 0xA81B | 43035 | [RS4 85-2 ] Baud Rate | U16 | FC03/FC06 | 1 |  |  | RW | 115200 baud rate, corresponding to bit 27 of feature code 3.
619 | Inverter Parameters (Setup) | 0xA81C | 43036 | [RS4 85-2 ] Verification Mode | U16 | FC03/FC06 | 1 |  |  | RW
620 | Inverter Parameters (Setup) | 0xA81D | 43037 | [RS4 85-2 ] Portmode | U16 | FC03/FC06 | 1 |  |  | RW
621 | Inverter Parameters (Setup) | 0xA827 | 43047 | Protocol Type | U16 | FC03/FC06 | 1 |  |  | RW
622 | Inverter Parameters (Setup) | 0xA828 | 43048 | Box- typetransformernumber | U16 | FC03/FC06 | 1 |  |  | RW | Only the 06 function code is supported. Local application
623 | Inverter Parameters (Setup) | 0xA829 | 43049 | Winding No. | U16 | FC03/FC06 | 1 |  |  | RW | Only the 06 function code is supported. Local application
624 | Inverter Parameters (Setup) | 0xA82A | 43050 | Mac Offset | U16 | FC03/FC06 | 1 |  |  | RW | Only the 06 function code is supported. Local application
625 | Inverter Parameters (Setup) | 0xA82C | 43052 | Powersettings | U16 | FC03/FC06 | 1 | dB |  | RW | Note: This parameter x 2 corresponds to the dB value.
626 | Inverter Parameters (Setup) | 0xA837 | 43063 | [Management System] TCP Frame Length | U16 | FC03/FC06 | 1 |  |  | RW | [320, 1500]
627 | Inverter Parameters (Setup) | 0xA838 | 43064 | [Management System] Application- Layer Heartbeat Interval | U16 | FC03/FC06 | 1 | min |  | RW | Default value: 30 minutes
628 | Inverter Parameters (Setup) | 0xA839 | 43065 | [Management System] TCP Heartbeat Interval | U16 | FC03/FC06 | 1 | s |  | RW | 0XFFFF indicates that there is no heartbeat. If this parameter is set to 0, the default heartbeat period is 3 minutes.
629 | Inverter Parameters (Setup) | 0xA83A | 43066 | [Management System] Protocol Type | U16 | FC03/FC06 | 1 |  |  | RW
630 | Inverter Parameters (Setup) | 0xA83B | 43067 | [Management System] Server | string | FC03/FC06 | 30 |  |  | RW | Domain name address or IP address
631 | Inverter Parameters (Setup) | 0xA859 | 43097 | [Managementsystem] Port 1 | U16 | FC03/FC06 | 1 |  |  | RW
632 | Inverter Parameters (Setup) | 0xA85A | 43098 | [Management System] TLS Encryption | U16 | FC03/FC06 | 1 |  |  | RW
633 | Inverter Parameters (Setup) | 0xA85C | 43100 | [Management System] Portmode | U16 | FC03/FC06 | 1 |  |  | RW
634 | Inverter Parameters (Setup) | 0xA85E | 43102 | [FE] Keypassword | string | FC06 | 32 |  |  | WO | Interface for delivering the key password when the app certifciate is replaced
635 | Inverter Parameters (Setup) | 0xA88B | 43147 | [STA ] Accessinga Wireless Router | U16 | FC03/FC06 | 1 |  |  | RW
636 | Inverter Parameters (Setup) | 0xA88C | 43148 | [STA ] Wireless Routing Network Name | string | FC03/FC06 | 16 |  |  | RW
637 | Inverter Parameters (Setup) | 0xA89C | 43164 | [STA ] Wireless Routing Encryption Mode | U16 | FC03/FC06 | 1 |  |  | RW
638 | Inverter Parameters (Setup) | 0xA89D | 43165 | [STA ] Wireless Router Login Password | string | FC03/FC06 | 32 |  |  | RW | This parameter is not displayed in non-encryption mode.
639 | Inverter Parameters (Setup) | 0xA8BD | 43197 | [FE] DHC P | U16 | FC03/FC06 | 1 |  |  | RW
640 | Inverter Parameters (Setup) | 0xA8BE | 43198 | [FE] IP address | IPv4 | FC03/FC06 | 2 |  |  | RW | If the IP address, subnet mask, and gateway address are modified, the other two parameters must be delivered in the same
641 | Inverter Parameters (Setup) | 0xA8C0 | 43200 | [FE] Subnet Mask | IPv4 | FC03/FC06 | 2 |  |  | RW
642 | Inverter Parameters (Setup) | 0xA8C2 | 43202 | [FE] Gatewayaddress | IPv4 | FC03/FC06 | 2 |  |  | RW
643 | Inverter Parameters (Setup) | 0xA8C4 | 43204 | [STA ] Preferred DNS Server | U32 | FC03/FC06 | 2 |  |  | RW
644 | Inverter Parameters (Setup) | 0xA8C6 | 43206 | [STA ] Standby DNS server | U32 | FC03/FC06 | 2 |  |  | RW
645 | Inverter Parameters (Setup) | 0xA8C8 | 43208 | [FE] DHC P | U16 | FC03/FC06 | 1 |  |  | RW | Decoupling mode: Feature code 2:18
646 | Inverter Parameters (Setup) | 0xA8C9 | 43209 | [FE] IP address | U32 | FC03/FC06 | 2 |  |  | RW | If the IP address, subnet mask, and gateway address are modified, the other two parameters must be delivered in the same
647 | Inverter Parameters (Setup) | 0xA8CB | 43211 | [FE] Subnet Mask | U32 | FC03/FC06 | 2 |  |  | RW
648 | Inverter Parameters (Setup) | 0xA8CD | 43213 | [FE] Gatewayaddress | U32 | FC03/FC06 | 2 |  |  | RW
649 | Inverter Parameters (Setup) | 0xA8CF | 43215 | [FE] Preferred DNS server | U32 | FC03/FC06 | 2 |  |  | RW | Decoupling mode: Feature code 2:18
650 | Inverter Parameters (Setup) | 0xA8D1 | 43217 | [FE] Secondary DNS server | U32 | FC03/FC06 | 2 |  |  | RW | Decoupling mode: Feature code 2:18
651 | Inverter Parameters (Setup) | 0xA8E4 | 43236 | WLA N O& M Policy | U16 | FC03/FC06 | 1 |  |  | RW | Configures O&M policies for WLAN ports. For the SACU, policies 0, 1, and 2 can be configured. For the APP, policies 0 an
652 | Inverter Parameters (Setup) | 0xA8E5 | 43237 | [AP] SSID broadcast | U16 | FC03/FC06 | 1 |  |  | RW | 0: enabled 1: disabled Default value: 0
653 | Inverter Parameters (Setup) | 0xA8E6 | 43238 | [AP] WLA N name | string | FC03/FC06 | 16 |  |  | RW | Wifi-AP mode
654 | Inverter Parameters (Setup) | 0xA8F6 | 43254 | [AP] WLA N Login Password | string | FC03/FC06 | 32 |  |  | RW | The password must contain at least eight characters.
655 | Inverter Parameters (Setup) | 0xA917 | 43287 | [AP] Gateway IP address | U32 | FC03/FC06 | 2 |  |  | RW
656 | Inverter Parameters (Setup) | 0xA919 | 43289 | [AP] subnetmask | U32 | FC03/FC06 | 2 |  |  | RW
657 | Inverter Parameters (Setup) | 0xA92F | 43311 | [NTP ] NTP timesynchronization | U16 | FC03/FC06 | 1 |  |  | RW
658 | Inverter Parameters (Setup) | 0xA930 | 43312 | [NTP ] NTP serveraddress | string | FC03/FC06 | 30 |  |  | RW
659 | Inverter Parameters (Setup) | 0xA94E | 43342 | [NTP ] NTP serverport | U16 | FC03/FC06 | 1 |  |  | RW
660 | Inverter Parameters (Setup) | 0xA94F | 43343 | [NTP ] NTP Service Time Interval | U16 | FC03/FC06 | 1 | min |  | RW
661 | Inverter Parameters (Setup) | 0xA955 | 43349 | Devicename | string | FC03/FC06 | 10 |  |  | RW | This parameter is left blank by default. It is used by the customer to modify the device name.
662 | Inverter Parameters (Setup) | 0xA95F | 43359 | [App ] Initialpower- onflag | U16 | FC03/FC06 | 1 |  |  | RW | After the SmartLogger is deployed, the power-on flag needs to be cleared.
663 | Inverter Parameters (Setup) | 0xA961 | 43361 | Parallelcommunicationmode | U16 | FC03/FC06 | 1 |  |  | RW | This interface is used to set the communication mode between the host machine and the parallel slave server in the Sdong
664 | Inverter Parameters (Setup) | 0xA96A | 43370 | [4G] 4G module | U16 | FC03/FC06 | 1 |  |  | RW
665 | Inverter Parameters (Setup) | 0xA97A | 43386 | [4G] Card No. | string | FC03/FC06 | 10 |  |  | RW
666 | Inverter Parameters (Setup) | 0xA9A6 | 43430 | [4G] Networkmode | U16 | FC03/FC06 | 1 |  |  | RW
667 | Inverter Parameters (Setup) | 0xA9A7 | 43431 | [4G] APN mode | U16 | FC03/FC06 | 1 |  |  | RW
668 | Inverter Parameters (Setup) | 0xA9A9 | 43433 | [4G] [Default] Identityauthenticationtype | U16 | FC03/FC06 | 1 |  |  | RW
669 | Inverter Parameters (Setup) | 0xA9AA | 43434 | [4G] [Default] APN | string | FC03/FC06 | 16 |  |  | RW
670 | Inverter Parameters (Setup) | 0xA9CA | 43466 | [4G] [Default] APN username | string | FC03/FC06 | 16 |  |  | RW
671 | Inverter Parameters (Setup) | 0xA9DA | 43482 | [4G] [Default] APN userpassword | string | FC03/FC06 | 16 |  |  | RW
672 | Inverter Parameters (Setup) | 0xA9EB | 43499 | [4G] Identityauthenticationtype | U16 | FC03/FC06 | 1 |  |  | RW
673 | Inverter Parameters (Setup) | 0xA9EC | 43500 | [4G] APN | string | FC03/FC06 | 16 |  |  | RW | APN name
674 | Inverter Parameters (Setup) | 0xA9FC | 43516 | [4G] APN dial- upnumber | string | FC03/FC06 | 16 |  |  | RW | Dial Number
675 | Inverter Parameters (Setup) | 0xAA0C | 43532 | [4G] APN User Name | string | FC03/FC06 | 16 |  |  | RW | APN User Name
676 | Inverter Parameters (Setup) | 0xAA1C | 43548 | [4G] APN userpassword | string | FC03/FC06 | 16 |  |  | RW | APN Password
677 | Inverter Parameters (Setup) | 0xAA2C | 43564 | [4G] Trafficpackage | U32 | FC03/FC06 | 2 | MB |  | RW
678 | Inverter Parameters (Setup) | 0xAA2E | 43566 | [4G] Monthlyusedtraffic | U32 | FC03/FC06 | 2 | MB |  | RW | Used for traffic correction.
679 | Inverter Parameters (Setup) | 0xAA30 | 43568 | [4G] PIN | string | FC06 | 4 |  |  | WO
680 | Inverter Parameters (Setup) | 0xAA70 | 43632 | Stringaccessdetection | U16 | FC03/FC06 | 1 |  |  | RW | 0: disabled (default) 1: enabled
681 | Inverter Parameters (Setup) | 0xAA71 | 43633 | Start -upcurrent | U16 | FC03/FC06 | 1 | A |  | RW | [3.0, 10.0] Default value: 5.0
682 | Inverter Parameters (Setup) | 0xAA72 | 43634 | Two- in- onedetectionstartingcurrent | U16 | FC03/FC06 | 1 | A |  | RW | [10.0, 20.0] Default value: 15.0
683 | Inverter Parameters (Setup) | 0xAA73 | 43635 | String 1 accesstype | U16 | FC03/FC06 | 1 |  |  | RW
684 | Inverter Parameters (Setup) | 0xAA74 | 43636 | String 2 Access Type | U16 | FC03/FC06 | 1 |  |  | RW
685 | Inverter Parameters (Setup) | 0xAA75 | 43637 | String 3 Access Type | U16 | FC03/FC06 | 1 |  |  | RW
686 | Inverter Parameters (Setup) | 0xAA76 | 43638 | String 4 Access Type | U16 | FC03/FC06 | 1 |  |  | RW
687 | Inverter Parameters (Setup) | 0xAA77 | 43639 | String 5 Access Type | U16 | FC03/FC06 | 1 |  |  | RW
688 | Inverter Parameters (Setup) | 0xAA78 | 43640 | String 6 Access Type | U16 | FC03/FC06 | 1 |  |  | RW
689 | Inverter Parameters (Setup) | 0xAA79 | 43641 | String 7 Access Type | U16 | FC03/FC06 | 1 |  |  | RW
690 | Inverter Parameters (Setup) | 0xAA7A | 43642 | String 8 Access Type | U16 | FC03/FC06 | 1 |  |  | RW
691 | Inverter Parameters (Setup) | 0xABE0 | 44000 | Support System Type | U16 | FC03/FC06 | 1 |  |  | RW | If the device vendor does not support one of the modes, the system returns the 03 error code.
692 | Inverter Parameters (Setup) | 0xABE1 | 44001 | Operatingmode | U16 | FC03/FC06 | 1 |  |  | RW
693 | Inverter Parameters (Setup) | 0xABE2 | 44002 | Controlperiod | U16 | FC03/FC06 | 1 | min |  | RW
694 | Inverter Parameters (Setup) | 0xABE3 | 44003 | Starttimeofreversetracinginthemorning (hour) | U16 | FC03/FC06 | 1 | hour |  | RW
695 | Inverter Parameters (Setup) | 0xABE4 | 44004 | Starttimeofreversetracinginthemorning (minutes) | U16 | FC03/FC06 | 1 | min |  | RW
696 | Inverter Parameters (Setup) | 0xABE5 | 44005 | Morning Backtracking Duration Minute | U16 | FC03/FC06 | 1 | min |  | RW
697 | Inverter Parameters (Setup) | 0xABE6 | 44006 | Tiltanglecontrol | string | FC03/FC06 | 2 |  |  | RW | HW: ID of the support system, ranging from 0 to 16. The value 0 indicates full control. LW: tilt angle. The gain is 100.
698 | Inverter Parameters (Setup) | 0xABE8 | 44008 | Bearingcontrol | string | FC03/FC06 | 2 |  |  | RW | HW: ID of the support system, ranging from 0 to 16. 0 indicates full control. LW: azimuth preset value, gain 100, range
699 | Inverter Parameters (Setup) | 0xABEA | 44010 | Numberofmotorscontrolledsimultaneously | U16 | FC03/FC06 | 1 |  |  | RW | If the actual number of motors is less than 16, the setting may fail.
700 | Inverter Parameters (Setup) | 0xABEB | 44011 | Starttimeofthereversetracingintheevening (hour) | U16 | FC03/FC06 | 1 | hour |  | RW
701 | Inverter Parameters (Setup) | 0xABEC | 44012 | Starttimeofthereversetracingintheevening (minute) | U16 | FC03/FC06 | 1 | min |  | RW
702 | Inverter Parameters (Setup) | 0xABED | 44013 | Evening Backtracking Duration Minute | U16 | FC03/FC06 | 1 | min |  | RW
703 | Inverter Parameters (Setup) | 0xABEE | 44014 | Sensorinstallationdirection | U16 | FC03/FC06 | 1 |  |  | RW
704 | Inverter Parameters (Setup) | 0xABEF | 44015 | Controllertimesynchronization | U16 | FC03/FC06 | 1 |  |  | RW
705 | Inverter Parameters (Setup) | 0xABF0 | 44016 | Numberofcontrolboxes | U16 | FC03/FC06 | 1 |  |  | RW
706 | Inverter Parameters (Setup) | 0xAC12 | 44050 | Totalnumberofstents | U16 | FC03/FC06 | 1 |  |  | RW | When dual-axis control is used, the maximum number of support systems is 8.
707 | Inverter Parameters (Setup) | 0xAC13 | 44051 | Installation Longitude | S16 | FC03/FC06 | 1 | ° |  | RW | The east longitude is positive and the west longitude is negative.
708 | Inverter Parameters (Setup) | 0xAC14 | 44052 | Installation Dimension | S16 | FC03/FC06 | 1 | ° |  | RW | The north latitude is positive and the south latitude is negative.
709 | Inverter Parameters (Setup) | 0xAC15 | 44053 | Controladdress 1 | U16 | FC03/FC06 | 1 |  |  | RW
710 | Inverter Parameters (Setup) | 0xAC16 | 44054 | Controladdress 2 | U16 | FC03/FC06 | 1 |  |  | RW
711 | Inverter Parameters (Setup) | 0xAC17 | 44055 | Southbound RS48 5 Check Mode | U16 | FC03/FC06 | 1 |  |  | RW
712 | Inverter Parameters (Setup) | 0xAC18 | 44056 | Southbound RS48 5 baudrate | U16 | FC03/FC06 | 1 |  |  | RW
713 | Inverter Parameters (Setup) | 0xAC19 | 44057 | Tiltanglecontrolupperlimit | S16 | FC03/FC06 | 1 | ° |  | RW | Tilt angle control upper limit must be greater than lower limit
714 | Inverter Parameters (Setup) | 0xAC1A | 44058 | Tiltanglecontrollowerlimit | S16 | FC03/FC06 | 1 | ° |  | RW | Tilt angle control upper limit must be greater than lower limit
715 | Inverter Parameters (Setup) | 0xAC1B | 44059 | Upperlimitofazimuthcontrol | S16 | FC03/FC06 | 1 | ° |  | RW | The upper limit of azimuth control must be greater than the lower limit.
716 | Inverter Parameters (Setup) | 0xAC1C | 44060 | Lowerlimitforazimuthcontrol | S16 | FC03/FC06 | 1 | ° |  | RW | The upper limit of azimuth control must be greater than the lower limit.
717 | Inverter Parameters (Setup) | 0xAC1D | 44061 | Sensor 1 address | U16 | FC03/FC06 | 1 |  |  | RW
718 | Inverter Parameters (Setup) | 0xAC1E | 44062 | Sensor 2 Address | U16 | FC03/FC06 | 1 |  |  | RW
719 | Inverter Parameters (Setup) | 0xAC1F | 44063 | Sensor 3 Address | U16 | FC03/FC06 | 1 |  |  | RW
720 | Inverter Parameters (Setup) | 0xAC20 | 44064 | Sensor 4 Address | U16 | FC03/FC06 | 1 |  |  | RW
721 | Inverter Parameters (Setup) | 0xAC21 | 44065 | Sensor 5 Address | U16 | FC03/FC06 | 1 |  |  | RW
722 | Inverter Parameters (Setup) | 0xAC22 | 44066 | Sensor 6 Address | U16 | FC03/FC06 | 1 |  |  | RW
723 | Inverter Parameters (Setup) | 0xAC23 | 44067 | Sensor 7 address | U16 | FC03/FC06 | 1 |  |  | RW
724 | Inverter Parameters (Setup) | 0xAC24 | 44068 | Sensor 8 Address | U16 | FC03/FC06 | 1 |  |  | RW
725 | Inverter Parameters (Setup) | 0xAC25 | 44069 | Sensor 9 Address | U16 | FC03/FC06 | 1 |  |  | RW
726 | Inverter Parameters (Setup) | 0xAC26 | 44070 | Sensor 10 Address | U16 | FC03/FC06 | 1 |  |  | RW
727 | Inverter Parameters (Setup) | 0xAC27 | 44071 | Sensor 11 address | U16 | FC03/FC06 | 1 |  |  | RW
728 | Inverter Parameters (Setup) | 0xAC28 | 44072 | Sensor 12 Address | U16 | FC03/FC06 | 1 |  |  | RW
729 | Inverter Parameters (Setup) | 0xAC29 | 44073 | Sensor 13 address | U16 | FC03/FC06 | 1 |  |  | RW
730 | Inverter Parameters (Setup) | 0xAC2A | 44074 | Sensor 14 Address | U16 | FC03/FC06 | 1 |  |  | RW
731 | Inverter Parameters (Setup) | 0xAC2B | 44075 | Sensor 15 Address | U16 | FC03/FC06 | 1 |  |  | RW
732 | Inverter Parameters (Setup) | 0xAC2C | 44076 | Sensor 16 Address | U16 | FC03/FC06 | 1 |  |  | RW
733 | Inverter Parameters (Setup) | 0xAC2D | 44077 | Trackingsystemcontroller | U16 | FC03/FC06 | 1 |  |  | RW
734 | Inverter Parameters (Setup) | 0xAC2F | 44079 | Controladdress 3 | U16 | FC03/FC06 | 1 |  |  | RW
735 | Inverter Parameters (Setup) | 0xAC30 | 44080 | Controladdress 4 | U16 | FC03/FC06 | 1 |  |  | RW
736 | Inverter Parameters (Setup) | 0xAC31 | 44081 | Southbound RS48 5 stopbit | U16 | FC03/FC06 | 1 |  |  | RW
737 | Inverter Parameters (Setup) | 0xAC32 | 44082 | Support Fault Clearance | U16 | FC06 | 1 |  |  | WO | 0: Clear all support faults. 1-16: Clear the fault of the specified support.
738 | Inverter Parameters (Setup) | 0xAC33 | 44083 | GPS time (localtime ): year | U16 | FC03/FC06 | 1 |  |  | RW
739 | Inverter Parameters (Setup) | 0xAC39 | 44089 | windspeed | U16 | FC03/FC06 | 1 | m/s |  | RW
740 | Inverter Parameters (Setup) | 0xAC3A | 44090 | Timezone | S16 | FC03/FC06 | 1 | min |  | RW
741 | Inverter Parameters (Setup) | 0xAC3B | 44091 | Controladdress 5 | U16 | FC03/FC06 | 1 |  |  | RW
742 | Inverter Parameters (Setup) | 0xAC3C | 44092 | Controladdress 6 | U16 | FC03/FC06 | 1 |  |  | RW
743 | Inverter Parameters (Setup) | 0xAC3D | 44093 | Controladdress 7 | U16 | FC03/FC06 | 1 |  |  | RW
744 | Inverter Parameters (Setup) | 0xAC3E | 44094 | Controladdress 8 | U16 | FC03/FC06 | 1 |  |  | RW
745 | Inverter Parameters (Setup) | 0xAC3F | 44095 | Controladdress 9 | U16 | FC03/FC06 | 1 |  |  | RW
746 | Inverter Parameters (Setup) | 0xAC40 | 44096 | Controladdress 10 | U16 | FC03/FC06 | 1 |  |  | RW
747 | Inverter Parameters (Setup) | 0xAC41 | 44097 | Controladdress 11 | U16 | FC03/FC06 | 1 |  |  | RW
748 | Inverter Parameters (Setup) | 0xAC42 | 44098 | Controladdress 12 | U16 | FC03/FC06 | 1 |  |  | RW
749 | Inverter Parameters (Setup) | 0xAC43 | 44099 | Controladdress 13 | U16 | FC03/FC06 | 1 |  |  | RW
750 | Inverter Parameters (Setup) | 0xAC44 | 44100 | Controladdress 14 | U16 | FC03/FC06 | 1 |  |  | RW
751 | Inverter Parameters (Setup) | 0xAC45 | 44101 | Controladdress 15 | U16 | FC03/FC06 | 1 |  |  | RW
752 | Inverter Parameters (Setup) | 0xAC46 | 44102 | Controladdress 16 | U16 | FC03/FC06 | 1 |  |  | RW
753 | Inverter Parameters (Setup) | 0xAC47 | 44103 | Scienceand Technology Jingke Protocol Version | U16 | FC03/FC06 | 1 |  |  | RW
754 | Inverter Parameters (Setup) | 0xAC48 | 44104 | Sensor Range | U16 | FC03/FC06 | 1 | ° |  | RW
755 | Inverter Parameters (Setup) | 0xAC49 | 44105 | Controlprecision | U16 | FC03/FC06 | 1 | ° |  | RW
756 | Inverter Parameters (Setup) | 0xACA8 | 44200 | KP | S16 | FC03/FC06 | 1 |  |  | RW | Debugging interface
757 | Inverter Parameters (Setup) | 0xACA9 | 44201 | KI | S16 | FC03/FC06 | 1 |  |  | RW | Debugging interface
758 | Inverter Parameters (Setup) | 0xACAA | 44202 | KD | S16 | FC03/FC06 | 1 |  |  | RW | Debugging interface
759 | Inverter Parameters (Setup) | 0xAD0C | 44300 | windspeed | U16 | FC06 | 1 | m/s |  | WO
760 | Inverter Parameters (Setup) | 0xAD0D | 44301 | Winddirection | U16 | FC06 | 1 | ° |  | WO
761 | Inverter Parameters (Setup) | 0xAD0E | 44302 | Startupcontrol | U16 | FC06 | 2 |  |  | WO | BIT0–BIT15: Start command of bracket 1–bracket system 16; BIT16–BIT31: reserved for future expansion.
762 | Inverter Parameters (Setup) | 0xAD10 | 44304 | Support Fault Clearance | U16 | FC06 | 2 |  |  | WO | BIT0–BIT15: Clear the faults of support 1–16 in sequence. Bits 16–32: reserved for future expansion.
763 | Inverter Parameters (Setup) | 0xAD12 | 44306 | Stopcontrol | U16 | FC06 | 2 |  |  | WO | BIT0~BIT15: stop command of rack 1~rack system 16; BIT16–BIT31: reserved for future expansion.
764 | Inverter Parameters (Setup) | 0xAD78 | 44408 | Temperature 1 | S16 | FC06 | 1 | °C |  | WO
765 | Inverter Parameters (Setup) | 0xAD7A | 44410 | Humidity 1 | U16 | FC06 | 1 | %RH |  | WO
766 | Inverter Parameters (Setup) | 0xAFC8 | 45000 | Restorefactorysettings. | U16 | FC06 | 1 |  |  | WO
767 | Inverter Parameters (Setup) | 0xAFC9 | 45001 | Clearingactivealarms | string | FC06 | 2 |  |  | WO
768 | Inverter Parameters (Setup) | 0xAFCB | 45003 | Alarmsetting | string | FC06 | 2 |  |  | WO
769 | Inverter Parameters (Setup) | 0xAFCD | 45005 | Alarmclearance | U16 | FC06 | 1 |  |  | WO
770 | Inverter Parameters (Setup) | 0xAFCE | 45006 | Alarmmasking | U16 | FC06 | 1 |  |  | WO
771 | Inverter Parameters (Setup) | 0xAFCF | 45007 | AFCI self- checkstart | U16 | FC06 | 1 |  |  | WO | Set the field to 0. Associate the AFCI controller in the in-position ID of the subdevice.
772 | Inverter Parameters (Setup) | 0xAFD0 | 45008 | Accumulatedenergyyieldcorrection | U32 | FC06 | 2 | kWh |  | WO
773 | Inverter Parameters (Setup) | 0xAFD2 | 45010 | Clearhistoricalbatterylevel. | U16 | FC06 | 1 |  |  | WO | Including the accumulated power generation capacity and accumulated charging capacity on the power side
774 | Inverter Parameters (Setup) | 0xAFD3 | 45011 | Cleartherunningtimeinformation. | U16 | FC06 | 1 |  |  | WO | Clears the accumulated running time, fault duration, and grid-tied running time.
775 | Inverter Parameters (Setup) | 0xAFD4 | 45012 | Spot Check | U16 | FC06 | 1 |  |  | WO
776 | Inverter Parameters (Setup) | 0xAFD6 | 45014 | Cleartheflashmemory. | U16 | FC06 | 1 |  |  | WO
777 | Inverter Parameters (Setup) | 0xAFD7 | 45015 | ESN validationcommand | U16 | FC06 | 1 |  |  | WO
778 | Inverter Parameters (Setup) | 0xAFD8 | 45016 | Restorethedefaultpassword . | string | FC06 | 10 |  |  | WO | Enter the equipment ESN in the Data field.
779 | Inverter Parameters (Setup) | 0xAFE2 | 45026 | [STA ] Startscanningtheavailable WLA N list. | U16 | FC06 | 1 |  |  | WO | 0
780 | Inverter Parameters (Setup) | 0xAFE3 | 45027 | [License Interface] License Deregistration | string | FC06 | 10 |  |  | WO | Fill the LSN in the data field.
781 | Inverter Parameters (Setup) | 0xAFED | 45037 | Alarmportself- checkstart | U16 | FC06 | 1 |  |  | WO | The data field is set to 0.
782 | Inverter Parameters (Setup) | 0xAFF0 | 45040 | Audibleandvisualalarmconfirmation | U16 | FC06 | 1 |  |  | WO | This parameter is added to disable the audible and visual alarm function. After the alarm condition is cleared, the audi
783 | Inverter Parameters (Setup) | 0xB799 | 47001 | Box- typetransformernumber | U16 | FC03/FC06 | 1 |  |  | RW | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
784 | Inverter Parameters (Setup) | 0xB79A | 47002 | Winding No. | U16 | FC03/FC06 | 1 |  |  | RW | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
785 | Inverter Parameters (Setup) | 0xB79B | 47003 | Mac Ofsfet | U16 | FC03/FC06 | 1 |  |  | RW | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
786 | Inverter Parameters (Setup) | 0xB79C | 47004 | Operatingmode | U16 | FC03/FC06 | 1 |  |  | RW
787 | Inverter Parameters (Setup) | 0xB7E7 | 47079 | Powerlimitforgrid- tiedsites | S32 | FC03/FC06 | 2 | W |  | RW
788 | Inverter Parameters (Setup) | 0xB810 | 47120 | Optimizer | U16 | FC03/FC06 | 1 |  |  | RW | Used to add the safety box. After the safety box is added, the DC-PLC status is set. Shenyanbai: This flag is forcibly s
789 | Inverter Parameters (Setup) | 0xB816 | 47126 | Single Optimizer Data Query | U16 | FC03/FC06 | 1 |  |  | RW | Optimizer Logical Address
790 | Inverter Parameters (Setup) | 0xB819 | 47129 | Alias Settings | string | FC06 | 11 |  |  | WO | W0: optimizer address; (small end) W1–10: alias character string
791 | Inverter Parameters (Setup) | 0xB824 | 47140 | Physicallocation | U16 | FC06 | 1 |  |  | WO | Anti-crosstalk is disabled.
792 | Inverter Parameters (Setup) | 0xB825 | 47141 | Importing Logs | U16 | FC06 | 1 |  |  | WO
793 | Inverter Parameters (Setup) | 0xB827 | 47143 | Brokenlinedetection | U16 | FC06 | 1 |  |  | WO
794 | Inverter Parameters (Setup) | 0xB828 | 47144 | Exportcompletelogs. | U16 | FC06 | 1 |  |  | WO
795 | Inverter Parameters (Setup) | 0xB829 | 47145 | Settingthe Accumulated Energy Yield | MULTIDATA | FC06 | 3 | 1 |  | WO | Gain: 1000 Unit: kWh
796 | Inverter Parameters (Setup) | 0xB82E | 47150 | Baud Rate | U16 | FC03/FC06 | 1 |  |  | RW | The MBUS register is 43113.
797 | Inverter Parameters (Setup) | 0xB82F | 47151 | Anti- crosstalk | U16 | FC03/FC06 | 1 |  |  | RW | The MBUS register is 47022.
798 | Inverter Parameters (Setup) | 0xB830 | 47152 | Networkfrequencyband | U16 | FC03/FC06 | 1 |  |  | RW | The MBUS register is 43116.
799 | Inverter Parameters (Setup) | 0xB831 | 47153 | Networking | U16 | FC03/FC06 | 1 |  |  | RW | The MBUS register is 47010.
800 | Inverter Parameters (Setup) | 0xB832 | 47154 | Packetlossratetest | U16 | FC03/FC06 | 1 |  |  | RW
801 | Inverter Parameters (Setup) | 0xB834 | 47156 | Securitymode | U16 | FC03/FC06 | 1 |  |  | RW | When the PLC enters and exits the unlock mode, the CCO is reset.
802 | Inverter Parameters (Setup) | 0xB835 | 47157 | Fastpower- downenable | U16 | FC03/FC06 | 1 |  |  | RW
803 | Inverter Parameters (Setup) | 0xB836 | 47158 | Fast Shutdown Self- Test | U16 | FC06 | 1 |  |  | WO
804 | Inverter Parameters (Setup) | 0xB8C4 | 47300 | Forwardpower | U16 | FC03/FC06 | 1 |  |  | RW
805 | Inverter Parameters (Setup) | 0xB8C5 | 47301 | Cableconnectionposition | U16 | FC03/FC06 | 1 |  |  | RW
806 | Inverter Parameters (Setup) | 0xB8C6 | 47302 | CT ratedcurrent | U16 | FC03/FC06 | 1 | A |  | RW
807 | Inverter Parameters (Setup) | 0xB8C7 | 47303 | Metermodel | U16 | FC03/FC06 | 1 |  |  | RW | Note: 47002 conflicts with the winding number of the [Remote Setting]. The winding number is reassigned. This interface
808 | Inverter Parameters (Setup) | 0xB8C8 | 47304 | Meteraddress | U16 | FC03/FC06 | 1 |  |  | RW | Note: 47003 conflicts with [Remote Settings] MAC Offset. This interface will be used in later versions.
809 | Inverter Parameters (Setup) | 0xB8C9 | 47305 | Metername | string | FC03/FC06 | 15 |  |  | RW | Used to store the name of the meter during model loading.
810 | Inverter Parameters (Setup) | 0xB928 | 47400 | Enableautomaticaddressallocation. | U16 | FC03/FC06 | 1 |  |  | RW
811 | Inverter Parameters (Setup) | 0xB929 | 47401 | Startaddressforautomaticaddressassignment | U16 | FC03/FC06 | 1 |  |  | RW
812 | Inverter Parameters (Setup) | 0xB936 | 47414 | Communicationmoduleaddress | U16 | FC03/FC06 | 1 |  |  | RW
813 | Inverter Parameters (Setup) | 0xB937 | 47415 | Activepowercontrolmode | U16 | FC03/FC06 | 1 |  |  | RW
814 | Inverter Parameters (Setup) | 0xB938 | 47416 | Maximumpowerfedtothegrid (kW) | S32 | FC03/FC06 | 2 | kW |  | RW
815 | Inverter Parameters (Setup) | 0xB93A | 47418 | Maximum Feed Grid Power (%) | S16 | FC03/FC06 | 1 | % |  | RW
816 | Inverter Parameters (Setup) | 0xB93B | 47419 | Restrictionmode | U16 | FC03/FC06 | 1 |  |  | RW
817 | Inverter Parameters (Setup) | 0xB93C | 47420 | Powerdecreaseadjustmentperiod | U16 | FC03/FC06 | 1 | s |  | RW
818 | Inverter Parameters (Setup) | 0xB93D | 47421 | Maximumprotectiontime | U16 | FC03/FC06 | 1 | s |  | RW
819 | Inverter Parameters (Setup) | 0xB93E | 47422 | Power Increase Threshold | U32 | FC03/FC06 | 2 | kW |  | RW
820 | Inverter Parameters (Setup) | 0xB940 | 47424 | Activepowerlimitforfailprotection [%] [lowprecision] | S16 | FC03/FC06 | 1 | % |  | RW | Not displayed on the GUI. The gains of the old interface are different. This function is used only to support the batch
821 | Inverter Parameters (Setup) | 0xB941 | 47425 | reactivepowercontrolmode | U16 | FC03/FC06 | 1 |  |  | RW
822 | Inverter Parameters (Setup) | 0xB942 | 47426 | Reactivefixedvalue | S32 | FC03/FC06 | 2 | kVar |  | RW
823 | Inverter Parameters (Setup) | 0xB944 | 47428 | targetpowerfactor | S16 | FC03/FC06 | 1 |  |  | RW
824 | Inverter Parameters (Setup) | 0xB945 | 47429 | Reactivepoweradjustmentperiod | U16 | FC03/FC06 | 1 | s |  | RW
825 | Inverter Parameters (Setup) | 0xB946 | 47430 | Adjusting Dead Zone | U16 | FC03/FC06 | 1 |  |  | RW
826 | Inverter Parameters (Setup) | 0xB947 | 47431 | Compensatingdelay | U16 | FC03/FC06 | 1 | s |  | RW
827 | Inverter Parameters (Setup) | 0xB948 | 47432 | Failureprotectionreactivepowerlimit [PF] | S16 | FC03/FC06 | 1 |  |  | RW | This parameter is displayed only when Communication Disconnection Failure Protection is set to Enabled and Reactive Powe
828 | Inverter Parameters (Setup) | 0xB949 | 47433 | Plantcapacity | U32 | FC03/FC06 | 2 | kW |  | RW
829 | Inverter Parameters (Setup) | 0xB94B | 47435 | Powerplant DC capacity | U32 | FC03/FC06 | 2 | kW |  | RW
830 | Inverter Parameters (Setup) | 0xB94D | 47437 | [Remote Output] Certificate | U16 | FC03/FC06 | 1 |  |  | RW | Note: "Output Control" is a direct reference in Japanese name, which essentially expresses the active output control und
831 | Inverter Parameters (Setup) | 0xB94E | 47438 | [Remoteoutput] PV plant ID | string | FC03/FC06 | 13 |  |  | RW | Only 26 digits are supported.
832 | Inverter Parameters (Setup) | 0xB95B | 47451 | [Remoteoutput] Remoteoutputcontrolserver | string | FC03/FC06 | 30 |  |  | RW | Other server addresses can be manually entered.
833 | Inverter Parameters (Setup) | 0xB979 | 47481 | [Remote Output] Remote Output Control Time | U16 | FC03/FC06 | 1 | min |  | RW | It refers to the time that the output of the plant is controlled from 0% to 100%.
834 | Inverter Parameters (Setup) | 0xB97A | 47482 | [Remoteoutput] Connectingtothedispatchserver | U16 | FC06 | 1 |  |  | WO
835 | Inverter Parameters (Setup) | 0xB97B | 47483 | closedloopcontroller | U16 | FC03/FC06 | 1 |  |  | RW | Note: The external controller uses the exponential data source or Dongle. In this case, the inverter does not perform th
836 | Inverter Parameters (Setup) | 0xB9EA | 47594 | [Local Access] Link Enabled | U16 | FC03/FC06 | 1 |  |  | RW
837 | Inverter Parameters (Setup) | 0xB9EB | 47595 | [Localaccess] Client 1 IP address | IPv4 | FC03/FC06 | 2 |  |  | RW
838 | Inverter Parameters (Setup) | 0xBA3A | 47674 | Schedule Task | U16 | FC03/FC06 | 1 |  |  | RW | South Australia Dynamic Feeder Requirements
839 | Inverter Parameters (Setup) | 0xBA3B | 47675 | Maximum Feed Grid Power Default | S32 | FC03/FC06 | 2 | kW |  | RW | Power limit on the grid-tied point when the default task is executed for the dynamic feeder network in South Australia.
840 | Inverter Parameters (Setup) | 0xBA3D | 47677 | Defaultactivepowerchangegradient | U32 | FC03/FC06 | 2 | %/s |  | RW | Power change rate during switchover between the default task and the planned task in South Australia dynamic feeder netw
841 | Inverter Parameters (Setup) | 0xBB4E | 47950 | Feedingpowerover- thresholdprotectionshutdown | U16 | FC03/FC06 | 1 | 1 |  | RW
842 | Inverter Parameters (Setup) | 0xBB4F | 47951 | Feedthreshold - crossingprotectionshutdownthreshold | S32 | FC03/FC06 | 2 | 1000 |  | RW
843 | Inverter Parameters (Setup) | 0xBB51 | 47953 | Feedthreshold - crossingprotectionshutdowntime | U16 | FC03/FC06 | 1 | 1 |  | RW
844 | Inverter Parameters (Setup) | 0xBB95 | 48021 | [Management System - 1] Management System Access | U16 | FC03/FC06 | 1 | N/A |  | RW
845 | Inverter Parameters (Setup) | 0xBBD7 | 48087 | [Management System- 1] Protocol Type | U16 | FC03/FC06 | 1 |  |  | RW | Automatically adapt to the "1" protocol for the SkyTeam OEM model.
846 | Inverter Parameters (Setup) | 0xBBDA | 48090 | Groundshortcircuitprotection | U16 | FC03/FC06 | 1 |  |  | RW

## Status_Definitions
Code | Name | Description | Bit_Definition
0 | INITIAL | Initial mode
1 | STANDBY | Standby mode
3 | ON_GRID | On-Grid mode
4 | OFF_GRID | Off-Grid mode
5 | FAULT | Fault mode
9 | SHUTDOWN | Shutdown mode
NOTE: Add/edit status codes. Descriptions used in Stage 2 InverterMode mapping.

## Error_Fault_Codes
Register | Bit | Error_No | Description | Notes
(No error codes detected from PDF)

## Grid_Codes
Code_Hex | Description
(No regulation codes detected from PDF)
NOTE: Register 0x5101 - Grid regulation/country code setting

## Fuse_Open_Data
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x1034~0x1035 — PV string fuse open status bits

## Status_Bits_03FC
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x03FC~03FD — DEA-AVM inverter action/run-state bits

## Fuse_Check_Mask
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x513D~0x513E — PV string fuse check enable/disable mask

## REMS_Error_Bits
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: REMS Error Code register — bit-field inverter alarm flags

## REMS_Registers
No | Description | Length_Bytes | Unit
(Not detected from PDF)
NOTE: REMS protocol register layout (function code 0x7E)