## Registers
No | Section | Address_Hex | Address_Dec | Definition | Data_Type | FC_Code | Registers | Unit | Scale_Factor | R/W | Description
--- Inverter Realtime Data ---
1 | Inverter Realtime Data | 0x0B94 | 2964 | PV12 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
2 | Inverter Realtime Data | 0x0B95 | 2965 | PV12 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
3 | Inverter Realtime Data | 0x0B96 | 2966 | PV12 input power | S32 | FC03 | 2 | 1W | 1 | RO
4 | Inverter Realtime Data | 0x0B98 | 2968 | PV11 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
5 | Inverter Realtime Data | 0x0B99 | 2969 | PV11 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
6 | Inverter Realtime Data | 0x0B9A | 2970 | PV11 input power | S32 | FC03 | 2 | 1W | 1 | RO
7 | Inverter Realtime Data | 0x0B9C | 2972 | PV10 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
8 | Inverter Realtime Data | 0x0B9D | 2973 | PV10 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
9 | Inverter Realtime Data | 0x0B9E | 2974 | PV10 input power | S32 | FC03 | 2 | 1W | 1 | RO
10 | Inverter Realtime Data | 0x0BA0 | 2976 | PV9 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
11 | Inverter Realtime Data | 0x0BA1 | 2977 | PV9 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
12 | Inverter Realtime Data | 0x0BA2 | 2978 | PV9 input power | S32 | FC03 | 2 | 1W | 1 | RO
13 | Inverter Realtime Data | 0x0BA4 | 2980 | PV8 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
14 | Inverter Realtime Data | 0x0BA5 | 2981 | PV8 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
15 | Inverter Realtime Data | 0x0BA6 | 2982 | PV8 input power | S32 | FC03 | 2 | 1W | 1 | RO
16 | Inverter Realtime Data | 0x0BA8 | 2984 | PV7 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
17 | Inverter Realtime Data | 0x0BA9 | 2985 | PV7 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
18 | Inverter Realtime Data | 0x0BAA | 2986 | PV7 input power | S32 | FC03 | 2 | 1W | 1 | RO
19 | Inverter Realtime Data | 0x0BAC | 2988 | PV6 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
20 | Inverter Realtime Data | 0x0BAD | 2989 | PV6 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
21 | Inverter Realtime Data | 0x0BAE | 2990 | PV6 input power | S32 | FC03 | 2 | 1W | 1 | RO
22 | Inverter Realtime Data | 0x0BB0 | 2992 | PV5 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
23 | Inverter Realtime Data | 0x0BB1 | 2993 | PV5 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
24 | Inverter Realtime Data | 0x0BB2 | 2994 | PV5 input power | S32 | FC03 | 2 | 1W | 1 | RO
25 | Inverter Realtime Data | 0x0BB4 | 2996 | PV4 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
26 | Inverter Realtime Data | 0x0BB5 | 2997 | PV4 input current | S16 | FC03 | 1 | 0.01A | 0.01 | RO
27 | Inverter Realtime Data | 0x0BB6 | 2998 | PV4 input power | S32 | FC03 | 2 | 1W | 1 | RO
28 | Inverter Realtime Data | 0x0BB8 | 3000 | PV1 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
29 | Inverter Realtime Data | 0x0BB9 | 3001 | PV2 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO | 1-3K not have.
30 | Inverter Realtime Data | 0x0BBA | 3002 | PV3 input voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO | 1-5K not have.
31 | Inverter Realtime Data | 0x0BBB | 3003 | PV1 input current | U16 | FC03 | 1 | 0.01A | 0.01 | RO
32 | Inverter Realtime Data | 0x0BBC | 3004 | PV2 input current | U16 | FC03 | 1 | 0.01A | 0.01 | RO | 1-3K not have.
33 | Inverter Realtime Data | 0x0BBD | 3005 | PV3 input current | U16 | FC03 | 1 | 0.01A | 0.01 | RO | 1-5K not have.
34 | Inverter Realtime Data | 0x0BBE | 3006 | PV1 input power | S32 | FC03 | 2 | 1W | 1 | RO
35 | Inverter Realtime Data | 0x0BC0 | 3008 | PV2 input power | S32 | FC03 | 2 | 1W | 1 | RO | 1-3K not have.
36 | Inverter Realtime Data | 0x0BC2 | 3010 | PV3 input power | S32 | FC03 | 2 | 1W | 1 | RO | 1-5K not have.
37 | Inverter Realtime Data | 0x0BC4 | 3012 | PBUS voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
38 | Inverter Realtime Data | 0x0BC5 | 3013 | NBUS voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO | 1-5K not have.
39 | Inverter Realtime Data | 0x0BC6 | 3014 | RS-phase grid voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
40 | Inverter Realtime Data | 0x0BC7 | 3015 | ST-phase grid voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO | 1-5K not have.
41 | Inverter Realtime Data | 0x0BC8 | 3016 | TR-phase grid voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO | 1-5K not have.
42 | Inverter Realtime Data | 0x0BC9 | 3017 | RS-phase grid frequency | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO
43 | Inverter Realtime Data | 0x0BCA | 3018 | ST-phase grid frequency | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO | 1-5K not have.
44 | Inverter Realtime Data | 0x0BCB | 3019 | TR-phase grid frequency | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO | 1-5K not have.
45 | Inverter Realtime Data | 0x0BCC | 3020 | R-phase grid-tied current | U16 | FC03 | 1 | 0.01A | 0.01 | RO
46 | Inverter Realtime Data | 0x0BCD | 3021 | S-phase grid-tied current | U16 | FC03 | 1 | 0.01A | 0.01 | RO | 1-5K not have.
47 | Inverter Realtime Data | 0x0BCE | 3022 | T-phase grid-tied current | U16 | FC03 | 1 | 0.01A | 0.01 | RO | 1-5K not have.
48 | Inverter Realtime Data | 0x0BCF | 3023 | Grid-tied power | S32 | FC03 | 2 | 1W | 1 | RO
49 | Inverter Realtime Data | 0x0BD1 | 3025 | Radiator temperature | S16 | FC03 | 1 | 0. 1℃ |  | RO
50 | Inverter Realtime Data | 0x0BD2 | 3026 | Module temperature | S16 | FC03 | 1 | 0. 1℃ |  | RO | 1-5K not have.
51 | Inverter Realtime Data | 0x0BD3 | 3027 | DSP alarm code | U16 | FC03 | 1 |  |  | RO
52 | Inverter Realtime Data | 0x0BD4 | 3028 | DSP error code | U32 | FC03 | 2 |  |  | RO
53 | Inverter Realtime Data | 0x0BD6 | 3030 | Operating | U8 | FC03 | 1 |  |  | RO | mode ¦ of ¦ the ¦ inverter
54 | Inverter Realtime Data | 0x0BD7 | 3031 | Rotational speed of fan A | U16 | FC03 | 1 | r/min |  | RO
55 | Inverter Realtime Data | 0x0BD8 | 3032 | Rotational speed of fan B | U16 | FC03 | 1 | r/min |  | RO | 1-5K not have.
56 | Inverter Realtime Data | 0x0BD9 | 3033 | Rotational speed of fan C | U16 | FC03 | 1 | r/min |  | RO | 1-5K not have.
57 | Inverter Realtime Data | 0x0BDA | 3034 | Reserve. | U32 | FC03 | 2 |  |  | RO
58 | Inverter Realtime Data | 0x0BDC | 3036 | ARM alarm code | U8 | FC03 | 1 |  |  | RO
59 | Inverter Realtime Data | 0x0BDD | 3037 | Input mode | U8 | FC03 | 1 |  |  | RO
60 | Inverter Realtime Data | 0x0BDE | 3038 | Total energy yield | U32 | FC03 | 2 | 0.1Kwh | 0.1 | RO
61 | Inverter Realtime Data | 0x0BE0 | 3040 | Annual energy yield | U32 | FC03 | 2 | Kwh |  | RO
62 | Inverter Realtime Data | 0x0BE2 | 3042 | Daily energy yield | U16 | FC03 | 1 | Kwh |  | RO
63 | Inverter Realtime Data | 0x0BE3 | 3043 | Power-on voltage | U16 | FC03 | 1 | 0.1V | 0.1 | RO
64 | Inverter Realtime Data | 0x0BE4 | 3044 | Power-on delay | U16 | FC03 | 1 | S |  | RO | 20-300
65 | Inverter Realtime Data | 0x0BE5 | 3045 | Lower | U16 | FC03 | 1 | 0.1V | 0.1 | RO | grid ¦ voltage ¦ threshold
66 | Inverter Realtime Data | 0x0BE6 | 3046 | Upper | U16 | FC03 | 1 | 0.1V | 0.1 | RO | grid ¦ voltage ¦ threshold
67 | Inverter Realtime Data | 0x0BE7 | 3047 | Lower | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO | grid ¦ frequency ¦ threshold
68 | Inverter Realtime Data | 0x0BE8 | 3048 | Upper | U16 | FC03 | 1 |  |  | RO | grid ¦ frequency ¦ threshold ¦ 0.01 Hz
69 | Inverter Realtime Data | 0x0BE9 | 3049 | Preset power factor | U16 | FC03 | 1 |  |  | RO
70 | Inverter Realtime Data | 0x0BEA | 3050 | Preset active power | U16 | FC03 | 1 | % |  | RO
71 | Inverter Realtime Data | 0x0BEB | 3051 | Preset reactive power | S8 | FC03 | 1 | 1KVar | 1 | RO
72 | Inverter Realtime Data | 0x0BEC | 3052 | Apparent power | S32 | FC03 | 2 | 1VA | 1 | RO
73 | Inverter Realtime Data | 0x0BEE | 3054 | Reactive power | S32 | FC03 | 2 | 1Var | 1 | RO
74 | Inverter Realtime Data | 0x0BF0 | 3056 | Power factor | U16 | FC03 | 1 |  |  | RO
75 | Inverter Realtime Data | 0x0BF1 | 3057 | DC insulation resistance | U16 | FC03 | 1 | Kohm |  | RO | 1-5K not have.
76 | Inverter Realtime Data | 0x0BF2 | 3058 | Overfrequency derating |  | FC03 | 1 |  |  | RO | 0: enabled ¦ 1: disabled
77 | Inverter Realtime Data | 0x0BF3 | 3059 | Overfrequency |  | FC03 | 1 |  |  | RO | derating ¦ threshold
78 | Inverter Realtime Data | 0x0BF4 | 3060 | Derating rate |  | FC03 | 1 | 0.01Hz | 0.01 | RO
79 | Inverter Realtime Data | 0x0BF5 | 3061 | Reserved |  | FC03 | 1 |  |  | RO
80 | Inverter Realtime Data | 0x0BF6 | 3062 | Reserved |  | FC03 | 1 |  |  | RO
81 | Inverter Realtime Data | 0x0BF7 | 3063 | Reserved |  | FC03 | 1 |  |  | RO
82 | Inverter Realtime Data | 0x0BF8 | 3064 | PV1 String current 1 | S16 | FC03 | 1 | 0.01A | 0.01 | RO | No ¦ string ¦ current ¦ in ¦ single phase inverter.
83 | Inverter Realtime Data | 0x0BF9 | 3065 | PV1 String current 2 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
84 | Inverter Realtime Data | 0x0BFA | 3066 | PV1 String current 3 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
85 | Inverter Realtime Data | 0x0BFB | 3067 | PV1 String current 4 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
86 | Inverter Realtime Data | 0x0BFC | 3068 | PV2 String current 1 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
87 | Inverter Realtime Data | 0x0BFD | 3069 | PV2 String current 2 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
88 | Inverter Realtime Data | 0x0BFE | 3070 | PV2 String current 3 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
89 | Inverter Realtime Data | 0x0BFF | 3071 | PV2 String current 4 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
90 | Inverter Realtime Data | 0x0C00 | 3072 | PV3 String current 1 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
91 | Inverter Realtime Data | 0x0C01 | 3073 | PV3 String current 2 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
92 | Inverter Realtime Data | 0x0C02 | 3074 | PV3 String current 3 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
93 | Inverter Realtime Data | 0x0C03 | 3075 | PV3 String current 4 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
94 | Inverter Realtime Data | 0x0C04 | 3076 | PV4 String current 1 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
95 | Inverter Realtime Data | 0x0C05 | 3077 | PV4 String current 2 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
96 | Inverter Realtime Data | 0x0C06 | 3078 | PV4 String current 3 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
97 | Inverter Realtime Data | 0x0C07 | 3079 | PV4 String current 4 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
98 | Inverter Realtime Data | 0x0C08 | 3080 | PV5 String current 1 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
99 | Inverter Realtime Data | 0x0C09 | 3081 | PV5 String current 2 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
100 | Inverter Realtime Data | 0x0C0A | 3082 | PV5 String current 3 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
101 | Inverter Realtime Data | 0x0C0B | 3083 | PV5 String current 4 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
102 | Inverter Realtime Data | 0x0C0C | 3084 | PV6 String current 1 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
103 | Inverter Realtime Data | 0x0C0D | 3085 | PV6 String current 2 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
104 | Inverter Realtime Data | 0x0C0E | 3086 | PV6 String current 3 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
105 | Inverter Realtime Data | 0x0C0F | 3087 | PV6 String current 4 | S16 | FC03 | 1 | 0.01A | 0.01 | RO
106 | Inverter Realtime Data | 0x0C10 | 3088 | Reserve |  | FC03 | 1 |  |  | RO
107 | Inverter Realtime Data | 0x0C11 | 3089 | Reserve |  | FC03 | 1 |  |  | RO
108 | Inverter Realtime Data | 0x0C12 | 3090 | Running Time | U32 | FC03 | 2 | Hour |  | RO
109 | Inverter Realtime Data | 0x0C14 | 3092 | Generating Time | U32 | FC03 | 2 | Hour |  | RO
110 | Inverter Realtime Data | 0x0C16 | 3094 | Number | U32 | FC03 | 2 |  |  | RO | of ¦ grid ¦ connection
111 | Inverter Realtime Data | 0x0C18 | 3096 | Power Peak After Starting | U32 | FC03 | 2 | W |  | RO
112 | Inverter Realtime Data | 0x0C1A | 3098 | Day Generation | U32 | FC03 | 2 | W |  | RO
113 | Inverter Realtime Data | 0x0C1C | 3100 | Week Generation | U32 | FC03 | 2 | Kwh |  | RO
114 | Inverter Realtime Data | 0x0C1E | 3102 | Month Generation | U32 | FC03 | 2 | Kwh |  | RO
115 | Inverter Realtime Data | 0x0C20 | 3104 | Last N days Generation | U32 | FC03 | 2 | Kwh |  | RO
116 | Inverter Realtime Data | 0x0C22 | 3106 | Value of N | U16 | FC03 | 1 |  |  | RO
117 | Inverter Realtime Data | 0x0C23 | 3107 | Year | U16 | FC03 | 1 |  |  | RO
118 | Inverter Realtime Data | 0x0C24 | 3108 | Month | U16 | FC03 | 1 |  |  | RO
119 | Inverter Realtime Data | 0x0C25 | 3109 | Date | U16 | FC03 | 1 |  |  | RO
120 | Inverter Realtime Data | 0x0C26 | 3110 |  | U16 | FC03 | 1 | Hour |  | RO
121 | Inverter Realtime Data | 0x0C27 | 3111 | Minute | U16 | FC03 | 1 |  |  | RO
122 | Inverter Realtime Data | 0x0C28 | 3112 | Second | U16 | FC03 | 1 |  |  | RO
123 | Inverter Realtime Data | 0x0C29 | 3113 | Week | U16 | FC03 | 1 |  |  | RO
124 | Inverter Realtime Data | 0x0C2A | 3114 | Back-current Power Limit | U16 | FC03 | 1 | W |  | RO | Setting
125 | Inverter Realtime Data | 0x0C2B | 3115 | Active Power of Soft Start | U16 | FC03 | 1 | %/min |  | RO | Change Rate
126 | Inverter Realtime Data | 0x0C2C | 3116 | Reserve | U16 | FC03 | 1 |  |  | RO
127 | Inverter Realtime Data | 0x0C2D | 3117 | 485Address(2) | U16 | FC03 | 1 |  |  | RO | 1-64
128 | Inverter Realtime Data | 0x0C2E | 3118 | 485 Baud Rate (2) | U16 | FC03 | 1 |  |  | RO
129 | Inverter Realtime Data | 0x0C2F | 3119 | 485 Agreement | U16 | FC03 | 1 |  |  | RO
130 | Inverter Realtime Data | 0x0C30 | 3120 | 485 Address(1) | U16 | FC03 | 1 |  |  | RO | 1-64
131 | Inverter Realtime Data | 0x0C31 | 3121 | 485Baud Rate(1) | U16 | FC03 | 1 |  |  | RO
132 | Inverter Realtime Data | 0x0C32 | 3122 | Three-phase System | U16 | FC03 | 1 |  |  | RO
133 | Inverter Realtime Data | 0x0C33 | 3123 | Remote Control Enable | U16 | FC03 | 1 |  |  | RO | 0:Disable ¦ 1:Enable
134 | Inverter Realtime Data | 0x0C34 | 3124 | String Test Threshold | U16 | FC03 | 1 | A |  | RO | 5-25
135 | Inverter Realtime Data | 0x0C35 | 3125 | Setting | U16 | FC03 | 1 |  |  | RO | Value ¦ of ¦ Self-check
136 | Inverter Realtime Data | 0x0C36 | 3126 | I/V Scan-status | U16 | FC03 | 1 |  |  | RO
137 | Inverter Realtime Data | 0x0C37 | 3127 | QV Curve | U16 | FC03 | 6 |  |  | RO
138 | Inverter Realtime Data | 0x0C3D | 3133 | R-phase | U16 | FC03 | 1 |  |  | RO | Voltage ¦ Calibration Factor ¦ Default：4096
139 | Inverter Realtime Data | 0x0C3E | 3134 | S-phase | U16 | FC03 | 1 |  |  | RO | Voltage ¦ Calibration Factor ¦ Default：4096
140 | Inverter Realtime Data | 0x0C3F | 3135 | T-phase | U16 | FC03 | 1 |  |  | RO | Voltage ¦ Calibration Factor ¦ Default：4096
141 | Inverter Realtime Data | 0x0C40 | 3136 | R-phase | U16 | FC03 | 1 |  |  | RO | Current ¦ Calibration Factor ¦ Default：4096
142 | Inverter Realtime Data | 0x0C41 | 3137 | S-phase Calibration Factor | U16 | FC03 | 1 |  |  | RO | Default：4096
143 | Inverter Realtime Data | 0x0C42 | 3138 | T-phase | U16 | FC03 | 1 |  |  | RO | Current ¦ Calibration Factor ¦ Default：4096
144 | Inverter Realtime Data | 0x0C43 | 3139 | Battery | U16 | FC03 | 1 |  |  | RO | Voltage ¦ Calibration Factor ¦ Default：4096
145 | Inverter Realtime Data | 0x0C44 | 3140 | Bluetooth enable | U16 | FC03 | 1 |  |  | RO | Default value：1 ¦ 0: prohibit ¦ 1: ¦ permit
146 | Inverter Realtime Data | 0x0C45 | 3141 | Reserved |  | FC03 | 4 |  |  | RO | (small ¦ three-phase) ¦ 354-
147 | Inverter Realtime Data | 0x0C4A | 3146 | Underfrequency | U16 | FC03 | 1 | % |  | RO | increase slope ¦ 1-100
148 | Inverter Realtime Data | 0x0C4B | 3147 | FrozenUpFreqEnb | U16 | FC03 | 1 |  |  | RO | Under ¦ frequency ¦ increase ¦ ON/OFF ¦ 0: ON ¦ 1: OFF
149 | Inverter Realtime Data | 0x0C4C | 3148 | FrozenUpFreq | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO | Underfrequency ¦ increase threshold ¦ 50Hz Grid standards ¦ 4500~5995 ¦ Default value：4500
150 | Inverter Realtime Data | 0x0C4D | 3149 | Slow increase in power | U16 | FC03 | 1 |  |  | RO | S（秒） ¦ 0~600 ¦ （Default value：0）
151 | Inverter Realtime Data | 0x0C4E | 3150 | Overfrequency | U16 | FC03 | 1 |  |  | RO | power ¦ reduction percentage ¦ 0.0001 ¦ Pref/Hz ¦ 0~4000 ¦ （Default value：0）
152 | Inverter Realtime Data | 0x0C4F | 3151 | FrozenUpVoltStart | U16 | FC03 | 1 | 0.1V | 0.1 | RO | Starting ¦ value ¦ of ¦ overvoltage derating ¦ four-wire：2200~3000
153 | Inverter Realtime Data | 0x0C50 | 3152 | FrozenUpVoltEnd | U16 | FC03 | 1 | 0.1V | 0.1 | RO | End ¦ value ¦ of ¦ overvoltage derating ¦ four-wire：2200~3000
154 | Inverter Realtime Data | 0x0C51 | 3153 | NPEVoltSet |  | FC03 | 1 |  |  | RO | Zero ¦ line ¦ to ¦ ground ¦ voltage ¦ detection ¦ threshold
155 | Inverter Realtime Data | 0x0C7A | 3194 | PLC area code | U16 | FC03 | 1 |  |  | RO | 460 ¦ Default value：1
156 | Inverter Realtime Data | 0x0C7B | 3195 | Bluetooth name format | U16 | FC03 | 1 |  |  | RO | 462 ¦ 0：Default value ¦ 1：Haixing ¦ Customization Format
157 | Inverter Realtime Data | 0x0C7C | 3196 | Setting value of rated | U16 | FC03 | 1 |  |  | RO | power for anti backflow ¦ 464 ¦ 0-Pmax，unit KW
158 | Inverter Realtime Data | 0x0C7D | 3197 | Upper | U16 | FC03 | 1 | 0.01A | 0.01 | RO | limit ¦ of ¦ fuse ¦ detection ¦ 466 ¦ scope 0.60-3.00A，
159 | Inverter Realtime Data | 0x0C7E | 3198 | Lower | U16 | FC03 | 1 | 0.01A | 0.01 | RO | limit ¦ of ¦ fuse ¦ detection ¦ 468 ¦ scope 0.10-0.50A，
160 | Inverter Realtime Data | 0x0C7F | 3199 | Fuse detection enable | U32 | FC03 | 2 |  |  | RO | 470 ¦ 0-23 bits valid， ¦ Enable by setting 1, ¦ disable by setting 0
161 | Inverter Realtime Data | 0x0C81 | 3201 | Fuse alarm information | U32 | FC03 | 2 |  |  | RO | 474 ¦ 0-23 bits valid，
162 | Inverter Realtime Data | 0x0C83 | 3203 | Anti | U16 | FC03 | 1 |  |  | RO | backflow ¦ meter ¦ configuration ¦ 478 ¦ / ¦ （0xXXXX）16 ¦ The
163 | Inverter Realtime Data | 0x0C84 | 3204 | Correction |  | FC03 | 1 |  |  | RO | value ¦ of ¦ anti ¦ reverse ¦ current ¦ meter ¦ 480 ¦ W（瓦）
164 | Inverter Realtime Data | 0x0C85 | 3205 | CT ratio | U16 | FC03 | 1 |  |  | RO
165 | Inverter Realtime Data | 0x0C8E | 3214 | PV1 | U16 | FC03 | 1 |  |  | RO | current ¦ calibration ¦ coefficient ¦ scope：3686~4505
166 | Inverter Realtime Data | 0x0C8F | 3215 | PV2 | U16 | FC03 | 1 |  |  | RO | current ¦ calibration ¦ coefficient ¦ scope：3686~4505
167 | Inverter Realtime Data | 0x0C9A | 3226 | Power change rate | U16 | FC03 | 1 |  |  | RO | %/s ¦ scope：1~100%
168 | Inverter Realtime Data | 0x0C9B | 3227 | Over | U16 | FC03 | 1 |  |  | RO | temperature ¦ derating ¦ warning ¦ enable ¦ Enable: 1 Prohibit: 0
169 | Inverter Realtime Data | 0x0C9C | 3228 | Soft start time | U16 | FC03 | 1 | s |  | RO | scope：1~30000s
170 | Inverter Realtime Data | 0x0C9D | 3229 | Low | U16 | FC03 | 1 |  |  | RO | penetration ¦ coefficient ¦ scope 0~100，Default ¦ value 2
171 | Inverter Realtime Data | 0x0C9E | 3230 | High | U16 | FC03 | 1 |  |  | RO | penetration ¦ coefficient ¦ scope 0~100，Default ¦ value 2
172 | Inverter Realtime Data | 0x0C9F | 3231 | Upper | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO | limit ¦ of ¦ frequency ¦ response ¦ dead band ¦ scope：5000~5500
173 | Inverter Realtime Data | 0x0CA0 | 3232 | Lower | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO | limit ¦ of ¦ frequency ¦ response ¦ dead band ¦ scope：4500~5000
174 | Inverter Realtime Data | 0x0CA1 | 3233 | Over | U16 | FC03 | 1 |  |  | RO | frequency ¦ derating coefficient ¦ Pn%/Hz ¦ scope：0~200 ¦ Default value：20
175 | Inverter Realtime Data | 0x0CA2 | 3234 | Underfrequency | U16 | FC03 | 1 |  |  | RO | amplification ¦ coefficient ¦ Pn%/Hz ¦ scope：0~200 ¦ Default value：20
176 | Inverter Realtime Data | 0x0CA3 | 3235 | Maximum Derating | U16 | FC03 | 1 | % |  | RO | scope：0~100 ¦ Default value：50
177 | Inverter Realtime Data | 0x0CA4 | 3236 | Maximum increase | U16 | FC03 | 1 | % |  | RO | scope：0~100 ¦ Default value：50
178 | Inverter Realtime Data | 0x0CA5 | 3237 | Debugging | S16 | FC03 | 1 |  |  | RO | coefficient ¦ -32768 ~ 32767
179 | Inverter Realtime Data | 0x0CA6 | 3238 | Debugging | S16 | FC03 | 1 |  |  | RO | coefficient ¦ -32768 ~ 32767
180 | Inverter Realtime Data | 0x0CA7 | 3239 | Debugging | S16 | FC03 | 1 |  |  | RO | coefficient ¦ -32768 ~ 32767
181 | Inverter Realtime Data | 0x0CA8 | 3240 | Debugging | S16 | FC03 | 2 |  |  | RO | coefficient ¦ -32768 ~ 32767
182 | Inverter Realtime Data | 0x0CA9 | 3241 | Daily power generation | U16 | FC03 | 1 | 0.1Kwh | 0.1 | RO | (0.1Kwh) ¦ 554
183 | Inverter Realtime Data | 0x0CAA | 3242 | Accumulated | U32 | FC03 | 2 | Kwh |  | RO | load ¦ electricity ¦ consumption on the grid ¦ side ¦ 556 ¦ 0~9999999
184 | Inverter Realtime Data | 0x0CAC | 3244 | Frequency | U16 | FC03 | 1 |  |  | RO | response ¦ hysteresis function ¦ 550 ¦ Enable: 0, Prohibit: 1
185 | Inverter Realtime Data | 0x0CAD | 3245 | Active reactive curve | U16 | FC03 | 1 |  |  | RO | 562 ¦ Enable: 0, Prohibit: 1
186 | Inverter Realtime Data | 0x0CAE | 3246 | Grid protected mode | U16 | FC03 | 1 |  |  | RO | 564 ¦ 0: Grid standard ¦ 1: Customize
187 | Inverter Realtime Data | 0x0CAF | 3247 | Grid type | U16 | FC03 | 1 |  |  | RO | 566 ¦ 0: ¦ Distribution ¦ network ¦ 1: ¦ Transmission ¦ network
188 | Inverter Realtime Data | 0x0CB0 | 3248 | Fault recovery time | U16 | FC03 | 1 |  |  | RO | 568 ¦ 0~1800 Default ¦ value ¦ 20s
189 | Inverter Realtime Data | 0x0CB1 | 3249 | Night SVG function | U16 | FC03 | 1 |  |  | RO | 570 ¦ Enable: 0, Prohibit: 1
190 | Inverter Realtime Data | 0x0CB2 | 3250 | IV | U16 | FC03 | 1 |  |  | RO | curve ¦ scanning ¦ function ¦ 572 ¦ Enable: 0, Prohibit: 1
191 | Inverter Realtime Data | 0x0CB3 | 3251 | R-phase | U16 | FC03 | 1 |  |  | RO | voltage ¦ calibration ¦ coefficient 2 ¦ 574 ¦ Default value：4096
192 | Inverter Realtime Data | 0x1388 | 5000 | PV1 Voltage Point 1 | U16 | FC03 | 1 | 0.1V | 0.1 | RO | IV scans data, occupying ¦ 2400 registers. When the ¦ register value is 0xFFFF,
193 | Inverter Realtime Data | 0x1388 | 5000 | Hight |  | FC03 | 251 | 60Hz | 60 | RO | voltage ¦ LN:600-650 ¦ LL:1100-1150 ¦ LN:1850-1900 ¦ LL:3250-3300
194 | Inverter Realtime Data | 0x12C0 | 4800 |  |  | FC03 | 1 |  |  | RO
--- Device Information (System Info) ---
195 | Device Information (System Info) | 0x0C80 | 3200 | Machine model | U8 | FC03 | 5 |  |  | RO | ASCII code
196 | Device Information (System Info) | 0x0C85 | 3205 | DSP version | U8 | FC03 | 1 |  |  | RO | 10 indicates V1.0.
197 | Device Information (System Info) | 0x0C86 | 3206 | Inverter SN | U8 | FC03 | 11 |  |  | RO | ASCII character
198 | Device Information (System Info) | 0x0C91 | 3217 | PLC MAC Address | U8 | FC03 | 3 |  |  | RO | MAC address
199 | Device Information (System Info) | 0x0C94 | 3220 | LCD Model Setting | U8 | FC03 | 1 |  |  | RO
200 | Device Information (System Info) | 0x0C95 | 3221 | Inverter | U8 | FC03 | 8 |  |  | RO | Model ¦ （New） ¦ ASCII character
201 | Device Information (System Info) | 0x0C9D | 3229 | DSP1 | U8 | FC03 | 1 |  |  | RO | Test ¦ version ¦ number ¦ Note 1
202 | Device Information (System Info) | 0x0C9E | 3230 | DSP2 version number | U8 | FC03 | 1 |  |  | RO | 10 means V1.0
203 | Device Information (System Info) | 0x0C9F | 3231 | Reserve | U8 | FC03 | 2 |  |  | RO
--- Inverter Parameters (Setup) ---
204 | Inverter Parameters (Setup) | 0x0CE4 | 3300 | Clock information | U8 | FC03 | 7 |  |  | RO
205 | Inverter Parameters (Setup) | 0x0CEB | 3307 | QV | U16 | FC03 | 4 |  |  | RO | Active ¦ Factor
206 | Inverter Parameters (Setup) | 0x0CEF | 3311 | Setting Inverter SN | string | FC03/FC06 | 12 |  |  | RW
207 | Inverter Parameters (Setup) | 0x0CFB | 3323 | Setting PLC MAC | U8 | FC03/FC06 | 3 |  |  | RW
208 | Inverter Parameters (Setup) | 0x0CFE | 3326 | QV Curve (2) | U16 | FC03 | 6 |  |  | RO
209 | Inverter Parameters (Setup) | 0x0D04 | 3332 | LCD Model Setting | U8 | FC03 | 1 |  |  | RO
210 | Inverter Parameters (Setup) | 0x0D05 | 3333 | Inverter Model | U8 | FC03/FC06 | 8 |  |  | RW
211 | Inverter Parameters (Setup) | 0x0CE4 | 3300 | Year (tens place) | U8 | FC03 | 1 |  |  | RO | ASCII code ¦ Year (ones place) ¦ U8 ¦ ASCII code
212 | Inverter Parameters (Setup) | 0x0CE5 | 3301 | Month (tens place) | U8 | FC03 | 1 |  |  | RO | ASCII code ¦ Month (ones place) ¦ U8 ¦ ASCII code
213 | Inverter Parameters (Setup) | 0x0CE6 | 3302 | Day (tens place) | U8 | FC03 | 1 |  |  | RO | ASCII code ¦ Day (ones place) ¦ U8 ¦ ASCII code
214 | Inverter Parameters (Setup) | 0x0CE7 | 3303 | Hour (tens place) | U8 | FC03 | 1 |  |  | RO | ASCII code ¦ Hour (ones place) ¦ U8 ¦ ASCII code
215 | Inverter Parameters (Setup) | 0x0CE8 | 3304 | Minute (tens place) | U8 | FC03 | 1 |  |  | RO | ASCII code ¦ Minute (ones place) ¦ U8 ¦ ASCII code
216 | Inverter Parameters (Setup) | 0x0CE9 | 3305 | Second (tens place) | U8 | FC03 | 1 |  |  | RO | ASCII code ¦ Second (ones place) ¦ U8 ¦ ASCII code
217 | Inverter Parameters (Setup) | 0x0CEA | 3306 | Week | U8 | FC03 | 1 |  |  | RO | ASCII code ¦ U8 ¦ ASCII code
--- DER-AVM Parameters (Control) ---
218 | DER-AVM Parameters (Control) | 0x0D04 | 3332 | LCD Model |  | FC03 | 1 |  |  | RO | Setting ¦ 0,1,2 ¦ null ¦ 0: Self- recognition ¦ The inverter will be automatically recognized after ¦ boot User Settings are disabled in this mode. ¦ 1: Topway ¦ If set to Topway, the external screen is Topway
219 | DER-AVM Parameters (Control) | 0x0FA0 | 4000 | Clear statistical | U16 | FC03/FC06 | 1 |  |  | RW | information ¦ DATA arbitrary number
220 | DER-AVM Parameters (Control) | 0x0FA1 | 4001 | Remote | U16 | FC03/FC06 | 1 |  |  | RW | power-off ¦ DATA arbitrary number
221 | DER-AVM Parameters (Control) | 0x0FA2 | 4002 | Revoke remote | U16 | FC03/FC06 | 1 |  |  | RW | power-off ¦ DATA arbitrary number
222 | DER-AVM Parameters (Control) | 0x0FA3 | 4003 | Set the power | U16 | FC03 | 1 |  |  | RO | factor
223 | DER-AVM Parameters (Control) | 0x0FA4 | 4004 | Set the active | U16 | FC03 | 1 | % |  | RO | power
224 | DER-AVM Parameters (Control) | 0x0FA5 | 4005 | Set the reactive | S16 | FC03 | 1 | 1KVar | 1 | RO | power
225 | DER-AVM Parameters (Control) | 0x0FA6 | 4006 | Set the reactive | U16 | FC03 | 1 |  |  | RO | control mode
226 | DER-AVM Parameters (Control) | 0x0FA7 | 4007 | Overfrequency | U16 | FC03/FC06 | 1 |  |  | RW | derating ¦ 0: enabled ¦ 1: disabled
227 | DER-AVM Parameters (Control) | 0x0FA8 | 4008 | Overfrequency | U16 | FC03 | 1 | 0.01Hz | 0.01 | RO
228 | DER-AVM Parameters (Control) | 0x0FA9 | 4009 | Set the derating | U16 | FC03/FC06 | 1 | Hz |  | RW | rate ¦ %/0.1 ¦ 0-20 ,the default is 4
229 | DER-AVM Parameters (Control) | 0x0FAA | 4010 | Set the active | U16 | FC03 | 1 |  |  | RO | power ¦ KW
230 | DER-AVM Parameters (Control) | 0x0FAB | 4011 | LOGO Settings | U16 | FC03 | 1 |  |  | RO
231 | DER-AVM Parameters (Control) | 0x0FAC | 4012 | Input | U16 | FC03 | 1 |  |  | RO | Mode ¦ Settings
232 | DER-AVM Parameters (Control) | 0x0FAD | 4013 | Grid | U16 | FC03 | 1 |  |  | RO | Connection ¦ Standard ¦ Settings
233 | DER-AVM Parameters (Control) | 0x0FAE | 4014 | Start | U16 | FC03 | 1 |  |  | RO | Voltage ¦ Settings ¦ (1-1.5K:1000-4500 ¦ 2K-5K:1500-4500 ¦ 10K-150K:2500-9000 ¦ 175K-250K:6500-1450
234 | DER-AVM Parameters (Control) | 0x0FAF | 4015 | Start | U16 | FC03/FC06 | 1 |  |  | RW | Delay ¦ Settings ¦ 20-300
235 | DER-AVM Parameters (Control) | 0x0FB0 | 4016 | Grid | U16 | FC03 | 1 |  |  | RO | Voltage ¦ Lower ¦ Limit ¦ Settings
236 | DER-AVM Parameters (Control) | 0x0FB1 | 4017 | Grid | U16 | FC03/FC06 | 1 |  |  | RW | Voltage ¦ Upper ¦ Limit ¦ Settings
237 | DER-AVM Parameters (Control) | 0x0FB2 | 4018 | Grid Frequency | U16 | FC03/FC06 | 1 |  |  | RW | Lower ¦ Limit ¦ Settings
238 | DER-AVM Parameters (Control) | 0x0FB3 | 4019 | Grid | U16 | FC03/FC06 | 1 |  |  | RW | Frequency ¦ Upper ¦ Limit ¦ Settings
239 | DER-AVM Parameters (Control) | 0x0FB4 | 4020 | Back | U16 | FC03/FC06 | 1 | W |  | RW | Current ¦ Power ¦ Limit ¦ Settings
240 | DER-AVM Parameters (Control) | 0x0FB5 | 4021 | Overvoltage | U16 | FC03/FC06 | 1 | 0.1% | 0.1 | RW | Derating ¦ Threshold ¦ Value
241 | DER-AVM Parameters (Control) | 0x0FB6 | 4022 | Reserve | U16 | FC03/FC06 | 1 |  |  | RW
242 | DER-AVM Parameters (Control) | 0x0FB7 | 4023 | 485 | U16 | FC03/FC06 | 1 |  |  | RW | Settings(U2) ¦ 1-64
243 | DER-AVM Parameters (Control) | 0x0FB8 | 4024 | 485 Baud Rate | U16 | FC03 | 1 |  |  | RO | Settings(U2)
244 | DER-AVM Parameters (Control) | 0x0FB9 | 4025 | 485 Protocol | U16 | FC03 | 1 |  |  | RO | Settings
245 | DER-AVM Parameters (Control) | 0x0FBA | 4026 | 485 | U16 | FC03/FC06 | 1 |  |  | RW | Settings(U4) ¦ 1-64
246 | DER-AVM Parameters (Control) | 0x0FBB | 4027 | 485 Baud Rate | U16 | FC03 | 1 |  |  | RO | Settings (U4)
247 | DER-AVM Parameters (Control) | 0x0FBC | 4028 | Three-phase | U16 | FC03 | 1 |  |  | RO | Settings
248 | DER-AVM Parameters (Control) | 0x0FBD | 4029 | Remote | U16 | FC03/FC06 | 1 |  |  | RW | Control ¦ Settings ¦ 0:Disable ¦ 1:Enable
249 | DER-AVM Parameters (Control) | 0x0FBE | 4030 | String | U16 | FC03/FC06 | 1 | A |  | RW | Test ¦ Threshold ¦ Value Settings ¦ 5-25
250 | DER-AVM Parameters (Control) | 0x0FBF | 4031 | Self-check | U16 | FC03 | 1 |  |  | RO | (Enable)
251 | DER-AVM Parameters (Control) | 0x0FC0 | 4032 | Self-check | U16 | FC03 | 1 |  |  | RO | (Disable)
252 | DER-AVM Parameters (Control) | 0x0FC1 | 4033 | Clear | U16 | FC03/FC06 | 1 |  |  | RW | Fault ¦ Record ¦ DATA arbitrary number
253 | DER-AVM Parameters (Control) | 0x0FC2 | 4034 | Factory | U16 | FC03/FC06 | 1 |  |  | RW | Data ¦ Reset ¦ DATA arbitrary number
254 | DER-AVM Parameters (Control) | 0x0FC3 | 4035 | Start I/V Scan | U16 | FC03/FC06 | 1 |  |  | RW | DATA arbitrary number
255 | DER-AVM Parameters (Control) | 0x0FC4 | 4036 | Active | S16 | FC03 | 1 |  |  | RO | Power ¦ Increment ¦ (KW) ¦ KW ¦ The ¦ machine
256 | DER-AVM Parameters (Control) | 0x0FC5 | 4037 | Active | S16 | FC03/FC06 | 1 | W |  | RW | Power ¦ The ¦ machine ¦ comes
257 | DER-AVM Parameters (Control) | 0x0FC6 | 4038 | Soft | S16 | FC03/FC06 | 1 | %/min |  | RW | Start ¦ Active ¦ Power ¦ Change Rate
258 | DER-AVM Parameters (Control) | 0x0FC7 | 4039 | Active Power | U16 | FC03/FC06 | 1 | 0.1% | 0.1 | RW | Settings ¦ (Decimals) ¦ 0-9
259 | DER-AVM Parameters (Control) | 0x0FC8 | 4040 | R-phase | U16 | FC03/FC06 | 1 |  |  | RW | Voltage ¦ Calibration ¦ Factor ¦ Default :4096
260 | DER-AVM Parameters (Control) | 0x0FC9 | 4041 | S-phase | U16 | FC03/FC06 | 1 |  |  | RW | Voltage ¦ Calibration ¦ Factor
261 | DER-AVM Parameters (Control) | 0x0FCA | 4042 | T-phase | U16 | FC03/FC06 | 1 |  |  | RW | Voltage ¦ Calibration ¦ Factor
262 | DER-AVM Parameters (Control) | 0x0FCB | 4043 | R-phase | U16 | FC03/FC06 | 1 |  |  | RW | Current ¦ Calibration ¦ Factor
263 | DER-AVM Parameters (Control) | 0x0FCC | 4044 | S-phase | U16 | FC03/FC06 | 1 |  |  | RW | Calibration ¦ Factor
264 | DER-AVM Parameters (Control) | 0x0FCD | 4045 | T-phase | U16 | FC03/FC06 | 1 |  |  | RW | Current ¦ Calibration ¦ Factor
265 | DER-AVM Parameters (Control) | 0x0FCE | 4046 | Battery Voltage | U16 | FC03/FC06 | 1 |  |  | RW | Calibration ¦ Factor
266 | DER-AVM Parameters (Control) | 0x112F | 4399 | Record | U16 | FC03 | 1 |  |  | RO | 798

## Status_Definitions
Code | Name | Description | Bit_Definition
0 | INITIAL | Initial mode
1 | STANDBY | Standby mode
3 | ON_GRID | On-Grid mode
4 | OFF_GRID | Off-Grid mode
5 | FAULT | Fault mode
9 | SHUTDOWN | Shutdown mode
NOTE: Add/edit status codes. Descriptions used in Stage 2 InverterMode mapping.

## Error_Fault_Codes
Register | Bit | Error_No | Description | Notes
(No error codes detected from PDF)

## Grid_Codes
Code_Hex | Description
(No regulation codes detected from PDF)
NOTE: Register 0x5101 - Grid regulation/country code setting

## Fuse_Open_Data
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x1034~0x1035 — PV string fuse open status bits

## Status_Bits_03FC
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x03FC~03FD — DEA-AVM inverter action/run-state bits

## Fuse_Check_Mask
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: Registers 0x513D~0x513E — PV string fuse check enable/disable mask

## REMS_Error_Bits
Bit | Description | Value_Definition
(Not detected from PDF)
NOTE: REMS Error Code register — bit-field inverter alarm flags

## REMS_Registers
No | Description | Length_Bytes | Unit
(Not detected from PDF)
NOTE: REMS protocol register layout (function code 0x7E)