## Register_Mapping
No | Section | Source_Addr_Hex | Source_Addr_Dec | Source_Name | Source_Type | Source_Unit | Source_Scale | Source_RW | Source_Regs | → | Solarize_Name | Solarize_Addr_Hex | Match_Type | Notes
--- Inverter Realtime Data ---
1 | Inverter Realtime Data | 0x0B94 | 2964 | PV12 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV2_VOLTAGE |  | Ref(76%)
2 | Inverter Realtime Data | 0x0B95 | 2965 | PV12 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV2_CURRENT |  | Ref(76%)
3 | Inverter Realtime Data | 0x0B96 | 2966 | PV12 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(81%)
4 | Inverter Realtime Data | 0x0B98 | 2968 | PV11 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV1_VOLTAGE |  | Ref(76%)
5 | Inverter Realtime Data | 0x0B99 | 2969 | PV11 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV1_CURRENT |  | Ref(76%)
6 | Inverter Realtime Data | 0x0B9A | 2970 | PV11 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(81%)
7 | Inverter Realtime Data | 0x0B9C | 2972 | PV10 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV1_VOLTAGE |  | Ref(76%)
8 | Inverter Realtime Data | 0x0B9D | 2973 | PV10 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV1_CURRENT |  | Ref(76%)
9 | Inverter Realtime Data | 0x0B9E | 2974 | PV10 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(81%)
10 | Inverter Realtime Data | 0x0BA0 | 2976 | PV9 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV_VOLTAGE |  | Ref(74%)
11 | Inverter Realtime Data | 0x0BA1 | 2977 | PV9 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV_CURRENT |  | Ref(74%)
12 | Inverter Realtime Data | 0x0BA2 | 2978 | PV9 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
13 | Inverter Realtime Data | 0x0BA4 | 2980 | PV8 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV8_VOLTAGE |  | Ref(79%)
14 | Inverter Realtime Data | 0x0BA5 | 2981 | PV8 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV8_CURRENT |  | Ref(79%)
15 | Inverter Realtime Data | 0x0BA6 | 2982 | PV8 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
16 | Inverter Realtime Data | 0x0BA8 | 2984 | PV7 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV7_VOLTAGE |  | Ref(79%)
17 | Inverter Realtime Data | 0x0BA9 | 2985 | PV7 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV7_CURRENT |  | Ref(79%)
18 | Inverter Realtime Data | 0x0BAA | 2986 | PV7 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
19 | Inverter Realtime Data | 0x0BAC | 2988 | PV6 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV6_VOLTAGE |  | Ref(79%)
20 | Inverter Realtime Data | 0x0BAD | 2989 | PV6 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV6_CURRENT |  | Ref(79%)
21 | Inverter Realtime Data | 0x0BAE | 2990 | PV6 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
22 | Inverter Realtime Data | 0x0BB0 | 2992 | PV5 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV5_VOLTAGE |  | Ref(79%)
23 | Inverter Realtime Data | 0x0BB1 | 2993 | PV5 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV5_CURRENT |  | Ref(79%)
24 | Inverter Realtime Data | 0x0BB2 | 2994 | PV5 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
25 | Inverter Realtime Data | 0x0BB4 | 2996 | PV4 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV4_VOLTAGE |  | Ref(79%)
26 | Inverter Realtime Data | 0x0BB5 | 2997 | PV4 input current | S16 | 0.01A | 0.01 | RO | 1 | → | PV4_CURRENT |  | Ref(79%)
27 | Inverter Realtime Data | 0x0BB6 | 2998 | PV4 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
28 | Inverter Realtime Data | 0x0BB8 | 3000 | PV1 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV1_VOLTAGE |  | Ref(79%)
29 | Inverter Realtime Data | 0x0BB9 | 3001 | PV2 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV2_VOLTAGE |  | Ref(79%)
30 | Inverter Realtime Data | 0x0BBA | 3002 | PV3 input voltage | U16 | 0.1V | 0.1 | RO | 1 | → | PV3_VOLTAGE |  | Ref(79%)
31 | Inverter Realtime Data | 0x0BBB | 3003 | PV1 input current | U16 | 0.01A | 0.01 | RO | 1 | → | PV1_CURRENT |  | Ref(79%)
32 | Inverter Realtime Data | 0x0BBC | 3004 | PV2 input current | U16 | 0.01A | 0.01 | RO | 1 | → | PV2_CURRENT |  | Ref(79%)
33 | Inverter Realtime Data | 0x0BBD | 3005 | PV3 input current | U16 | 0.01A | 0.01 | RO | 1 | → | PV3_CURRENT |  | Ref(79%)
34 | Inverter Realtime Data | 0x0BBE | 3006 | PV1 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
35 | Inverter Realtime Data | 0x0BC0 | 3008 | PV2 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
36 | Inverter Realtime Data | 0x0BC2 | 3010 | PV3 input power | S32 | 1W | 1 | RO | 2 | → | INPUT_POWER |  | Ref(85%)
37 | Inverter Realtime Data | 0x0BC4 | 3012 | PBUS voltage | U16 | 0.1V | 0.1 | RO | 1 | → | BUS_VOLTAGE |  | Ref(96%)
38 | Inverter Realtime Data | 0x0BC5 | 3013 | NBUS voltage | U16 | 0.1V | 0.1 | RO | 1 | → | BUS_VOLTAGE |  | Ref(96%)
39 | Inverter Realtime Data | 0x0BC6 | 3014 | RS-phase grid voltage | U16 | 0.1V | 0.1 | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(83%)
40 | Inverter Realtime Data | 0x0BC7 | 3015 | ST-phase grid voltage | U16 | 0.1V | 0.1 | RO | 1 | → | T_PHASE_VOLTAGE |  | Ref(83%)
41 | Inverter Realtime Data | 0x0BC8 | 3016 | TR-phase grid voltage | U16 | 0.1V | 0.1 | RO | 1 | → | T_PHASE_VOLTAGE |  | Ref(83%)
42 | Inverter Realtime Data | 0x0BC9 | 3017 | RS-phase grid frequency | U16 | 0.01Hz | 0.01 | RO | 1 | → | GRID_FREQUENCY |  | Ref(76%)
43 | Inverter Realtime Data | 0x0BCA | 3018 | ST-phase grid frequency | U16 | 0.01Hz | 0.01 | RO | 1 | → | GRID_FREQUENCY |  | Ref(76%)
44 | Inverter Realtime Data | 0x0BCB | 3019 | TR-phase grid frequency | U16 | 0.01Hz | 0.01 | RO | 1 | → | GRID_FREQUENCY |  | Ref(76%)
45 | Inverter Realtime Data | 0x0BCC | 3020 | R-phase grid-tied current | U16 | 0.01A | 0.01 | RO | 1 | → | R_PHASE_CURRENT |  | Ref(75%)
46 | Inverter Realtime Data | 0x0BCD | 3021 | S-phase grid-tied current | U16 | 0.01A | 0.01 | RO | 1 | → | S_PHASE_CURRENT |  | Ref(75%)
47 | Inverter Realtime Data | 0x0BCE | 3022 | T-phase grid-tied current | U16 | 0.01A | 0.01 | RO | 1 | → | T_PHASE_CURRENT |  | Ref(75%)
48 | Inverter Realtime Data | 0x0BCF | 3023 | Grid-tied power | S32 | 1W | 1 | RO | 2 | → | GRID_T_POWER |  | Ref(89%)
49 | Inverter Realtime Data | 0x0BD1 | 3025 | Radiator temperature | S16 | 0. 1℃ |  | RO | 1 | → | RADIATOR_TEMP |  | Ref(79%)
50 | Inverter Realtime Data | 0x0BD2 | 3026 | Module temperature | S16 | 0. 1℃ |  | RO | 1 | → |  |  | Unmapped
51 | Inverter Realtime Data | 0x0BD3 | 3027 | DSP alarm code | U16 |  |  | RO | 1 | → | DSP_ALARM_CODE_H |  | Ref(93%)
52 | Inverter Realtime Data | 0x0BD4 | 3028 | DSP error code | U32 |  |  | RO | 2 | → | DSP_ERROR_CODE_H |  | Ref(93%)
53 | Inverter Realtime Data | 0x0BD6 | 3030 | Operating | U8 |  |  | RO | 1 | → | OPERATION_MODE |  | Ref(70%)
54 | Inverter Realtime Data | 0x0BD7 | 3031 | Rotational speed of fan A | U16 | r/min |  | RO | 1 | → |  |  | Unmapped
55 | Inverter Realtime Data | 0x0BD8 | 3032 | Rotational speed of fan B | U16 | r/min |  | RO | 1 | → |  |  | Unmapped
56 | Inverter Realtime Data | 0x0BD9 | 3033 | Rotational speed of fan C | U16 | r/min |  | RO | 1 | → |  |  | Unmapped
57 | Inverter Realtime Data | 0x0BDA | 3034 | Reserve. | U32 |  |  | RO | 2 | → |  |  | Unmapped
58 | Inverter Realtime Data | 0x0BDC | 3036 | ARM alarm code | U8 |  |  | RO | 1 | → | DSP_ALARM_CODE_H |  | Ref(73%)
59 | Inverter Realtime Data | 0x0BDD | 3037 | Input mode | U8 |  |  | RO | 1 | → | INPUT_POWER |  | Ref(76%)
60 | Inverter Realtime Data | 0x0BDE | 3038 | Total energy yield | U32 | 0.1Kwh | 0.1 | RO | 2 | → | TOTAL_ENERGY_L |  | Ref(88%)
61 | Inverter Realtime Data | 0x0BE0 | 3040 | Annual energy yield | U32 | Kwh |  | RO | 2 | → | TOTAL_ENERGY_L |  | Ref(67%)
62 | Inverter Realtime Data | 0x0BE2 | 3042 | Daily energy yield | U16 | Kwh |  | RO | 1 | → | DAILY_ENERGY_FEEDIN |  | Ref(76%)
63 | Inverter Realtime Data | 0x0BE3 | 3043 | Power-on voltage | U16 | 0.1V | 0.1 | RO | 1 | → | R_VOLTAGE |  | Ref(72%)
64 | Inverter Realtime Data | 0x0BE4 | 3044 | Power-on delay | U16 | S |  | RO | 1 | → | POWER_FACTOR_SET |  | Ref(60%)
65 | Inverter Realtime Data | 0x0BE5 | 3045 | Lower | U16 | 0.1V | 0.1 | RO | 1 | → | AC_POWER |  | Ref(62%)
66 | Inverter Realtime Data | 0x0BE6 | 3046 | Upper | U16 | 0.1V | 0.1 | RO | 1 | → | PV_POWER |  | Ref(62%)
67 | Inverter Realtime Data | 0x0BE7 | 3047 | Lower | U16 | 0.01Hz | 0.01 | RO | 1 | → | AC_POWER |  | Ref(62%)
68 | Inverter Realtime Data | 0x0BE8 | 3048 | Upper | U16 |  |  | RO | 1 | → | PV_POWER |  | Ref(62%)
69 | Inverter Realtime Data | 0x0BE9 | 3049 | Preset power factor | U16 |  |  | RO | 1 | → | POWER_FACTOR |  | Ref(77%)
70 | Inverter Realtime Data | 0x0BEA | 3050 | Preset active power | U16 | % |  | RO | 1 | → | REACTIVE_POWER |  | Ref(85%)
71 | Inverter Realtime Data | 0x0BEB | 3051 | Preset reactive power | S8 | 1KVar | 1 | RO | 1 | → | REACTIVE_POWER |  | Ref(80%)
72 | Inverter Realtime Data | 0x0BEC | 3052 | Apparent power | S32 | 1VA | 1 | RO | 2 | → | REACTIVE_POWER |  | Ref(64%)
73 | Inverter Realtime Data | 0x0BEE | 3054 | Reactive power | S32 | 1Var | 1 | RO | 2 | → | REACTIVE_POWER |  | Ref(100%)
74 | Inverter Realtime Data | 0x0BF0 | 3056 | Power factor | U16 |  |  | RO | 1 | → | POWER_FACTOR |  | Ref(100%)
75 | Inverter Realtime Data | 0x0BF1 | 3057 | DC insulation resistance | U16 | Kohm |  | RO | 1 | → | CLEAR_PV_INSULATION_WARNING |  | Ref(63%)
76 | Inverter Realtime Data | 0x0BF2 | 3058 | Overfrequency derating | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(65%)
77 | Inverter Realtime Data | 0x0BF3 | 3059 | Overfrequency | U16 |  |  | RO | 1 | → | R_FREQUENCY |  | Ref(83%)
78 | Inverter Realtime Data | 0x0BF4 | 3060 | Derating rate | U16 | 0.01Hz | 0.01 | RO | 1 | → | POWER_DERATING_PCT |  | Ref(65%)
79 | Inverter Realtime Data | 0x0BF5 | 3061 | Reserved | U16 |  |  | RO | 1 | → |  |  | Unmapped
80 | Inverter Realtime Data | 0x0BF6 | 3062 | Reserved | U16 |  |  | RO | 1 | → |  |  | Unmapped
81 | Inverter Realtime Data | 0x0BF7 | 3063 | Reserved | U16 |  |  | RO | 1 | → |  |  | Unmapped
82 | Inverter Realtime Data | 0x0BF8 | 3064 | PV1 String current 1 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
83 | Inverter Realtime Data | 0x0BF9 | 3065 | PV1 String current 2 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
84 | Inverter Realtime Data | 0x0BFA | 3066 | PV1 String current 3 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
85 | Inverter Realtime Data | 0x0BFB | 3067 | PV1 String current 4 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
86 | Inverter Realtime Data | 0x0BFC | 3068 | PV2 String current 1 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
87 | Inverter Realtime Data | 0x0BFD | 3069 | PV2 String current 2 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
88 | Inverter Realtime Data | 0x0BFE | 3070 | PV2 String current 3 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
89 | Inverter Realtime Data | 0x0BFF | 3071 | PV2 String current 4 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
90 | Inverter Realtime Data | 0x0C00 | 3072 | PV3 String current 1 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
91 | Inverter Realtime Data | 0x0C01 | 3073 | PV3 String current 2 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
92 | Inverter Realtime Data | 0x0C02 | 3074 | PV3 String current 3 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
93 | Inverter Realtime Data | 0x0C03 | 3075 | PV3 String current 4 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
94 | Inverter Realtime Data | 0x0C04 | 3076 | PV4 String current 1 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
95 | Inverter Realtime Data | 0x0C05 | 3077 | PV4 String current 2 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
96 | Inverter Realtime Data | 0x0C06 | 3078 | PV4 String current 3 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
97 | Inverter Realtime Data | 0x0C07 | 3079 | PV4 String current 4 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
98 | Inverter Realtime Data | 0x0C08 | 3080 | PV5 String current 1 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
99 | Inverter Realtime Data | 0x0C09 | 3081 | PV5 String current 2 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
100 | Inverter Realtime Data | 0x0C0A | 3082 | PV5 String current 3 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
101 | Inverter Realtime Data | 0x0C0B | 3083 | PV5 String current 4 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
102 | Inverter Realtime Data | 0x0C0C | 3084 | PV6 String current 1 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
103 | Inverter Realtime Data | 0x0C0D | 3085 | PV6 String current 2 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
104 | Inverter Realtime Data | 0x0C0E | 3086 | PV6 String current 3 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
105 | Inverter Realtime Data | 0x0C0F | 3087 | PV6 String current 4 | S16 | 0.01A | 0.01 | RO | 1 | → | STRING3_CURRENT |  | Ref(80%)
106 | Inverter Realtime Data | 0x0C10 | 3088 | Reserve | U16 |  |  | RO | 1 | → |  |  | Unmapped
107 | Inverter Realtime Data | 0x0C11 | 3089 | Reserve | U16 |  |  | RO | 1 | → |  |  | Unmapped
108 | Inverter Realtime Data | 0x0C12 | 3090 | Running Time | U32 | Hour |  | RO | 2 | → | RUNNING_STATUS |  | Ref(69%)
109 | Inverter Realtime Data | 0x0C14 | 3092 | Generating Time | U32 | Hour |  | RO | 2 | → | TOTAL_GENERATION_TIME_LOW |  | Ref(70%)
110 | Inverter Realtime Data | 0x0C16 | 3094 | Number | U32 |  |  | RO | 2 | → | SERIAL_NUMBER |  | Ref(63%)
111 | Inverter Realtime Data | 0x0C18 | 3096 | Power Peak After Starting | U32 | W |  | RO | 2 | → | POWER_DERATING_PCT |  | Ref(60%)
112 | Inverter Realtime Data | 0x0C1A | 3098 | Day Generation | U32 | W |  | RO | 2 | → | TOTAL_GENERATION_TIME_LOW |  | Ref(62%)
113 | Inverter Realtime Data | 0x0C1C | 3100 | Week Generation | U32 | Kwh |  | RO | 2 | → | TOTAL_GENERATION_TIME_LOW |  | Ref(55%)
114 | Inverter Realtime Data | 0x0C1E | 3102 | Month Generation | U32 | Kwh |  | RO | 2 | → | TOTAL_GENERATION_TIME_LOW |  | Ref(63%)
115 | Inverter Realtime Data | 0x0C20 | 3104 | Last N days Generation | U32 | Kwh |  | RO | 2 | → |  |  | Unmapped
116 | Inverter Realtime Data | 0x0C22 | 3106 | Value of N | U16 |  |  | RO | 1 | → |  |  | Unmapped
117 | Inverter Realtime Data | 0x0C23 | 3107 | Year | U16 |  |  | RO | 1 | → |  |  | Unmapped
118 | Inverter Realtime Data | 0x0C24 | 3108 | Month | U16 |  |  | RO | 1 | → |  |  | Unmapped
119 | Inverter Realtime Data | 0x0C25 | 3109 | Date | U16 |  |  | RO | 1 | → |  |  | Unmapped
120 | Inverter Realtime Data | 0x0C26 | 3110 |  | U16 | Hour |  | RO | 1 | → |  |  | Unmapped
121 | Inverter Realtime Data | 0x0C27 | 3111 | Minute | U16 |  |  | RO | 1 | → | INPUT_POWER |  | Ref(59%)
122 | Inverter Realtime Data | 0x0C28 | 3112 | Second | U16 |  |  | RO | 1 | → |  |  | Unmapped
123 | Inverter Realtime Data | 0x0C29 | 3113 | Week | U16 |  |  | RO | 1 | → |  |  | Unmapped
124 | Inverter Realtime Data | 0x0C2A | 3114 | Back-current Power Limit | U16 | W |  | RO | 1 | → | AC_POWER_L |  | Ref(59%)
125 | Inverter Realtime Data | 0x0C2B | 3115 | Active Power of Soft Start | U16 | %/min |  | RO | 1 | → | REACTIVE_POWER_SET |  | Ref(68%)
126 | Inverter Realtime Data | 0x0C2C | 3116 | Reserve | U16 |  |  | RO | 1 | → |  |  | Unmapped
127 | Inverter Realtime Data | 0x0C2D | 3117 | 485Address(2) | U16 |  |  | RO | 1 | → |  |  | Unmapped
128 | Inverter Realtime Data | 0x0C2E | 3118 | 485 Baud Rate (2) | U16 |  |  | RO | 1 | → |  |  | Unmapped
129 | Inverter Realtime Data | 0x0C2F | 3119 | 485 Agreement | U16 |  |  | RO | 1 | → |  |  | Unmapped
130 | Inverter Realtime Data | 0x0C30 | 3120 | 485 Address(1) | U16 |  |  | RO | 1 | → |  |  | Unmapped
131 | Inverter Realtime Data | 0x0C31 | 3121 | 485Baud Rate(1) | U16 |  |  | RO | 1 | → |  |  | Unmapped
132 | Inverter Realtime Data | 0x0C32 | 3122 | Three-phase System | U16 |  |  | RO | 1 | → | T_PHASE_VOLTAGE |  | Ref(61%)
133 | Inverter Realtime Data | 0x0C33 | 3123 | Remote Control Enable | U16 |  |  | RO | 1 | → | INVERTER_CONTROL |  | Ref(59%)
134 | Inverter Realtime Data | 0x0C34 | 3124 | String Test Threshold | U16 | A |  | RO | 1 | → |  |  | Unmapped
135 | Inverter Realtime Data | 0x0C35 | 3125 | Setting | U16 |  |  | RO | 1 | → |  |  | Unmapped
136 | Inverter Realtime Data | 0x0C36 | 3126 | I/V Scan-status | U16 |  |  | RO | 1 | → | IV_SCAN_STATUS |  | Ref(97%)
137 | Inverter Realtime Data | 0x0C37 | 3127 | QV Curve | U16 |  |  | RO | 6 | → | IV_CURVE_SCAN |  | Ref(67%)
138 | Inverter Realtime Data | 0x0C3D | 3133 | R-phase | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(67%)
139 | Inverter Realtime Data | 0x0C3E | 3134 | S-phase | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(67%)
140 | Inverter Realtime Data | 0x0C3F | 3135 | T-phase | U16 |  |  | RO | 1 | → | T_PHASE_VOLTAGE |  | Ref(67%)
141 | Inverter Realtime Data | 0x0C40 | 3136 | R-phase | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(67%)
142 | Inverter Realtime Data | 0x0C41 | 3137 | S-phase Calibration Factor | U16 |  |  | RO | 1 | → |  |  | Unmapped
143 | Inverter Realtime Data | 0x0C42 | 3138 | T-phase | U16 |  |  | RO | 1 | → | T_PHASE_VOLTAGE |  | Ref(67%)
144 | Inverter Realtime Data | 0x0C43 | 3139 | Battery | U16 |  |  | RO | 1 | → |  |  | Unmapped
145 | Inverter Realtime Data | 0x0C44 | 3140 | Bluetooth enable | U16 |  |  | RO | 1 | → |  |  | Unmapped
146 | Inverter Realtime Data | 0x0C45 | 3141 | Reserved | U16 |  |  | RO | 4 | → |  |  | Unmapped
147 | Inverter Realtime Data | 0x0C4A | 3146 | Underfrequency | U16 | % |  | RO | 1 | → | R_FREQUENCY |  | Ref(80%)
148 | Inverter Realtime Data | 0x0C4B | 3147 | FrozenUpFreqEnb | U16 |  |  | RO | 1 | → | R_FREQUENCY |  | Ref(55%)
149 | Inverter Realtime Data | 0x0C4C | 3148 | FrozenUpFreq | U16 | 0.01Hz | 0.01 | RO | 1 | → |  |  | Unmapped
150 | Inverter Realtime Data | 0x0C4D | 3149 | Slow increase in power | U16 |  |  | RO | 1 | → | REACTIVE_POWER |  | Ref(56%)
151 | Inverter Realtime Data | 0x0C4E | 3150 | Overfrequency | U16 |  |  | RO | 1 | → | R_FREQUENCY |  | Ref(83%)
152 | Inverter Realtime Data | 0x0C4F | 3151 | FrozenUpVoltStart | U16 | 0.1V | 0.1 | RO | 1 | → |  |  | Unmapped
153 | Inverter Realtime Data | 0x0C50 | 3152 | FrozenUpVoltEnd | U16 | 0.1V | 0.1 | RO | 1 | → |  |  | Unmapped
154 | Inverter Realtime Data | 0x0C51 | 3153 | NPEVoltSet | U16 |  |  | RO | 1 | → | PV_VOLTAGE |  | Ref(57%)
155 | Inverter Realtime Data | 0x0C7A | 3194 | PLC area code | U16 |  |  | RO | 1 | → | DSP_ALARM_CODE_H |  | Ref(62%)
156 | Inverter Realtime Data | 0x0C7B | 3195 | Bluetooth name format | U16 |  |  | RO | 1 | → |  |  | Unmapped
157 | Inverter Realtime Data | 0x0C7C | 3196 | Setting value of rated | U16 |  |  | RO | 1 | → |  |  | Unmapped
158 | Inverter Realtime Data | 0x0C7D | 3197 | Upper | U16 | 0.01A | 0.01 | RO | 1 | → | PV_POWER |  | Ref(62%)
159 | Inverter Realtime Data | 0x0C7E | 3198 | Lower | U16 | 0.01A | 0.01 | RO | 1 | → | AC_POWER |  | Ref(62%)
160 | Inverter Realtime Data | 0x0C7F | 3199 | Fuse detection enable | U32 |  |  | RO | 2 | → |  |  | Unmapped
161 | Inverter Realtime Data | 0x0C81 | 3201 | Fuse alarm information | U32 |  |  | RO | 2 | → |  |  | Unmapped
162 | Inverter Realtime Data | 0x0C83 | 3203 | Anti | U16 |  |  | RO | 1 | → |  |  | Unmapped
163 | Inverter Realtime Data | 0x0C84 | 3204 | Correction | U16 |  |  | RO | 1 | → |  |  | Unmapped
164 | Inverter Realtime Data | 0x0C85 | 3205 | CT ratio | U16 |  |  | RO | 1 | → |  |  | Unmapped
165 | Inverter Realtime Data | 0x0C8E | 3214 | PV1 | U16 |  |  | RO | 1 | → |  |  | Unmapped
166 | Inverter Realtime Data | 0x0C8F | 3215 | PV2 | U16 |  |  | RO | 1 | → |  |  | Unmapped
167 | Inverter Realtime Data | 0x0C9A | 3226 | Power change rate | U16 |  |  | RO | 1 | → | POWER_DERATING_PCT |  | Ref(57%)
168 | Inverter Realtime Data | 0x0C9B | 3227 | Over | U16 |  |  | RO | 1 | → |  |  | Unmapped
169 | Inverter Realtime Data | 0x0C9C | 3228 | Soft start time | U16 | s |  | RO | 1 | → |  |  | Unmapped
170 | Inverter Realtime Data | 0x0C9D | 3229 | Low | U16 |  |  | RO | 1 | → |  |  | Unmapped
171 | Inverter Realtime Data | 0x0C9E | 3230 | High | U16 |  |  | RO | 1 | → |  |  | Unmapped
172 | Inverter Realtime Data | 0x0C9F | 3231 | Upper | U16 | 0.01Hz | 0.01 | RO | 1 | → | PV_POWER |  | Ref(62%)
173 | Inverter Realtime Data | 0x0CA0 | 3232 | Lower | U16 | 0.01Hz | 0.01 | RO | 1 | → | AC_POWER |  | Ref(62%)
174 | Inverter Realtime Data | 0x0CA1 | 3233 | Over | U16 |  |  | RO | 1 | → |  |  | Unmapped
175 | Inverter Realtime Data | 0x0CA2 | 3234 | Underfrequency | U16 |  |  | RO | 1 | → | R_FREQUENCY |  | Ref(80%)
176 | Inverter Realtime Data | 0x0CA3 | 3235 | Maximum Derating | U16 | % |  | RO | 1 | → |  |  | Unmapped
177 | Inverter Realtime Data | 0x0CA4 | 3236 | Maximum increase | U16 | % |  | RO | 1 | → |  |  | Unmapped
178 | Inverter Realtime Data | 0x0CA5 | 3237 | Debugging | S16 |  |  | RO | 1 | → |  |  | Unmapped
179 | Inverter Realtime Data | 0x0CA6 | 3238 | Debugging | S16 |  |  | RO | 1 | → |  |  | Unmapped
180 | Inverter Realtime Data | 0x0CA7 | 3239 | Debugging | S16 |  |  | RO | 1 | → |  |  | Unmapped
181 | Inverter Realtime Data | 0x0CA8 | 3240 | Debugging | S16 |  |  | RO | 2 | → |  |  | Unmapped
182 | Inverter Realtime Data | 0x0CA9 | 3241 | Daily power generation | U16 | 0.1Kwh | 0.1 | RO | 1 | → | DAILY_PRODUCTION |  | Ref(63%)
183 | Inverter Realtime Data | 0x0CAA | 3242 | Accumulated | U32 | Kwh |  | RO | 2 | → | ACCUMULATED_ENERGY |  | Ref(76%)
184 | Inverter Realtime Data | 0x0CAC | 3244 | Frequency | U16 |  |  | RO | 1 | → | FREQUENCY |  | Ref(100%)
185 | Inverter Realtime Data | 0x0CAD | 3245 | Active reactive curve | U16 |  |  | RO | 1 | → | REACTIVE_POWER |  | Ref(57%)
186 | Inverter Realtime Data | 0x0CAE | 3246 | Grid protected mode | U16 |  |  | RO | 1 | → | GRID_TOTAL_REACTIVE_POWER_LOW |  | Ref(58%)
187 | Inverter Realtime Data | 0x0CAF | 3247 | Grid type | U16 |  |  | RO | 1 | → | GRID_T_POWER |  | Ref(76%)
188 | Inverter Realtime Data | 0x0CB0 | 3248 | Fault recovery time | U16 |  |  | RO | 1 | → | FAULT_CODE_2 |  | Ref(65%)
189 | Inverter Realtime Data | 0x0CB1 | 3249 | Night SVG function | U16 |  |  | RO | 1 | → |  |  | Unmapped
190 | Inverter Realtime Data | 0x0CB2 | 3250 | IV | U16 |  |  | RO | 1 | → |  |  | Unmapped
191 | Inverter Realtime Data | 0x0CB3 | 3251 | R-phase | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(67%)
192 | Inverter Realtime Data | 0x1388 | 5000 | PV1 Voltage Point 1 | U16 | 0.1V | 0.1 | RO | 1 | → | PV1_VOLTAGE |  | Ref(73%)
193 | Inverter Realtime Data | 0x1388 | 5000 | Hight | U16 | 60Hz | 60 | RO | 251 | → |  |  | Unmapped
194 | Inverter Realtime Data | 0x12C0 | 4800 |  | U16 |  |  | RO | 1 | → |  |  | Unmapped
--- Device Information (System Info) ---
195 | Device Information (System Info) | 0x0C80 | 3200 | Machine model | U8 |  |  | RO | 5 | → | ACTION_MODE |  | Ref(75%)
196 | Device Information (System Info) | 0x0C85 | 3205 | DSP version | U8 |  |  | RO | 1 | → | DSP_VERSION |  | Ref(100%)
197 | Device Information (System Info) | 0x0C86 | 3206 | Inverter SN | U8 |  |  | RO | 11 | → | INVERTER_ON_OFF |  | Ref(77%)
198 | Device Information (System Info) | 0x0C91 | 3217 | PLC MAC Address | U8 |  |  | RO | 3 | → |  |  | Unmapped
199 | Device Information (System Info) | 0x0C94 | 3220 | LCD Model Setting | U8 |  |  | RO | 1 | → |  |  | Unmapped
200 | Device Information (System Info) | 0x0C95 | 3221 | Inverter | U8 |  |  | RO | 8 | → | INVERTER_MODE |  | Ref(76%)
201 | Device Information (System Info) | 0x0C9D | 3229 | DSP1 | U8 |  |  | RO | 1 | → |  |  | Unmapped
202 | Device Information (System Info) | 0x0C9E | 3230 | DSP2 version number | U8 |  |  | RO | 1 | → | DSP_VERSION |  | Ref(73%)
203 | Device Information (System Info) | 0x0C9F | 3231 | Reserve | U8 |  |  | RO | 2 | → |  |  | Unmapped
--- Inverter Parameters (Setup) ---
204 | Inverter Parameters (Setup) | 0x0CE4 | 3300 | Clock information | U8 |  |  | RO | 7 | → |  |  | Unmapped
205 | Inverter Parameters (Setup) | 0x0CEB | 3307 | QV | U16 |  |  | RO | 4 | → |  |  | Unmapped
206 | Inverter Parameters (Setup) | 0x0CEF | 3311 | Setting Inverter SN | string |  |  | RW | 12 | → | INVERTER_ON_OFF |  | Ref(59%)
207 | Inverter Parameters (Setup) | 0x0CFB | 3323 | Setting PLC MAC | U8 |  |  | RW | 3 | → |  |  | Unmapped
208 | Inverter Parameters (Setup) | 0x0CFE | 3326 | QV Curve (2) | U16 |  |  | RO | 6 | → | IV_CURVE_SCAN |  | Ref(70%)
209 | Inverter Parameters (Setup) | 0x0D04 | 3332 | LCD Model Setting | U8 |  |  | RO | 1 | → |  |  | Unmapped
210 | Inverter Parameters (Setup) | 0x0D05 | 3333 | Inverter Model | U8 |  |  | RW | 8 | → | INVERTER_MODE |  | Ref(96%)
211 | Inverter Parameters (Setup) | 0x0CE4 | 3300 | Year (tens place) | U8 |  |  | RO | 1 | → |  |  | Unmapped
212 | Inverter Parameters (Setup) | 0x0CE5 | 3301 | Month (tens place) | U8 |  |  | RO | 1 | → |  |  | Unmapped
213 | Inverter Parameters (Setup) | 0x0CE6 | 3302 | Day (tens place) | U8 |  |  | RO | 1 | → | TODAY_ENERGY_L |  | Ref(57%)
214 | Inverter Parameters (Setup) | 0x0CE7 | 3303 | Hour (tens place) | U8 |  |  | RO | 1 | → |  |  | Unmapped
215 | Inverter Parameters (Setup) | 0x0CE8 | 3304 | Minute (tens place) | U8 |  |  | RO | 1 | → |  |  | Unmapped
216 | Inverter Parameters (Setup) | 0x0CE9 | 3305 | Second (tens place) | U8 |  |  | RO | 1 | → |  |  | Unmapped
217 | Inverter Parameters (Setup) | 0x0CEA | 3306 | Week | U8 |  |  | RO | 1 | → |  |  | Unmapped
--- DER-AVM Parameters (Control) ---
218 | DER-AVM Parameters (Control) | 0x0D04 | 3332 | LCD Model | U16 |  |  | RO | 1 | → | DEVICE_MODEL |  | Ref(67%)
219 | DER-AVM Parameters (Control) | 0x0FA0 | 4000 | Clear statistical | U16 |  |  | RW | 1 | → | DEA_STATUS_FLAG_LOW |  | Ref(56%)
220 | DER-AVM Parameters (Control) | 0x0FA1 | 4001 | Remote | U16 |  |  | RW | 1 | → |  |  | Unmapped
221 | DER-AVM Parameters (Control) | 0x0FA2 | 4002 | Revoke remote | U16 |  |  | RW | 1 | → | DEVICE_MODEL |  | Ref(56%)
222 | DER-AVM Parameters (Control) | 0x0FA3 | 4003 | Set the power | U16 |  |  | RO | 1 | → | INV_T_POWER |  | Ref(67%)
223 | DER-AVM Parameters (Control) | 0x0FA4 | 4004 | Set the active | U16 | % |  | RO | 1 | → |  |  | Unmapped
224 | DER-AVM Parameters (Control) | 0x0FA5 | 4005 | Set the reactive | S16 | 1KVar | 1 | RO | 1 | → |  |  | Unmapped
225 | DER-AVM Parameters (Control) | 0x0FA6 | 4006 | Set the reactive | U16 |  |  | RO | 1 | → |  |  | Unmapped
226 | DER-AVM Parameters (Control) | 0x0FA7 | 4007 | Overfrequency | U16 |  |  | RW | 1 | → | R_FREQUENCY |  | Ref(83%)
227 | DER-AVM Parameters (Control) | 0x0FA8 | 4008 | Overfrequency | U16 | 0.01Hz | 0.01 | RO | 1 | → | R_FREQUENCY |  | Ref(83%)
228 | DER-AVM Parameters (Control) | 0x0FA9 | 4009 | Set the derating | U16 | Hz |  | RW | 1 | → | POWER_DERATING_PCT |  | Ref(59%)
229 | DER-AVM Parameters (Control) | 0x0FAA | 4010 | Set the active | U16 |  |  | RO | 1 | → |  |  | Unmapped
230 | DER-AVM Parameters (Control) | 0x0FAB | 4011 | LOGO Settings | U16 |  |  | RO | 1 | → |  |  | Unmapped
231 | DER-AVM Parameters (Control) | 0x0FAC | 4012 | Input | U16 |  |  | RO | 1 | → | INPUT_POWER |  | Ref(62%)
232 | DER-AVM Parameters (Control) | 0x0FAD | 4013 | Grid | U16 |  |  | RO | 1 | → |  |  | Unmapped
233 | DER-AVM Parameters (Control) | 0x0FAE | 4014 | Start | U16 |  |  | RO | 1 | → | BLOCK5_START |  | Ref(59%)
234 | DER-AVM Parameters (Control) | 0x0FAF | 4015 | Start | U16 |  |  | RW | 1 | → | BLOCK5_START |  | Ref(59%)
235 | DER-AVM Parameters (Control) | 0x0FB0 | 4016 | Grid | U16 |  |  | RO | 1 | → |  |  | Unmapped
236 | DER-AVM Parameters (Control) | 0x0FB1 | 4017 | Grid | U16 |  |  | RW | 1 | → |  |  | Unmapped
237 | DER-AVM Parameters (Control) | 0x0FB2 | 4018 | Grid Frequency | U16 |  |  | RW | 1 | → | GRID_FREQUENCY |  | Ref(100%)
238 | DER-AVM Parameters (Control) | 0x0FB3 | 4019 | Grid | U16 |  |  | RW | 1 | → |  |  | Unmapped
239 | DER-AVM Parameters (Control) | 0x0FB4 | 4020 | Back | U16 | W |  | RW | 1 | → |  |  | Unmapped
240 | DER-AVM Parameters (Control) | 0x0FB5 | 4021 | Overvoltage | U16 | 0.1% | 0.1 | RW | 1 | → | R_VOLTAGE |  | Ref(80%)
241 | DER-AVM Parameters (Control) | 0x0FB6 | 4022 | Reserve | U16 |  |  | RW | 1 | → |  |  | Unmapped
242 | DER-AVM Parameters (Control) | 0x0FB7 | 4023 | 485 | U16 |  |  | RW | 1 | → |  |  | Unmapped
243 | DER-AVM Parameters (Control) | 0x0FB8 | 4024 | 485 Baud Rate | U16 |  |  | RO | 1 | → |  |  | Unmapped
244 | DER-AVM Parameters (Control) | 0x0FB9 | 4025 | 485 Protocol | U16 |  |  | RO | 1 | → |  |  | Unmapped
245 | DER-AVM Parameters (Control) | 0x0FBA | 4026 | 485 | U16 |  |  | RW | 1 | → |  |  | Unmapped
246 | DER-AVM Parameters (Control) | 0x0FBB | 4027 | 485 Baud Rate | U16 |  |  | RO | 1 | → |  |  | Unmapped
247 | DER-AVM Parameters (Control) | 0x0FBC | 4028 | Three-phase | U16 |  |  | RO | 1 | → |  |  | Unmapped
248 | DER-AVM Parameters (Control) | 0x0FBD | 4029 | Remote | U16 |  |  | RW | 1 | → |  |  | Unmapped
249 | DER-AVM Parameters (Control) | 0x0FBE | 4030 | String | U16 | A |  | RW | 1 | → | PV_STRING_BASE |  | Ref(60%)
250 | DER-AVM Parameters (Control) | 0x0FBF | 4031 | Self-check | U16 |  |  | RO | 1 | → |  |  | Unmapped
251 | DER-AVM Parameters (Control) | 0x0FC0 | 4032 | Self-check | U16 |  |  | RO | 1 | → |  |  | Unmapped
252 | DER-AVM Parameters (Control) | 0x0FC1 | 4033 | Clear | U16 |  |  | RW | 1 | → |  |  | Unmapped
253 | DER-AVM Parameters (Control) | 0x0FC2 | 4034 | Factory | U16 |  |  | RW | 1 | → | POWER_FACTOR |  | Ref(63%)
254 | DER-AVM Parameters (Control) | 0x0FC3 | 4035 | Start I/V Scan | U16 |  |  | RW | 1 | → |  |  | Unmapped
255 | DER-AVM Parameters (Control) | 0x0FC4 | 4036 | Active | S16 |  |  | RO | 1 | → | ACTIVE_POWER |  | Ref(67%)
256 | DER-AVM Parameters (Control) | 0x0FC5 | 4037 | Active | S16 | W |  | RW | 1 | → | ACTIVE_POWER |  | Ref(67%)
257 | DER-AVM Parameters (Control) | 0x0FC6 | 4038 | Soft | S16 | %/min |  | RW | 1 | → |  |  | Unmapped
258 | DER-AVM Parameters (Control) | 0x0FC7 | 4039 | Active Power | U16 | 0.1% | 0.1 | RW | 1 | → | ACTIVE_POWER |  | Ref(100%)
259 | DER-AVM Parameters (Control) | 0x0FC8 | 4040 | R-phase | U16 |  |  | RW | 1 | → | R_PHASE_CURRENT |  | Ref(67%)
260 | DER-AVM Parameters (Control) | 0x0FC9 | 4041 | S-phase | U16 |  |  | RW | 1 | → | S_PHASE_VOLTAGE |  | Ref(67%)
261 | DER-AVM Parameters (Control) | 0x0FCA | 4042 | T-phase | U16 |  |  | RW | 1 | → | T_PHASE_VOLTAGE |  | Ref(67%)
262 | DER-AVM Parameters (Control) | 0x0FCB | 4043 | R-phase | U16 |  |  | RW | 1 | → | R_PHASE_CURRENT |  | Ref(67%)
263 | DER-AVM Parameters (Control) | 0x0FCC | 4044 | S-phase | U16 |  |  | RW | 1 | → | S_PHASE_VOLTAGE |  | Ref(67%)
264 | DER-AVM Parameters (Control) | 0x0FCD | 4045 | T-phase | U16 |  |  | RW | 1 | → | T_PHASE_VOLTAGE |  | Ref(67%)
265 | DER-AVM Parameters (Control) | 0x0FCE | 4046 | Battery Voltage | U16 |  |  | RW | 1 | → | R_VOLTAGE |  | Ref(75%)
266 | DER-AVM Parameters (Control) | 0x112F | 4399 | Record | U16 |  |  | RO | 1 | → |  |  | Unmapped
Mode: OFFLINE ¦ Match stats: Auto/Ref=170, Unmapped=96 ¦ Edit "Solarize_Name" for Unmapped rows (red = needs review).

## Status_Mapping
Raw_Code | Raw_Name | InverterMode_State | Solarize_Code | Notes
0 | INITIAL | INITIAL | 0
1 | STANDBY | STANDBY | 1
3 | ON_GRID | ON_GRID | 3
4 | OFF_GRID | ON_GRID | 3
5 | FAULT | FAULT | 5
9 | SHUTDOWN | SHUTDOWN | 9
NOTE: Edit "InverterMode_State" column: INITIAL/STANDBY/ON_GRID/FAULT/SHUTDOWN

## DER_AVM_Control
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x07D0 | 2000 | DER_POWER_FACTOR_SET | S16 | FC06 | 1 |  | 0.001 | RW | Power factor setpoint [-1000,-800],[800,1000]
0x07D1 | 2001 | DER_ACTION_MODE | U16 | FC06 | 1 |  | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
0x07D2 | 2002 | DER_REACTIVE_POWER_PCT | S16 | FC06 | 1 | % | 0.1 | RW | Reactive power % [-484,484]
0x07D3 | 2003 | DER_ACTIVE_POWER_PCT | U16 | FC06 | 1 | % | 0.1 | RW | Active power % [0,1100]
0x0834 | 2100 | INVERTER_ON_OFF | U16 | FC06 | 1 |  | 1 | RW | On/Off control: 0=ON, 1=OFF
0x0835 | 2101 | CLEAR_PV_INSULATION_WARNING | U16 | FC06 | 1 |  | 1 | WO | Clear PV insulation warning: 1=Clear
0x6001 | 24577 | INVERTER_CONTROL | U16 | FC06 | 1 |  | 1 | WO | Inverter control: 0=Power on, 1=Shut down
0x600D | 24589 | IV_CURVE_SCAN | U16 | FC06 | 1 |  | 1 | RW | IV curve scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
0x600F | 24591 | POWER_FACTOR_DYNAMIC | S16 | FC06 | 1 |  | 0.001 | RW | Dynamic power factor control
0x6010 | 24592 | REACTIVE_POWER_DYNAMIC | S16 | FC06 | 1 | % | 0.01 | RW | Dynamic reactive power control (%)
0x3005 | 12293 | POWER_DERATING_PCT | U16 | FC06 | 1 | % | 1 | RW | Active power derating [0-110]%
NOTE: DER-AVM control registers (always included). Do not modify addresses.

## DEA_AVM_Monitor
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x03E8 | 1000 | DEA_L1_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L1 current (low word)
0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 current (high word)
0x03EA | 1002 | DEA_L2_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L2 current (low word)
0x03EB | 1003 | DEA_L2_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 current (high word)
0x03EC | 1004 | DEA_L3_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L3 current (low word)
0x03ED | 1005 | DEA_L3_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 current (high word)
0x03EE | 1006 | DEA_L1_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L1 voltage (low word)
0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 voltage (high word)
0x03F0 | 1008 | DEA_L2_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L2 voltage (low word)
0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 voltage (high word)
0x03F2 | 1010 | DEA_L3_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L3 voltage (low word)
0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 voltage (high word)
0x03F4 | 1012 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | FC03 | 2 | kW | 0.1 | RO | DEA total active power (low word)
0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total active power (high word)
0x03F6 | 1014 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | FC03 | 2 | Var | 1 | RO | DEA total reactive power (low word)
0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total reactive power (high word)
0x03F8 | 1016 | DEA_POWER_FACTOR_LOW | S32 | FC03 | 2 |  | 0.001 | RO | DEA power factor (low word)
0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | S32 | FC03 | 1 |  |  | RO | DEA power factor (high word)
0x03FA | 1018 | DEA_FREQUENCY_LOW | S32 | FC03 | 2 | Hz | 0.1 | RO | DEA frequency (low word)
0x03FB | 1019 | DEA_FREQUENCY_HIGH | S32 | FC03 | 1 |  |  | RO | DEA frequency (high word)
0x03FC | 1020 | DEA_STATUS_FLAG_LOW | S32 | FC03 | 2 |  | 1 | RO | DEA status flag (low word)
0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | S32 | FC03 | 1 |  |  | RO | DEA status flag (high word)
NOTE: DEA-AVM monitoring registers (always included). Do not modify addresses.