## SUMMARY
Category | Count | Notes
INFO | 12 | Device info (model, SN, FW, rated values)
MONITORING | 100 | AC(12) + MPPT 1-9(27) + Grid totals(10) + String 1-24(48) + Misc(3)
STATUS | 1 | Inverter Mode (0x101D)
ALARM | 3 | Error Code 1/2/3 (48-bit total)
DER_CONTROL | 11 | DER-AVM control registers
DER_MONITOR | 11 | DEA-AVM real-time monitoring
IV_SCAN | 45 | 9 trackers x (1 voltage + 4 string current) = 45 blocks, 64 points each
REVIEW | 5 | All 5 are duplicate addresses -> verdict: DELETE
TOTAL | 188

## META
Key | Value
Manufacturer | Senergy (APD)
Protocol Version | V1.2.4
Protocol Name | senergy
MPPT Count (PDF max) | 9
Strings per MPPT | 4
Total Strings (PDF max) | 24
IV Scan Support | Yes (9 trackers x 4 strings x 64 points)
DER-AVM Support | Yes
Solarize Protocol Compatible | Yes (same register base)
Stage | Stage 1 (full extraction)
Generated | 2026-04-01
Source PDF | Senergy Modbus Protocol-Korea-V1.2.4.pdf

## INFO
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match
1 | INFO | Device Model name | 0x1A00 | 8 | string | ASCII | RO |  |  | DEVICE_MODEL
2 | INFO | Device Serial number | 0x1A10 | 8 | string | ASCII | RO |  |  | SERIAL_NUMBER
3 | INFO | Master firmware version | 0x1A1C | 3 | string | ASCII | RO |  |  | FIRMWARE_VERSION
4 | INFO | Slave firmware version | 0x1A26 | 3 | string | ASCII | RO |  |  | FIRMWARE_VERSION
5 | INFO | MPPT Number | 0x1A3B | 1 | U16 |  | RO | 1=1 MPPT |  | MPPT_COUNT
6 | INFO | Nominal Voltage | 0x1A44 | 1 | U16 | 0.1V | RO | 2200=220V |  | NOMINAL_VOLTAGE
7 | INFO | Nominal Frequency | 0x1A45 | 1 | U16 | 0.01Hz | RO | 5000=50Hz |  | NOMINAL_FREQUENCY
8 | INFO | Nominal Active Power (Low) | 0x1A46 | 1 | U16 | 1W | RO | 1500=1500W |  | NOMINAL_POWER
9 | INFO | Nominal Active Power (High) | 0x1A4E | 1 | U16 | 1W | RO | 1*65536W |  | NOMINAL_POWER
10 | INFO | Grid Phase Number | 0x1A48 | 1 | U16 |  | RO | 1=single,2=split,3=three |  | GRID_PHASE_NUMBER
11 | INFO | EMS Firmware Version | 0x1A60 | 3 | string | ASCII | RO |  |  | FIRMWARE_VERSION
12 | INFO | LCD firmware version | 0x1A8E | 3 | string | ASCII | RO |  |  | FIRMWARE_VERSION

## MONITORING
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match
1 | MONITORING | L1 Voltage | 0x1001 | 1 | U16 | 0.1V | RO |  | r_voltage | L1_VOLTAGE
2 | MONITORING | L1 Current | 0x1002 | 1 | U16 | 0.01A | RO |  | r_current | L1_CURRENT
3 | MONITORING | L1 Power | 0x1003 | 2 | S32 | 0.1W | RO |  | r_power
4 | MONITORING | L1 Frequency | 0x1005 | 1 | U16 | 0.01Hz | RO |  | frequency | L1_FREQUENCY
5 | MONITORING | L2 Voltage | 0x1006 | 1 | U16 | 0.1V | RO |  | s_voltage | L2_VOLTAGE
6 | MONITORING | L2 Current | 0x1007 | 1 | U16 | 0.01A | RO |  | s_current | L2_CURRENT
7 | MONITORING | L2 Power | 0x1008 | 2 | S32 | 0.1W | RO |  | s_power
8 | MONITORING | L2 Frequency | 0x100A | 1 | U16 | 0.01Hz | RO
9 | MONITORING | L3 Voltage | 0x100B | 1 | U16 | 0.1V | RO |  | t_voltage | L3_VOLTAGE
10 | MONITORING | L3 Current | 0x100C | 1 | U16 | 0.01A | RO |  | t_current | L3_CURRENT
11 | MONITORING | L3 Power | 0x100D | 2 | S32 | 0.1W | RO |  | t_power
12 | MONITORING | L3 Frequency | 0x100F | 1 | U16 | 0.01Hz | RO
13 | MONITORING | MPPT1 Voltage | 0x1010 | 1 | U16 | 0.1V | RO |  | mppt1_voltage | MPPT_VOLTAGE
14 | MONITORING | MPPT1 Current | 0x1011 | 1 | S16 | 0.01A | RO |  | mppt1_current | MPPT_CURRENT
15 | MONITORING | MPPT1 Power | 0x1012 | 2 | U32 | 0.1W | RO |  | mppt1_power | MPPT_POWER
16 | MONITORING | MPPT2 Voltage | 0x1014 | 1 | U16 | 0.1V | RO |  | mppt2_voltage | MPPT_VOLTAGE
17 | MONITORING | MPPT2 Current | 0x1015 | 1 | S16 | 0.01A | RO |  | mppt2_current | MPPT_CURRENT
18 | MONITORING | MPPT2 Power | 0x1016 | 2 | U32 | 0.1W | RO |  | mppt2_power | MPPT_POWER
19 | MONITORING | MPPT3 Voltage | 0x1018 | 1 | U16 | 0.1V | RO |  | mppt3_voltage | MPPT_VOLTAGE
20 | MONITORING | MPPT3 Current | 0x1019 | 1 | S16 | 0.01A | RO |  | mppt3_current | MPPT_CURRENT
21 | MONITORING | MPPT3 Power | 0x101A | 2 | U32 | 0.1W | RO |  | mppt3_power | MPPT_POWER
22 | MONITORING | Inner Temperature | 0x101C | 1 | S16 | 1C | RO |  | temperature | INNER_TEMP
23 | MONITORING | MPPT4 Voltage | 0x103E | 1 | U16 | 0.1V | RO |  | mppt4_voltage | MPPT_VOLTAGE
24 | MONITORING | MPPT4 Current | 0x103F | 1 | S16 | 0.01A | RO |  | mppt4_current | MPPT_CURRENT
25 | MONITORING | MPPT4 Power | 0x1040 | 2 | U32 | 0.1W | RO |  | mppt4_power | MPPT_POWER
26 | MONITORING | MPPT5 Voltage | 0x1080 | 1 | U16 | 0.1V | RO |  | mppt5_voltage | MPPT_VOLTAGE
27 | MONITORING | MPPT5 Current | 0x1081 | 1 | S16 | 0.01A | RO |  | mppt5_current | MPPT_CURRENT
28 | MONITORING | MPPT5 Power | 0x1082 | 2 | U32 | 0.1W | RO |  | mppt5_power | MPPT_POWER
29 | MONITORING | MPPT6 Voltage | 0x1084 | 1 | U16 | 0.1V | RO |  | mppt6_voltage | MPPT_VOLTAGE
30 | MONITORING | MPPT6 Current | 0x1085 | 1 | S16 | 0.01A | RO |  | mppt6_current | MPPT_CURRENT
31 | MONITORING | MPPT6 Power | 0x1086 | 2 | U32 | 0.1W | RO |  | mppt6_power | MPPT_POWER
32 | MONITORING | MPPT7 Voltage | 0x1088 | 1 | U16 | 0.1V | RO |  | mppt7_voltage | MPPT_VOLTAGE
33 | MONITORING | MPPT7 Current | 0x1089 | 1 | S16 | 0.01A | RO |  | mppt7_current | MPPT_CURRENT
34 | MONITORING | MPPT7 Power | 0x108A | 2 | U32 | 0.1W | RO |  | mppt7_power | MPPT_POWER
35 | MONITORING | MPPT8 Voltage | 0x108C | 1 | U16 | 0.1V | RO |  | mppt8_voltage | MPPT_VOLTAGE
36 | MONITORING | MPPT8 Current | 0x108D | 1 | S16 | 0.01A | RO |  | mppt8_current | MPPT_CURRENT
37 | MONITORING | MPPT8 Power | 0x108E | 2 | U32 | 0.1W | RO |  | mppt8_power | MPPT_POWER
38 | MONITORING | MPPT9 Voltage | 0x1090 | 1 | U16 | 0.1V | RO |  | mppt9_voltage | MPPT_VOLTAGE
39 | MONITORING | MPPT9 Current | 0x1091 | 1 | S16 | 0.01A | RO |  | mppt9_current | MPPT_CURRENT
40 | MONITORING | MPPT9 Power | 0x1092 | 2 | U32 | 0.1W | RO |  | mppt9_power | MPPT_POWER
41 | MONITORING | Grid total Active Power | 0x1037 | 2 | S32 | 0.1W | RO | L1+L2+L3 | ac_power | GRID_TOTAL_ACTIVE_POWER
42 | MONITORING | Grid total Reactive Power | 0x1039 | 2 | S32 | 0.1Var | RO | L1+L2+L3 | reactive_power | REACTIVE_POWER
43 | MONITORING | PV Today Peak Power | 0x103B | 2 | S32 | 0.1W | RO
44 | MONITORING | Power Factor | 0x103D | 1 | S16 | 0.001 | RO |  | power_factor | POWER_FACTOR
45 | MONITORING | PV total input power | 0x1048 | 2 | U32 | 0.1W | RO | Add all MPPT | pv_power | PV_TOTAL_INPUT_POWER
46 | MONITORING | Decimals of total energy | 0x104C | 1 | U16 | Wh | RO | Relate to 0x1021 | cumulative_energy(dec)
47 | MONITORING | Total Energy | 0x1021 | 2 | U32 | kWh | RO |  | cumulative_energy | TOTAL_ENERGY
48 | MONITORING | Total generation time | 0x1023 | 2 | U32 | Hour | RO
49 | MONITORING | Today Energy | 0x1027 | 2 | U32 | Wh | RO |  | daily_energy | DAILY_ENERGY
50 | MONITORING | Fuse open data | 0x1034 | 2 | U16 |  | RO | Fuse Open Data Table (B1-B8)
51 | MONITORING | String1 input voltage | 0x1050 | 1 | U16 | 0.1V | RO |  | string1_voltage | STRING_VOLTAGE
52 | MONITORING | String1 input current | 0x1051 | 1 | S16 | 0.01A | RO |  | string1_current | STRING_CURRENT
53 | MONITORING | String2 input voltage | 0x1052 | 1 | U16 | 0.1V | RO |  | string2_voltage | STRING_VOLTAGE
54 | MONITORING | String2 input current | 0x1053 | 1 | S16 | 0.01A | RO |  | string2_current | STRING_CURRENT
55 | MONITORING | String3 input voltage | 0x1054 | 1 | U16 | 0.1V | RO |  | string3_voltage | STRING_VOLTAGE
56 | MONITORING | String3 input current | 0x1055 | 1 | S16 | 0.01A | RO |  | string3_current | STRING_CURRENT
57 | MONITORING | String4 input voltage | 0x1056 | 1 | U16 | 0.1V | RO |  | string4_voltage | STRING_VOLTAGE
58 | MONITORING | String4 input current | 0x1057 | 1 | S16 | 0.01A | RO |  | string4_current | STRING_CURRENT
59 | MONITORING | String5 input voltage | 0x1058 | 1 | U16 | 0.1V | RO |  | string5_voltage | STRING_VOLTAGE
60 | MONITORING | String5 input current | 0x1059 | 1 | S16 | 0.01A | RO |  | string5_current | STRING_CURRENT
61 | MONITORING | String6 input voltage | 0x105A | 1 | U16 | 0.1V | RO |  | string6_voltage | STRING_VOLTAGE
62 | MONITORING | String6 input current | 0x105B | 1 | S16 | 0.01A | RO |  | string6_current | STRING_CURRENT
63 | MONITORING | String7 input voltage | 0x105C | 1 | U16 | 0.1V | RO |  | string7_voltage | STRING_VOLTAGE
64 | MONITORING | String7 input current | 0x105D | 1 | S16 | 0.01A | RO |  | string7_current | STRING_CURRENT
65 | MONITORING | String8 input voltage | 0x105E | 1 | U16 | 0.1V | RO |  | string8_voltage | STRING_VOLTAGE
66 | MONITORING | String8 input current | 0x105F | 1 | S16 | 0.01A | RO |  | string8_current | STRING_CURRENT
67 | MONITORING | String9 input voltage | 0x1060 | 1 | U16 | 0.1V | RO |  | string9_voltage | STRING_VOLTAGE
68 | MONITORING | String9 input current | 0x1061 | 1 | S16 | 0.01A | RO |  | string9_current | STRING_CURRENT
69 | MONITORING | String10 input voltage | 0x1062 | 1 | U16 | 0.1V | RO |  | string10_voltage | STRING_VOLTAGE
70 | MONITORING | String10 input current | 0x1063 | 1 | S16 | 0.01A | RO |  | string10_current | STRING_CURRENT
71 | MONITORING | String11 input voltage | 0x1064 | 1 | U16 | 0.1V | RO |  | string11_voltage | STRING_VOLTAGE
72 | MONITORING | String11 input current | 0x1065 | 1 | S16 | 0.01A | RO |  | string11_current | STRING_CURRENT
73 | MONITORING | String12 input voltage | 0x1066 | 1 | U16 | 0.1V | RO |  | string12_voltage | STRING_VOLTAGE
74 | MONITORING | String12 input current | 0x1067 | 1 | S16 | 0.01A | RO |  | string12_current | STRING_CURRENT
75 | MONITORING | String13 input voltage | 0x1068 | 1 | U16 | 0.1V | RO |  | string13_voltage | STRING_VOLTAGE
76 | MONITORING | String13 input current | 0x1069 | 1 | S16 | 0.01A | RO |  | string13_current | STRING_CURRENT
77 | MONITORING | String14 input voltage | 0x106A | 1 | U16 | 0.1V | RO |  | string14_voltage | STRING_VOLTAGE
78 | MONITORING | String14 input current | 0x106B | 1 | S16 | 0.01A | RO |  | string14_current | STRING_CURRENT
79 | MONITORING | String15 input voltage | 0x106C | 1 | U16 | 0.1V | RO |  | string15_voltage | STRING_VOLTAGE
80 | MONITORING | String15 input current | 0x106D | 1 | S16 | 0.01A | RO |  | string15_current | STRING_CURRENT
81 | MONITORING | String16 input voltage | 0x106E | 1 | U16 | 0.1V | RO |  | string16_voltage | STRING_VOLTAGE
82 | MONITORING | String16 input current | 0x106F | 1 | S16 | 0.01A | RO |  | string16_current | STRING_CURRENT
83 | MONITORING | String17 input voltage | 0x1070 | 1 | U16 | 0.1V | RO |  | string17_voltage | STRING_VOLTAGE
84 | MONITORING | String17 input current | 0x1071 | 1 | S16 | 0.01A | RO |  | string17_current | STRING_CURRENT
85 | MONITORING | String18 input voltage | 0x1072 | 1 | U16 | 0.1V | RO |  | string18_voltage | STRING_VOLTAGE
86 | MONITORING | String18 input current | 0x1073 | 1 | S16 | 0.01A | RO |  | string18_current | STRING_CURRENT
87 | MONITORING | String19 input voltage | 0x1074 | 1 | U16 | 0.1V | RO |  | string19_voltage | STRING_VOLTAGE
88 | MONITORING | String19 input current | 0x1075 | 1 | S16 | 0.01A | RO |  | string19_current | STRING_CURRENT
89 | MONITORING | String20 input voltage | 0x1076 | 1 | U16 | 0.1V | RO |  | string20_voltage | STRING_VOLTAGE
90 | MONITORING | String20 input current | 0x1077 | 1 | S16 | 0.01A | RO |  | string20_current | STRING_CURRENT
91 | MONITORING | String21 input voltage | 0x1078 | 1 | U16 | 0.1V | RO |  | string21_voltage | STRING_VOLTAGE
92 | MONITORING | String21 input current | 0x1079 | 1 | S16 | 0.01A | RO |  | string21_current | STRING_CURRENT
93 | MONITORING | String22 input voltage | 0x107A | 1 | U16 | 0.1V | RO |  | string22_voltage | STRING_VOLTAGE
94 | MONITORING | String22 input current | 0x107B | 1 | S16 | 0.01A | RO |  | string22_current | STRING_CURRENT
95 | MONITORING | String23 input voltage | 0x107C | 1 | U16 | 0.1V | RO |  | string23_voltage | STRING_VOLTAGE
96 | MONITORING | String23 input current | 0x107D | 1 | S16 | 0.01A | RO |  | string23_current | STRING_CURRENT
97 | MONITORING | String24 input voltage | 0x107E | 1 | U16 | 0.1V | RO |  | string24_voltage | STRING_VOLTAGE
98 | MONITORING | String24 input current | 0x107F | 1 | S16 | 0.01A | RO |  | string24_current | STRING_CURRENT
99 | MONITORING | External fan speed duty | 0x120C | 1 | U16 | 1% | RO
100 | MONITORING | DER-AVM digital meter connect status | 0x1210 | 1 | U16 |  | RO | 0:disconnected, 1:connected

## STATUS
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match
1 | STATUS | Inverter Mode | 0x101D | 1 | U16 |  | RO | 0x00=Initial, 0x01=Standby, 0x03=On-Grid, 0x04=Off-Grid, 0x05=Fault, 0x09=Shutdown | status | INVERTER_MODE

## ALARM
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match
1 | ALARM | Error Code1 | 0x101E | 1 | U16 |  | RO | B0:DC-bias overcurrent B1:Relay abnormal B2:Remote off B3:Over temperature B4:GFCI abnormal B5:PV string reverse B6:System type error B7:Fan abnormal B8:DC-link unbalance B9:DC-link overvoltage B10:Internal comm error B11:SW incompatibility B12:Internal storage error B13:Data inconsistency B14:Inverter abnormal B15:Boost abnormal | alarm1 | ERROR_CODE1
2 | ALARM | Error Code2 | 0x101F | 1 | U16 |  | RO | B0:Grid overvoltage B1:Grid undervoltage B2:Grid absent B3:Grid overfrequency B4:Grid underfrequency B5:PV overvoltage B6:PV insulation abnormal B7:Leakage current abnormal B8:Power limit state B9:Internal PSU abnormal B10:PV string abnormal B11:PV undervoltage B12:PV irradiation weak B13:Grid abnormal B14:Arc fault detection B15:AC moving avg voltage high | alarm2 | ERROR_CODE2
3 | ALARM | Error Code3 | 0x1020 | 1 | U16 |  | RO | B0:Reserved B1:Logger EEPROM fail B2:Reserved B3:PID device abnormal B4:AFCI lost B5:Data logger lost B6:Meter lost B7:Inverter lost B8:Grid N abnormal B9:SPD defective B10:Parallel ID warning B11:Parallel SYN signal warning B12:Parallel BAT abnormal B13:Parallel GRID abnormal B14:Generator voltage abnormal B15:Reserved | alarm3 | ERROR_CODE3

## DER_CONTROL
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match
1 | DER_CONTROL | DER-AVM mode | 0x1211 | 1 | U16 |  | RW | 0:self control, 1:DER-AVM control
2 | DER_CONTROL | Power factor setting | 0x07D0 | 1 | S16 | 0.001 | RW | [-1000,-800],[800,1000] Default 1000 |  | POWER_FACTOR_SET
3 | DER_CONTROL | Action mode | 0x07D1 | 1 | U16 |  | RW | 0:self-control, 2:DER-AVM control, 5:Q(V)control. Default 2 |  | OPERATION_MODE
4 | DER_CONTROL | Reactive power percent setting | 0x07D2 | 1 | S16 | 0.1% | RW | [-484,484] Default 0 |  | REACTIVE_POWER_SET
5 | DER_CONTROL | Active power percent setting | 0x07D3 | 1 | U16 | 0.1% | RW | [0,1100] Default 1000 (100%=no limit) |  | ACTIVE_POWER_LIMIT
6 | DER_CONTROL | Inverter off | 0x0834 | 1 | U16 |  | RW | 0:Inverter on, 1:Inverter off. Default 0 |  | ON_OFF
7 | DER_CONTROL | Clear PV insulation warning | 0x0835 | 1 | U16 |  | RW | 0:Non-active, 1:Clear PV insulation warning
8 | DER_CONTROL | Power derating percent by Modbus | 0x3005 | 1 | U16 |  | RW | [0,110] Dynamic active power regulation |  | ACTIVE_POWER_LIMIT
9 | DER_CONTROL | Output reactive power mode | 0x5030 | 1 | U16 |  | RW | 0:Pure active, 1:cos_phi const, 2:Q const, 3:cos_phi(P), 4:Q(U), 5:AUTO P(U), 6:Watt(U), 7:Q(U) AS4777, 8:Q const(P priority), 9:Q(P) Curve |  | OPERATION_MODE
10 | DER_CONTROL | Power factor setting (grid code) | 0x5031 | 1 | S16 | 0.001 | RW | [-1000,-800],[800,1000] |  | POWER_FACTOR_SET
11 | DER_CONTROL | Q Reference Output reactive power | 0x5032 | 1 | S16 | 0.1kVAR | RW |  |  | REACTIVE_POWER_SET

## DER_MONITOR
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match
1 | DER_MONITOR | DEA-AVM L1 Current | 0x03E8 | 2 | S32 | 0.1A | RO |  | r_current(dea)
2 | DER_MONITOR | DEA-AVM L2 Current | 0x03EA | 2 | S32 | 0.1A | RO |  | s_current(dea)
3 | DER_MONITOR | DEA-AVM L3 Current | 0x03EC | 2 | S32 | 0.1A | RO |  | t_current(dea)
4 | DER_MONITOR | DEA-AVM L1 Voltage | 0x03EE | 2 | S32 | 0.1V | RO |  | r_voltage(dea)
5 | DER_MONITOR | DEA-AVM L2 Voltage | 0x03F0 | 2 | S32 | 0.1V | RO |  | s_voltage(dea)
6 | DER_MONITOR | DEA-AVM L3 Voltage | 0x03F2 | 2 | S32 | 0.1V | RO |  | t_voltage(dea)
7 | DER_MONITOR | DEA-AVM Grid total Active Power | 0x03F4 | 2 | S32 | 0.1kW | RO | L1+L2+L3 | ac_power(dea)
8 | DER_MONITOR | DEA-AVM Grid total Reactive Power | 0x03F6 | 2 | S32 | Var | RO | L1+L2+L3 | reactive_power(dea)
9 | DER_MONITOR | DEA-AVM Power Factor | 0x03F8 | 2 | S32 | 0.001 | RO |  | power_factor(dea)
10 | DER_MONITOR | DEA-AVM Frequency | 0x03FA | 2 | S32 | 0.1Hz | RO |  | frequency(dea)
11 | DER_MONITOR | DEA-AVM Status Flag 1 | 0x03FC | 2 | S32 |  | RO | B1:Inv action(0=Run/1=Fail) B2:CB action(0=Run/1=Fail) B3:Run state(0=DER-AVM/1=Self) B4:AP ctrl ack B5:Inv action ctrl ack

## IV_SCAN
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match
1 | IV_SCAN | Tracker 1 voltage | 0x8000 | 64 | U16 | 0.1V | RO | 64 data points
2 | IV_SCAN | String 1-1 current | 0x8040 | 64 | S16 | 0.01A | RO | 64 data points
3 | IV_SCAN | String 1-2 current | 0x8080 | 64 | S16 | 0.01A | RO | 64 data points
4 | IV_SCAN | String 1-3 current | 0x80C0 | 64 | S16 | 0.01A | RO | 64 data points
5 | IV_SCAN | String 1-4 current | 0x8100 | 64 | S16 | 0.01A | RO | 64 data points
6 | IV_SCAN | Tracker 2 voltage | 0x8140 | 64 | U16 | 0.1V | RO | 64 data points
7 | IV_SCAN | String 2-1 current | 0x8180 | 64 | S16 | 0.01A | RO | 64 data points
8 | IV_SCAN | String 2-2 current | 0x81C0 | 64 | S16 | 0.01A | RO | 64 data points
9 | IV_SCAN | String 2-3 current | 0x8200 | 64 | S16 | 0.01A | RO | 64 data points
10 | IV_SCAN | String 2-4 current | 0x8240 | 64 | S16 | 0.01A | RO | 64 data points
11 | IV_SCAN | Tracker 3 voltage | 0x8280 | 64 | U16 | 0.1V | RO | 64 data points
12 | IV_SCAN | String 3-1 current | 0x82C0 | 64 | S16 | 0.01A | RO | 64 data points
13 | IV_SCAN | String 3-2 current | 0x8300 | 64 | S16 | 0.01A | RO | 64 data points
14 | IV_SCAN | String 3-3 current | 0x8340 | 64 | S16 | 0.01A | RO | 64 data points
15 | IV_SCAN | String 3-4 current | 0x8380 | 64 | S16 | 0.01A | RO | 64 data points
16 | IV_SCAN | Tracker 4 voltage | 0x83C0 | 64 | U16 | 0.1V | RO | 64 data points
17 | IV_SCAN | String 4-1 current | 0x8400 | 64 | S16 | 0.01A | RO | 64 data points
18 | IV_SCAN | String 4-2 current | 0x8440 | 64 | S16 | 0.01A | RO | 64 data points
19 | IV_SCAN | String 4-3 current | 0x8480 | 64 | S16 | 0.01A | RO | 64 data points
20 | IV_SCAN | String 4-4 current | 0x84C0 | 64 | S16 | 0.01A | RO | 64 data points
21 | IV_SCAN | Tracker 5 voltage | 0x8500 | 64 | U16 | 0.1V | RO | 64 data points
22 | IV_SCAN | String 5-1 current | 0x8540 | 64 | S16 | 0.01A | RO | 64 data points
23 | IV_SCAN | String 5-2 current | 0x8580 | 64 | S16 | 0.01A | RO | 64 data points
24 | IV_SCAN | String 5-3 current | 0x85C0 | 64 | S16 | 0.01A | RO | 64 data points
25 | IV_SCAN | String 5-4 current | 0x8600 | 64 | S16 | 0.01A | RO | 64 data points
26 | IV_SCAN | Tracker 6 voltage | 0x8640 | 64 | U16 | 0.1V | RO | 64 data points
27 | IV_SCAN | String 6-1 current | 0x8680 | 64 | S16 | 0.01A | RO | 64 data points
28 | IV_SCAN | String 6-2 current | 0x86C0 | 64 | S16 | 0.01A | RO | 64 data points
29 | IV_SCAN | String 6-3 current | 0x8700 | 64 | S16 | 0.01A | RO | 64 data points
30 | IV_SCAN | String 6-4 current | 0x8740 | 64 | S16 | 0.01A | RO | 64 data points
31 | IV_SCAN | Tracker 7 voltage | 0x8780 | 64 | U16 | 0.1V | RO | 64 data points
32 | IV_SCAN | String 7-1 current | 0x87C0 | 64 | S16 | 0.01A | RO | 64 data points
33 | IV_SCAN | String 7-2 current | 0x8800 | 64 | S16 | 0.01A | RO | 64 data points
34 | IV_SCAN | String 7-3 current | 0x8840 | 64 | S16 | 0.01A | RO | 64 data points
35 | IV_SCAN | String 7-4 current | 0x8880 | 64 | S16 | 0.01A | RO | 64 data points
36 | IV_SCAN | Tracker 8 voltage | 0x88C0 | 64 | U16 | 0.1V | RO | 64 data points
37 | IV_SCAN | String 8-1 current | 0x8900 | 64 | S16 | 0.01A | RO | 64 data points
38 | IV_SCAN | String 8-2 current | 0x8940 | 64 | S16 | 0.01A | RO | 64 data points
39 | IV_SCAN | String 8-3 current | 0x8980 | 64 | S16 | 0.01A | RO | 64 data points
40 | IV_SCAN | String 8-4 current | 0x89C0 | 64 | S16 | 0.01A | RO | 64 data points
41 | IV_SCAN | Tracker 9 voltage | 0x8A00 | 64 | U16 | 0.1V | RO | 64 data points
42 | IV_SCAN | String 9-1 current | 0x8A40 | 64 | S16 | 0.01A | RO | 64 data points
43 | IV_SCAN | String 9-2 current | 0x8A80 | 64 | S16 | 0.01A | RO | 64 data points
44 | IV_SCAN | String 9-3 current | 0x8AC0 | 64 | S16 | 0.01A | RO | 64 data points
45 | IV_SCAN | String 9-4 current | 0x8B00 | 64 | S16 | 0.01A | RO | 64 data points

## REVIEW
Index | Category | Definition | Address | Reg Count | Type | Unit/Scale | R/W | Comment | H01 Field | Synonym Match | Verdict | Reason
1 | REVIEW | Q (Reference Output reactive power) | 0x1226 | 1 | S16 | 0.1kVAR | RO | Same physical quantity as 0x1039 and 0x03F6 | reactive_power | REACTIVE_POWER | DELETE | 0x1039(MONITORING) + 0x03F6(DER_MONITOR) already cover this. Duplicate.
2 | REVIEW | L1-N phase voltage of grid | 0x131A | 1 | U16 | 0.1V | RO | External meter grid voltage. Same as L1 Voltage 0x1001 | r_voltage | L1_VOLTAGE | DELETE | 0x1001(MONITORING L1 Voltage) already exists. External meter duplicate.
3 | REVIEW | L2-N phase voltage of grid | 0x131B | 1 | U16 | 0.1V | RO | External meter grid voltage. Same as L2 Voltage 0x1006 | s_voltage | L2_VOLTAGE | DELETE | 0x1006(MONITORING L2 Voltage) already exists. External meter duplicate.
4 | REVIEW | L3-N phase voltage of grid | 0x131C | 1 | U16 | 0.1V | RO | External meter grid voltage. Same as L3 Voltage 0x100B | t_voltage | L3_VOLTAGE | DELETE | 0x100B(MONITORING L3 Voltage) already exists. External meter duplicate.
5 | REVIEW | Frequency of grid | 0x1338 | 1 | U16 | 0.01Hz | RO | External meter frequency. Same as L1 Frequency 0x1005 | frequency | L1_FREQUENCY | DELETE | 0x1005(MONITORING L1 Frequency) already exists. External meter duplicate.