## Device_Info
Index | Definition | Address (Hex) | Address (Dec) | Register Number | Type | R/W | Unit | Comment / Notes
1 | Device Model Name | 0x1A00 | 6656 | 8 | string | RO | ASCII | Ex.: PV 30KTL
2 | Device Serial Number | 0x1A10 | 6672 | 8 | string | RO | ASCII | Ex.: 1234-123456789
3 | Master Firmware Version | 0x1A1C | 6684 | 3 | string | RO | ASCII | Ex.: 123456
4 | Slave Firmware Version | 0x1A26 | 6694 | 3 | string | RO | ASCII | Ex.: 123456
5 | MPPT Number | 0x1A3B | 6715 | 1 | U16 | RO |  | Ex.: 1 = 1 MPPT
6 | Nominal Voltage | 0x1A44 | 6724 | 1 | U16 | RW | 0.1V | Ex.: 2200 = 220V. 200/220/230/240/380/440/460/480V
7 | Nominal Frequency | 0x1A45 | 6725 | 1 | U16 | RO | 0.01Hz | Ex.: 5000 = 50Hz. 50/60Hz
8 | Nominal Active Power (Low) | 0x1A46 | 6726 | 1 | U16 | RO | 1W | Ex.: 1500 = 1500W
9 | Nominal Active Power (High) | 0x1A4E | 6734 | 1 | U16 | RO | 1W | Ex.: 1 = (1*65536)W
10 | Grid Phase Number | 0x1A48 | 6728 | 1 | U16 | RO |  | 1=single phase, 2=split phase, 3=three phases
11 | EMS Firmware Version | 0x1A60 | 6752 | 3 | string | RO | ASCII | Ex.: 123456
12 | LCD Firmware Version | 0x1A8E | 6798 | 3 | string | RO | ASCII | Ex.: 123456

## Inverter_RealTime
Index | Definition | Address (Hex) | Address (Dec) | Register Number | Type | R/W | Unit | Comment / Notes
1 | L1 Voltage | 0x1001 | 4097 | 1 | U16 | RO | 0.1V
2 | L1 Current | 0x1002 | 4098 | 1 | U16 | RO | 0.01A
3 | L1 Power | 0x1003 | 4099 | 2 | S32 | RO | 0.1W
4 | L1 Frequency | 0x1005 | 4101 | 1 | U16 | RO | 0.01Hz
5 | L2 Voltage | 0x1006 | 4102 | 1 | U16 | RO | 0.1V
6 | L2 Current | 0x1007 | 4103 | 1 | U16 | RO | 0.01A
7 | L2 Power | 0x1008 | 4104 | 2 | S32 | RO | 0.1W
8 | L2 Frequency | 0x100A | 4106 | 1 | U16 | RO | 0.01Hz
9 | L3 Voltage | 0x100B | 4107 | 1 | U16 | RO | 0.1V
10 | L3 Current | 0x100C | 4108 | 1 | U16 | RO | 0.01A
11 | L3 Power | 0x100D | 4109 | 2 | S32 | RO | 0.1W
12 | L3 Frequency | 0x100F | 4111 | 1 | U16 | RO | 0.01Hz
13 | MPPT1 Voltage | 0x1010 | 4112 | 1 | U16 | RO | 0.1V
14 | MPPT1 Current | 0x1011 | 4113 | 1 | S16 | RO | 0.01A
15 | MPPT1 Power | 0x1012 | 4114 | 2 | U32 | RO | 0.1W
16 | MPPT2 Voltage | 0x1014 | 4116 | 1 | U16 | RO | 0.1V
17 | MPPT2 Current | 0x1015 | 4117 | 1 | S16 | RO | 0.01A
18 | MPPT2 Power | 0x1016 | 4118 | 2 | U32 | RO | 0.1W
19 | MPPT3 Voltage | 0x1018 | 4120 | 1 | U16 | RO | 0.1V
20 | MPPT3 Current | 0x1019 | 4121 | 1 | S16 | RO | 0.01A
21 | MPPT3 Power | 0x101A | 4122 | 2 | U32 | RO | 0.1W
22 | Inner Temperature | 0x101C | 4124 | 1 | S16 | RO | 1°C
23 | Inverter Mode | 0x101D | 4125 | 1 | U16 | RO |  | See Inverter Mode Table
24 | Error Code 1 | 0x101E | 4126 | 1 | U16 | RO |  | See Error Code Table 1
25 | Error Code 2 | 0x101F | 4127 | 1 | U16 | RO |  | See Error Code Table 2
26 | Error Code 3 | 0x1020 | 4128 | 1 | U16 | RO |  | See Error Code Table 3
27 | Total Energy | 0x1021 | 4129 | 2 | U32 | RO | kWh
28 | Total Generation Time | 0x1023 | 4131 | 2 | U32 | RO | Hour
29 | Today Energy | 0x1027 | 4135 | 2 | U32 | RO | Wh
30 | Fuse Open Data | 0x1034 | 4148 | 2 | U16 | RO |  | See Fuse Open Data Table
31 | Grid Total Active Power | 0x1037 | 4151 | 2 | S32 | RO | 0.1W | L1+L2+L3
32 | Grid Total Reactive Power | 0x1039 | 4153 | 2 | S32 | RO | 0.1Var | L1+L2+L3
33 | PV Today Peak Power | 0x103B | 4155 | 2 | S32 | RO | 0.1W
34 | Power Factor | 0x103D | 4157 | 1 | S16 | RO | 0.001
35 | MPPT4 Voltage | 0x103E | 4158 | 1 | U16 | RO | 0.1V
36 | MPPT4 Current | 0x103F | 4159 | 1 | S16 | RO | 0.01A
37 | MPPT4 Power | 0x1040 | 4160 | 2 | U32 | RO | 0.1W
38 | PV Total Input Power | 0x1048 | 4168 | 2 | U32 | RO | 0.1W | Sum of all MPPT
39 | Decimals of Total Energy | 0x104C | 4172 | 1 | U16 | RO | Wh | Relate to 0x1021. e.g. 220.836kWh → 836
40 | String1 Input Voltage | 0x1050 | 4176 | 1 | U16 | RO | 0.1V
41 | String1 Input Current | 0x1051 | 4177 | 1 | S16 | RO | 0.01A
42 | String2 Input Voltage | 0x1052 | 4178 | 1 | U16 | RO | 0.1V
43 | String2 Input Current | 0x1053 | 4179 | 1 | S16 | RO | 0.01A
44 | String3 Input Voltage | 0x1054 | 4180 | 1 | U16 | RO | 0.1V
45 | String3 Input Current | 0x1055 | 4181 | 1 | S16 | RO | 0.01A
46 | String4 Input Voltage | 0x1056 | 4182 | 1 | U16 | RO | 0.1V
47 | String4 Input Current | 0x1057 | 4183 | 1 | S16 | RO | 0.01A
48 | String5 Input Voltage | 0x1058 | 4184 | 1 | U16 | RO | 0.1V
49 | String5 Input Current | 0x1059 | 4185 | 1 | S16 | RO | 0.01A
50 | String6 Input Voltage | 0x105A | 4186 | 1 | U16 | RO | 0.1V
51 | String6 Input Current | 0x105B | 4187 | 1 | S16 | RO | 0.01A
52 | String7 Input Voltage | 0x105C | 4188 | 1 | U16 | RO | 0.1V
53 | String7 Input Current | 0x105D | 4189 | 1 | S16 | RO | 0.01A
54 | String8 Input Voltage | 0x105E | 4190 | 1 | U16 | RO | 0.1V
55 | String8 Input Current | 0x105F | 4191 | 1 | S16 | RO | 0.01A
56 | String9 Input Voltage | 0x1060 | 4192 | 1 | U16 | RO | 0.1V
57 | String9 Input Current | 0x1061 | 4193 | 1 | S16 | RO | 0.01A
58 | String10 Input Voltage | 0x1062 | 4194 | 1 | U16 | RO | 0.1V
59 | String10 Input Current | 0x1063 | 4195 | 1 | S16 | RO | 0.01A
60 | String11 Input Voltage | 0x1064 | 4196 | 1 | U16 | RO | 0.1V
61 | String11 Input Current | 0x1065 | 4197 | 1 | S16 | RO | 0.01A
62 | String12 Input Voltage | 0x1066 | 4198 | 1 | U16 | RO | 0.1V
63 | String12 Input Current | 0x1067 | 4199 | 1 | S16 | RO | 0.01A
64 | String13 Input Voltage | 0x1068 | 4200 | 1 | U16 | RO | 0.1V
65 | String13 Input Current | 0x1069 | 4201 | 1 | S16 | RO | 0.01A
66 | String14 Input Voltage | 0x106A | 4202 | 1 | U16 | RO | 0.1V
67 | String14 Input Current | 0x106B | 4203 | 1 | S16 | RO | 0.01A
68 | String15 Input Voltage | 0x106C | 4204 | 1 | U16 | RO | 0.1V
69 | String15 Input Current | 0x106D | 4205 | 1 | S16 | RO | 0.01A
70 | String16 Input Voltage | 0x106E | 4206 | 1 | U16 | RO | 0.1V
71 | String16 Input Current | 0x106F | 4207 | 1 | S16 | RO | 0.01A
72 | String17 Input Voltage | 0x1070 | 4208 | 1 | U16 | RO | 0.1V
73 | String17 Input Current | 0x1071 | 4209 | 1 | S16 | RO | 0.01A
74 | String18 Input Voltage | 0x1072 | 4210 | 1 | U16 | RO | 0.1V
75 | String18 Input Current | 0x1073 | 4211 | 1 | S16 | RO | 0.01A
76 | String19 Input Voltage | 0x1074 | 4212 | 1 | U16 | RO | 0.1V
77 | String19 Input Current | 0x1075 | 4213 | 1 | S16 | RO | 0.01A
78 | String20 Input Voltage | 0x1076 | 4214 | 1 | U16 | RO | 0.1V
79 | String20 Input Current | 0x1077 | 4215 | 1 | S16 | RO | 0.01A
80 | String21 Input Voltage | 0x1078 | 4216 | 1 | U16 | RO | 0.1V
81 | String21 Input Current | 0x1079 | 4217 | 1 | S16 | RO | 0.01A
82 | String22 Input Voltage | 0x107A | 4218 | 1 | U16 | RO | 0.1V
83 | String22 Input Current | 0x107B | 4219 | 1 | S16 | RO | 0.01A
84 | String23 Input Voltage | 0x107C | 4220 | 1 | U16 | RO | 0.1V
85 | String23 Input Current | 0x107D | 4221 | 1 | S16 | RO | 0.01A
86 | String24 Input Voltage | 0x107E | 4222 | 1 | U16 | RO | 0.1V
87 | String24 Input Current | 0x107F | 4223 | 1 | S16 | RO | 0.01A
88 | MPPT5 Voltage | 0x1080 | 4224 | 1 | U16 | RO | 0.1V | Model-dependent
89 | MPPT5 Current | 0x1081 | 4225 | 1 | S16 | RO | 0.01A | Model-dependent
90 | MPPT5 Power | 0x1082 | 4226 | 2 | U32 | RO | 0.1W | Model-dependent
91 | MPPT6 Voltage | 0x1084 | 4228 | 1 | U16 | RO | 0.1V | Model-dependent
92 | MPPT6 Current | 0x1085 | 4229 | 1 | S16 | RO | 0.01A | Model-dependent
93 | MPPT6 Power | 0x1086 | 4230 | 2 | U32 | RO | 0.1W | Model-dependent
94 | MPPT7 Voltage | 0x1088 | 4232 | 1 | U16 | RO | 0.1V | Model-dependent
95 | MPPT7 Current | 0x1089 | 4233 | 1 | S16 | RO | 0.01A | Model-dependent
96 | MPPT7 Power | 0x108A | 4234 | 2 | U32 | RO | 0.1W | Model-dependent
97 | MPPT8 Voltage | 0x108C | 4236 | 1 | U16 | RO | 0.1V | Model-dependent
98 | MPPT8 Current | 0x108D | 4237 | 1 | S16 | RO | 0.01A | Model-dependent
99 | MPPT8 Power | 0x108E | 4238 | 2 | U32 | RO | 0.1W | Model-dependent
100 | MPPT9 Voltage | 0x1090 | 4240 | 1 | U16 | RO | 0.1V | Model-dependent
101 | MPPT9 Current | 0x1091 | 4241 | 1 | S16 | RO | 0.01A | Model-dependent
102 | MPPT9 Power | 0x1092 | 4242 | 2 | U32 | RO | 0.1W | Model-dependent
103 | External Fan Speed Duty % | 0x120C | 4620 | 1 | U16 | RO | 1%
104 | DER-AVM Digital Meter Connect | 0x1210 | 4624 | 1 | U16 | RO |  | 0=disconnected, 1=connected
105 | Q Reference Output Reactive | 0x1226 | 4646 | 1 | S16 | RO | 0.1kVAR
106 | L1 Watt of Grid | 0x1300 | 4864 | 2 | S32 | RO | 0.1W | +: Grid to inverter, -: Inverter to grid
107 | L2 Watt of Grid | 0x1302 | 4866 | 2 | S32 | RO | 0.1W | +: Grid to inverter, -: Inverter to grid
108 | L3 Watt of Grid | 0x1304 | 4868 | 2 | S32 | RO | 0.1W | +: Grid to inverter, -: Inverter to grid
109 | Accumulated Energy of Import | 0x1306 | 4870 | 2 | U32 | RO | 10Wh | Grid to inverter
110 | Accumulated Energy of Export | 0x1308 | 4872 | 2 | U32 | RO | 10Wh | Inverter to grid
111 | L1 Watt of Load | 0x130A | 4874 | 2 | U32 | RO | 0.1W
112 | L2 Watt of Load | 0x130C | 4876 | 2 | U32 | RO | 0.1W
113 | L3 Watt of Load | 0x130E | 4878 | 2 | U32 | RO | 0.1W
114 | Accumulated Energy of Load | 0x1310 | 4880 | 2 | U32 | RO | 10Wh
115 | L1-N Phase Voltage of Grid | 0x131A | 4890 | 1 | U16 | RO | 0.1V
116 | L2-N Phase Voltage of Grid | 0x131B | 4891 | 1 | U16 | RO | 0.1V
117 | L3-N Phase Voltage of Grid | 0x131C | 4892 | 1 | U16 | RO | 0.1V
118 | L1 Current of Grid | 0x131D | 4893 | 2 | S32 | RO | 0.01A | +: Grid to inverter, -: Inverter to grid
119 | L2 Current of Grid | 0x131F | 4895 | 2 | S32 | RO | 0.01A | +: Grid to inverter, -: Inverter to grid
120 | L3 Current of Grid | 0x1321 | 4897 | 2 | S32 | RO | 0.01A | +: Grid to inverter, -: Inverter to grid
121 | L1-N Phase Voltage of Load | 0x1323 | 4899 | 1 | U16 | RO | 0.1V
122 | L2-N Phase Voltage of Load | 0x1324 | 4900 | 1 | U16 | RO | 0.1V
123 | L3-N Phase Voltage of Load | 0x1325 | 4901 | 1 | U16 | RO | 0.1V
124 | L1 Current of Load | 0x1326 | 4902 | 2 | S32 | RO | 0.01A
125 | L2 Current of Load | 0x1328 | 4904 | 2 | S32 | RO | 0.01A
126 | L3 Current of Load | 0x132A | 4906 | 2 | S32 | RO | 0.01A
127 | Today Import Energy | 0x1332 | 4914 | 2 | U32 | RO | 10Wh
128 | Today Export Energy | 0x1334 | 4916 | 2 | U32 | RO | 10Wh
129 | Today Load Energy | 0x1336 | 4918 | 2 | U32 | RO | 10Wh
130 | Frequency of Grid | 0x1338 | 4920 | 1 | U16 | RO | 0.01Hz
131 | Tracker 1 Voltage | 0x8000 | 32768 | 64 | U16 | RO | 0.1V
132 | String 1-1 Current | 0x8040 | 32832 | 64 | S16 | RO | 0.01A
133 | String 1-2 Current | 0x8080 | 32896 | 64 | S16 | RO | 0.01A
134 | String 1-3 Current | 0x80C0 | 32960 | 64 | S16 | RO | 0.01A
135 | String 1-4 Current | 0x8100 | 33024 | 64 | S16 | RO | 0.01A
136 | Tracker 2 Voltage | 0x8140 | 33088 | 64 | U16 | RO | 0.1V
137 | String 2-1 Current | 0x8180 | 33152 | 64 | S16 | RO | 0.01A
138 | String 2-2 Current | 0x81C0 | 33216 | 64 | S16 | RO | 0.01A
139 | String 2-3 Current | 0x8200 | 33280 | 64 | S16 | RO | 0.01A
140 | String 2-4 Current | 0x8240 | 33344 | 64 | S16 | RO | 0.01A
141 | Tracker 3 Voltage | 0x8280 | 33408 | 64 | U16 | RO | 0.1V
142 | String 3-1 Current | 0x82C0 | 33472 | 64 | S16 | RO | 0.01A
143 | String 3-2 Current | 0x8300 | 33536 | 64 | S16 | RO | 0.01A
144 | String 3-3 Current | 0x8340 | 33600 | 64 | S16 | RO | 0.01A
145 | String 3-4 Current | 0x8380 | 33664 | 64 | S16 | RO | 0.01A
146 | Tracker 4 Voltage | 0x83C0 | 33728 | 64 | U16 | RO | 0.1V
147 | String 4-1 Current | 0x8400 | 33792 | 64 | S16 | RO | 0.01A
148 | String 4-2 Current | 0x8440 | 33856 | 64 | S16 | RO | 0.01A
149 | String 4-3 Current | 0x8480 | 33920 | 64 | S16 | RO | 0.01A
150 | String 4-4 Current | 0x84C0 | 33984 | 64 | S16 | RO | 0.01A
151 | Tracker 5 Voltage | 0x8500 | 34048 | 64 | U16 | RO | 0.1V
152 | String 5-1 Current | 0x8540 | 34112 | 64 | S16 | RO | 0.01A
153 | String 5-2 Current | 0x8580 | 34176 | 64 | S16 | RO | 0.01A
154 | String 5-3 Current | 0x85C0 | 34240 | 64 | S16 | RO | 0.01A
155 | String 5-4 Current | 0x8600 | 34304 | 64 | S16 | RO | 0.01A
156 | Tracker 6 Voltage | 0x8640 | 34368 | 64 | U16 | RO | 0.1V
157 | String 6-1 Current | 0x8680 | 34432 | 64 | S16 | RO | 0.01A
158 | String 6-2 Current | 0x86C0 | 34496 | 64 | S16 | RO | 0.01A
159 | String 6-3 Current | 0x8700 | 34560 | 64 | S16 | RO | 0.01A
160 | String 6-4 Current | 0x8740 | 34624 | 64 | S16 | RO | 0.01A
161 | Tracker 7 Voltage | 0x8780 | 34688 | 64 | U16 | RO | 0.1V
162 | String 7-1 Current | 0x87C0 | 34752 | 64 | S16 | RO | 0.01A
163 | String 7-2 Current | 0x8800 | 34816 | 64 | S16 | RO | 0.01A
164 | String 7-3 Current | 0x8840 | 34880 | 64 | S16 | RO | 0.01A
165 | String 7-4 Current | 0x8880 | 34944 | 64 | S16 | RO | 0.01A
166 | Tracker 8 Voltage | 0x88C0 | 35008 | 64 | U16 | RO | 0.1V
167 | String 8-1 Current | 0x8900 | 35072 | 64 | S16 | RO | 0.01A
168 | String 8-2 Current | 0x8940 | 35136 | 64 | S16 | RO | 0.01A
169 | String 8-3 Current | 0x8980 | 35200 | 64 | S16 | RO | 0.01A
170 | String 8-4 Current | 0x89C0 | 35264 | 64 | S16 | RO | 0.01A
171 | Tracker 9 Voltage | 0x8A00 | 35328 | 64 | U16 | RO | 0.1V
172 | String 9-1 Current | 0x8A40 | 35392 | 64 | S16 | RO | 0.01A
173 | String 9-2 Current | 0x8A80 | 35456 | 64 | S16 | RO | 0.01A
174 | String 9-3 Current | 0x8AC0 | 35520 | 64 | S16 | RO | 0.01A
175 | String 9-4 Current | 0x8B00 | 35584 | 64 | S16 | RO | 0.01A
176 | History Log 0 | 0xB600 | 46592 | 3 | U16 | RO |  | Query: 01 03 B6 00 00 03 23 83
177 | History Log 1~127 | 0xB603~0xB77D |  |  | U16 | RO |  | Pattern: 3 regs each, same format

## DEA_AVM_RealTime
Index | Definition | Address (Hex) | Address (Dec) | Register Number | Type | R/W | Unit | Comment / Notes
1 | L1 Current | 0x03E8 | 1000 | 2 | S32 | RO | 0.1A
2 | L2 Current | 0x03EA | 1002 | 2 | S32 | RO | 0.1A
3 | L3 Current | 0x03EC | 1004 | 2 | S32 | RO | 0.1A
4 | L1 Voltage | 0x03EE | 1006 | 2 | S32 | RO | 0.1V
5 | L2 Voltage | 0x03F0 | 1008 | 2 | S32 | RO | 0.1V
6 | L3 Voltage | 0x03F2 | 1010 | 2 | S32 | RO | 0.1V
7 | Grid Total Active Power | 0x03F4 | 1012 | 2 | S32 | RO | 0.1kW | L1+L2+L3
8 | Grid Total Reactive Power | 0x03F6 | 1014 | 2 | S32 | RO | Var | L1+L2+L3
9 | Power Factor | 0x03F8 | 1016 | 2 | S32 | RO | 0.001
10 | Frequency | 0x03FA | 1018 | 2 | S32 | RO | 0.1Hz
11 | Status Flag 1 | 0x03FC | 1020 | 2 | S32 | RO |  | Bit1: Inverter action, Bit2: CB action, Bit3: Run state, Bit4: Active power ctrl, Bit5: Inverter action ctrl

## Inverter_Params
Index | Definition | Address (Hex) | Address (Dec) | Register Number | Type | R/W | Unit | Comment / Notes
1 | DER-AVM Mode | 0x1211 | 4625 | 1 | U16 | RW |  | 0=self control, 1=DER-AVM control
2 | RS485-2 Modbus Address | 0x1240 | 4672 | 1 | U16 | RW |  | [1, 255]
3 | RS485-2 UART Baud Rate | 0x1241 | 4673 | 1 | U16 | RW |  | 3=9600, 4=14400, 5=19200, 6=38400
4 | RS485-2 Terminal Resistance | 0x1242 | 4674 | 1 | U16 | RW |  | 0=open, 1=close
5 | RS485-3 Modbus Address | 0x1243 | 4675 | 1 | U16 | RW |  | [1, 255]
6 | RS485-3 UART Baud Rate | 0x1244 | 4676 | 1 | U16 | RW |  | 3=9600, 4=14400, 5=19200, 6=38400
7 | RS485-3 Terminal Resistance | 0x1245 | 4677 | 1 | U16 | RW |  | 0=open, 1=close
8 | Nominal Voltage | 0x1A44 | 6724 | 1 | U16 | RW | 0.1V
9 | Date: Year | 0x3000 | 12288 | 1 | U16 | RW |  | [2000, 2099]
10 | Date: Month + Day | 0x3001 | 12289 | 1 | U16 | RW |  | High Byte=Month[1-12], Low Byte=Day[1-31]
11 | Date: Hour + Minute | 0x3002 | 12290 | 1 | U16 | RW |  | High Byte=Hour[0-23], Low Byte=Minute[0-59]
12 | Date: Second + 0 | 0x3003 | 12291 | 1 | U16 | RW |  | High Byte=Second[0-59], Low Byte=0
13 | Power Derating % by Modbus | 0x3005 | 12293 | 1 | U16 | RW |  | [0,110] Dynamic active power regulation
14 | RS485-1 Modbus Address | 0x303E | 12350 | 1 | U16 | RW |  | [1, 247] Default 1
15 | RS485-1 Baud Rate | 0x304C | 12364 | 1 | U16 | RW |  | 3=9600, 4=14400, 5=19200, 6=38400
16 | WIFI STA SSID | 0x3060 | 12384 | 16 | string | RW | ASCII
17 | WIFI STA Password | 0x3070 | 12400 | 16 | string | RW | ASCII
18 | Digital Meter Modbus Address | 0x30B0 | 12464 | 1 | U16 | RW |  | [1,255] Default 1
19 | Digital Meter Type | 0x30B1 | 12465 | 1 | U16 | RW |  | 0=Unknown,1=Gavazzi/EM340,2=CHINT/DTSU666,4=Lovato/DMG210,6=Gavazzi/ET112,8=CHINT/DDSU666,9=EM530,10=EM540
20 | Power Flow Direction | 0x30B2 | 12466 | 1 | U16 | RW |  | 0=Grid to inverter, 1=Inverter to grid
21 | Power Limit Function | 0x30B3 | 12467 | 1 | U16 | RW |  | 0=Disable,1=External device,2=PVI external CT,3=Digital meter
22 | Power Limit CT Ratio | 0x30B4 | 12468 | 1 | U16 | RW |  | 0=Unknown,1=1000:1,2=2000:1,3=2500:1,4=3000:1,5=4000:1,6=5000:1,7=6000:1,8=10000:1
23 | Meter Location | 0x30B5 | 12469 | 1 | U16 | RW |  | 0=CT on Grid, 1=CT on Load
24 | Maximum Feed-in Grid Power | 0x30B9 | 12473 | 2 | U32 | RW | W | [0, Pnom]
25 | First Connect Start Time | 0x5000 | 20480 | 1 | U16 | RW | s | [10, 600]
26 | Reconnect Time | 0x5001 | 20481 | 1 | U16 | RW | s | [10, 900]
27 | Grid Freq High Loss Lvl1 Limit | 0x5002 | 20482 | 1 | U16 | RW | 0.01Hz | 50Hz:[5001,5500], 60Hz:[6001,6500]
28 | Grid Freq Low Loss Lvl1 Limit | 0x5003 | 20483 | 1 | U16 | RW | 0.01Hz | 50Hz:[4500,4999], 60Hz:[5500,5999]
29 | Grid Volt High Loss Lvl1 Limit | 0x5004 | 20484 | 1 | U16 | RW | 0.1V | [1, 1.5]*Vnom
30 | Grid Volt Low Loss Lvl1 Limit | 0x5005 | 20485 | 1 | U16 | RW | 0.1V | [0.1, 1]*Vnom
31 | Grid Freq High Loss Lvl1 Trip Time | 0x5006 | 20486 | 1 | U16 | RW | 1ms | [0, 65535]
32 | Grid Freq Low Loss Lvl1 Trip Time | 0x5007 | 20487 | 1 | U16 | RW | 1ms | [0, 65535]
33 | Grid Volt High Loss Lvl1 Trip Time | 0x5008 | 20488 | 1 | U16 | RW | 1ms | [0, 65535]
34 | Grid Volt Low Loss Lvl1 Trip Time | 0x5009 | 20489 | 1 | U16 | RW | 1ms | [0, 65535]
35 | Grid Freq High Loss Lvl2 Limit | 0x500A | 20490 | 1 | U16 | RW | 0.01Hz | 50Hz:[5001,5500], 60Hz:[6001,6500]
36 | Grid Freq Low Loss Lvl2 Limit | 0x500B | 20491 | 1 | U16 | RW | 0.01Hz | 50Hz:[4500,4999], 60Hz:[5500,5999]
37 | Grid Volt High Loss Lvl2 Limit | 0x500C | 20492 | 1 | U16 | RW | 0.1V | [1, 1.5]*Vnom
38 | Grid Volt Low Loss Lvl2 Limit | 0x500D | 20493 | 1 | U16 | RW | 0.1V | [0.1, 1]*Vnom
39 | Grid Freq High Loss Lvl2 Trip Time | 0x500E | 20494 | 1 | U16 | RW | 1ms | [0, 65535]
40 | Grid Freq Low Loss Lvl2 Trip Time | 0x500F | 20495 | 1 | U16 | RW | 1ms | [0, 65535]
41 | Grid Volt High Loss Lvl2 Trip Time | 0x5010 | 20496 | 1 | U16 | RW | 1ms | [0, 65535]
42 | Grid Volt Low Loss Lvl2 Trip Time | 0x5011 | 20497 | 1 | U16 | RW | 1ms | [0, 65535]
43 | Grid Freq High Lvl1 Back | 0x5012 | 20498 | 1 | U16 | RW | 0.01Hz | 50Hz:[5001,5500], 60Hz:[6001,6500]
44 | Grid Freq Low Lvl1 Back | 0x5013 | 20499 | 1 | U16 | RW | 0.01Hz | 50Hz:[5001,5500], 60Hz:[6001,6500]
45 | 10 Min Avg Sustained Voltage | 0x5018 | 20504 | 1 | U16 | RW | 0.1V | [1, 1.5]*Vnom
46 | Reconnect Soft Output Power % | 0x5019 | 20505 | 1 | U16 | RW | %/min | [1,100]
47 | Over Freq Power Reduction Droop | 0x501A | 20506 | 1 | U16 | RW | 0.1%/Hz | [20,120]
48 | Insulation Resistance Active Limit | 0x501B | 20507 | 1 | U16 | RW | 1kΩ | [10,5000]
49 | Grid Over Voltage De-rating Point | 0x501E | 20510 | 1 | U16 | RW | 0.1V | [1, 1.5]*Vnom
50 | Grid Freq High Lvl1 Trip Time HW | 0x501F | 20511 | 1 | U16 | RW | ms | [0,15] High word
51 | Grid Freq Low Lvl1 Trip Time HW | 0x5020 | 20512 | 1 | U16 | RW | ms | [0,15] High word
52 | Grid Over Freq Derating Start | 0x5021 | 20513 | 1 | U16 | RW | 0.01Hz | 50Hz:[5001,5500], 60Hz:[6001,6500]
53 | Grid Over Freq Derating End | 0x5022 | 20514 | 1 | U16 | RW | 0.01Hz | 50Hz:[5001,5500], 60Hz:[6001,6500]
54 | Grid Volt High Lvl1 Trip Time HW | 0x5025 | 20517 | 1 | U16 | RW | ms | [0,9] High word
55 | Grid Volt Low Lvl1 Trip Time HW | 0x5026 | 20518 | 1 | U16 | RW | ms | [0,9] High word
56 | Grid Volt High Lvl1 Back | 0x5027 | 20519 | 1 | U16 | RW | 0.1V | [Vnom+1, Vnom*1.5]
57 | Grid Volt Low Lvl1 Back | 0x5028 | 20520 | 1 | U16 | RW | 0.1V | [0, Vnom-1]
58 | First Connect Soft Start Power % | 0x5029 | 20521 | 1 | U16 | RW | % | [1,100]
59 | Output Reactive Power Mode | 0x5030 | 20528 | 1 | U16 | RW |  | 0=Pure active,1=cosφ const,2=Q const,3=cosφ(P),4=Q(U),5=AUTO P(U),6=Watt(U),7=Q(U)AS4777,8=Q const P-pri,9=Q(P)
60 | Power Factor Setting | 0x5031 | 20529 | 1 | S16 | RW | 0.001 | [-1000,-800],[800,1000]
61 | Reactive Control Response Time | 0x5033 | 20531 | 1 | U16 | RW | s | [0,120]
62 | Q(U) Curve Node1 % (U/Un) | 0x503C | 20540 | 1 | U16 | RW | % | [80,120]
63 | Q(U) Curve Node2 % (U/Un) | 0x503D | 20541 | 1 | U16 | RW | % | [80,120]
64 | Q(U) Curve Node3 % (U/Un) | 0x503E | 20542 | 1 | U16 | RW | % | [80,120]
65 | Q(U) Curve Node4 % (U/Un) | 0x503F | 20543 | 1 | U16 | RW | % | [80,120]
66 | Q(U) Curve Node1 Value (Q/S) | 0x5040 | 20544 | 1 | S16 | RW | 0.1% | [-1100,1100]
67 | Q(U) Curve Node2 Value (Q/S) | 0x5041 | 20545 | 1 | S16 | RW | 0.1% | [-1100,1100]
68 | Q(U) Curve Node3 Value (Q/S) | 0x5042 | 20546 | 1 | S16 | RW | 0.1% | [-1100,1100]
69 | Q(U) Curve Node4 Value (Q/S) | 0x5043 | 20547 | 1 | S16 | RW | 0.1% | [-1100,1100]
70 | Volt-Watt Node1 Voltage | 0x504B | 20555 | 1 | U16 | RW | 0.1V | [0.8,1.5]*Vnom
71 | Volt-Watt Node2 Voltage | 0x504C | 20556 | 1 | U16 | RW | 0.1V | [0.8,1.5]*Vnom
72 | Volt-Watt Node1 Output Power % | 0x504F | 20559 | 1 | U16 | RW | % | [0,110]
73 | Volt-Watt Node2 Output Power % | 0x5050 | 20560 | 1 | U16 | RW | % | [0,110]
74 | Q(P) Curve Node1 % (P/Pn) | 0x505A | 20570 | 1 | U16 | RW | % | [0,100]
75 | Q(P) Curve Node2 % (P/Pn) | 0x505B | 20571 | 1 | U16 | RW | % | [0,100]
76 | Q(P) Curve Node3 % (P/Pn) | 0x505C | 20572 | 1 | U16 | RW | % | [0,100]
77 | Q(P) Curve Node4 % (P/Pn) | 0x505D | 20573 | 1 | U16 | RW | % | [0,100]
78 | Q(P) Curve Node1 Value (Q/Pn) | 0x505E | 20574 | 1 | S16 | RW | 0.10% | [-600,600]
79 | Q(P) Curve Node2 Value (Q/Pn) | 0x505F | 20575 | 1 | S16 | RW | 0.10% | [-600,600]
80 | Q(P) Curve Node3 Value (Q/Pn) | 0x5060 | 20576 | 1 | S16 | RW | 0.10% | [-600,600]
81 | Q(P) Curve Node4 Value (Q/Pn) | 0x5061 | 20577 | 1 | S16 | RW | 0.10% | [-600,600]
82 | LVRT Triggering Voltage | 0x5063 | 20579 | 1 | U16 | RW | 0.1V | [0.1,0.9]*Vnom
83 | HVRT Triggering Voltage | 0x5064 | 20580 | 1 | U16 | RW | 0.1V | [1.1,1.5]*Vnom
84 | FRT Mode | 0x5065 | 20581 | 1 | U16 | RW |  | 0=Zero current mode, 1=Full grid support mode
85 | FRT Zero Current Mode Threshold | 0x5066 | 20582 | 1 | U16 | RW | % | [5,150]
86 | FRT Grid Voltage Jump Threshold | 0x5067 | 20583 | 1 | U16 | RW | % | [5,150]
87 | Grid Freq High Lvl2 Trip Time HW | 0x506C | 20588 | 1 | U16 | RW | ms | [0,15] High word
88 | Grid Freq Low Lvl2 Trip Time HW | 0x506D | 20589 | 1 | U16 | RW | ms | [0,15] High word
89 | Grid Freq High Lvl3 Limit | 0x5070 | 20592 | 1 | U16 | RW | 0.01Hz | 50Hz:[5001,5500], 60Hz:[6001,6500]
90 | Grid Freq Low Lvl3 Limit | 0x5071 | 20593 | 1 | U16 | RW | 0.01Hz | 50Hz:[4500,4999], 60Hz:[5500,5999]
91 | Grid Volt High Lvl3 Limit | 0x5072 | 20594 | 1 | U16 | RW | 0.1V | [1,1.5]*Vnom
92 | Grid Volt Low Lvl3 Limit | 0x5073 | 20595 | 1 | U16 | RW | 0.1V | [0.1,1]*Vnom
93 | Grid Freq High Lvl3 Trip Time | 0x5074 | 20596 | 1 | U16 | RW | ms | [0,65535]
94 | Grid Freq Low Lvl3 Trip Time | 0x5075 | 20597 | 1 | U16 | RW | ms | [0,65535]
95 | Grid Volt High Lvl3 Trip Time | 0x5076 | 20598 | 1 | U16 | RW | ms | [0,65535]
96 | Grid Volt Low Lvl3 Trip Time | 0x5077 | 20599 | 1 | U16 | RW | ms | [0,65535]
97 | Over Freq Derating Ref Power | 0x507F | 20607 | 1 | U16 | RW |  | 0=rating power, 1=current power
98 | Grid Under Freq Rise Power Start | 0x5081 | 20609 | 1 | U16 | RW | 0.01Hz | 50Hz:[4500,4999], 60Hz:[5500,5999]
99 | Grid Under Freq Rise Power Stop | 0x5082 | 20610 | 1 | U16 | RW | 0.01Hz | 50Hz:[4500,4999], 60Hz:[5500,5999]
100 | Under Freq Rise Power Droop | 0x5083 | 20611 | 1 | U16 | RW | 0.001 | [20,120]
101 | Under Freq Rise Power Reference | 0x5084 | 20612 | 1 | U16 | RW |  | 0=rating power, 1=current power
102 | Regulation Code | 0x5101 | 20737 | 1 | U16 | RW |  | See Regulation Code Table
103 | Derating Watt Percent | 0x5104 | 20740 | 1 | U16 | RO | % | [0,110] % of nominal power
104 | MPPT Shadow Manage | 0x5106 | 20742 | 1 | U16 | RW |  | 0=disable, 1=enable
105 | MPPT Shadow Manage Interval Time | 0x5107 | 20743 | 1 | U16 | RW | s | [30,7200]
106 | Islanding Detection | 0x510E | 20750 | 1 | U16 | RW |  | 0=disable, 1=enable
107 | Ground Current Limit | 0x5110 | 20752 | 1 | U16 | RW | mA | [1, S*0.01]
108 | Low Voltage Through Detection | 0x5112 | 20754 | 1 | U16 | RW |  | 0=disable, 1=enable (3-phase only)
109 | Reactive Power Percent | 0x5114 | 20756 | 1 | S16 | RW | % | [-60,60] % of nominal. Do NOT use for dynamic regulation.
110 | RS485-1 Terminal Resistance | 0x5115 | 20757 | 1 | U16 | RW |  | 0=open, 1=close (3-phase only)
111 | Insulation Resistor Detection | 0x5117 | 20759 | 1 | U16 | RW |  | 0=disable, 1=enable
112 | Ground Current Detection | 0x5118 | 20760 | 1 | U16 | RW |  | 0=disable, 1=enable
113 | Grid High Voltage Load Derating | 0x511D | 20765 | 1 | U16 | RW |  | 0=disable, 1=enable. Related to 0x501E
114 | Reactive Power Percent (Fine) | 0x5121 | 20769 | 1 | S16 | RW | 0.01% | [-11000,11000]
115 | Fuse Open Check Mask | 0x513D | 20797 | 2 | U32 | RW |  | See Fuse Open Check Mask Table
116 | Inverter Control | 0x6001 | 24577 | 1 | U16 | RW |  | 0=power on, 1=shut down
117 | EEPROM Default | 0x6006 | 24582 | 1 | U16 | RW |  | 0=NOT default, 1=EEPROM to default
118 | Clear EEPROM History Energy | 0x6009 | 24585 | 1 | U16 | RW |  | 0=NOT clear, 1=Clear
119 | I-V Curve Scan | 0x600D | 24589 | 1 | U16 | RW |  | Write:0=Non-active,1=Active; Read:0=Idle,1=Running,2=Finished
120 | P.F (cosφ) Dynamic | 0x600F | 24591 | 1 | S16 | RW | 0.001 | [-1000,-800],[800,1000]. Dynamic PF regulation.
121 | Reactive Power Percent Dynamic | 0x6010 | 24592 | 1 | S16 | RW | 0.01% | [0,65535]. Dynamic reactive power regulation.

## DERAVM_Params
Index | Definition | Address (Hex) | Address (Dec) | Register Number | Type | R/W | Unit | Comment / Notes
1 | Power Factor Setting | 0x07D0 | 2000 | 1 | S16 | RW | 0.001 | [-1000,-800],[800,1000] Default 1000
2 | Action Mode | 0x07D1 | 2001 | 1 | U16 | RW |  | 0=self-control, 2=DER-AVM control, 5=Q(V)control. Default 2
3 | Reactive Power Percent Setting | 0x07D2 | 2002 | 1 | S16 | RW | 0.1% | [-484,484] Default 0
4 | Active Power Percent Setting | 0x07D3 | 2003 | 1 | U16 | RW | 0.1% | [0,1100] Default 1000
5 | Inverter Off | 0x0834 | 2100 | 1 | U16 | RW |  | 0=Inverter on, 1=Inverter off. Default 0
6 | Clear PV Insulation Warning | 0x0835 | 2101 | 1 | U16 | RW |  | 0=Non-active, 1=Clear PV insulation abnormal warning

## Error_Codes
Register | Bit No. | Error No. | Description
0x101E (Table1) | 0 | 16 | Inverter over dc-bias current
0x101E (Table1) | 1 | 17 | Inverter relay abnormal
0x101E (Table1) | 2 | 18 | Remote off
0x101E (Table1) | 3 | 19 | Inverter over temperature
0x101E (Table1) | 4 | 20 | GFCI abnormal
0x101E (Table1) | 5 | 21 | PV string reverse
0x101E (Table1) | 6 | 22 | System type error
0x101E (Table1) | 7 | 23 | Fan abnormal
0x101E (Table1) | 8 | 24 | Dc-link unbalance or under voltage
0x101E (Table1) | 9 | 25 | Dc-link over voltage
0x101E (Table1) | 10 | 26 | Internal communication error
0x101E (Table1) | 11 | 27 | Software incompatibility
0x101E (Table1) | 12 | 28 | Internal storage error
0x101E (Table1) | 13 | 29 | Data inconsistency
0x101E (Table1) | 14 | 30 | Inverter abnormal
0x101E (Table1) | 15 | 31 | Boost abnormal
0x101F (Table2) | 0 | 0 | Grid over voltage
0x101F (Table2) | 1 | 1 | Grid under voltage
0x101F (Table2) | 2 | 2 | Grid absent
0x101F (Table2) | 3 | 3 | Grid over frequency
0x101F (Table2) | 4 | 4 | Grid under frequency
0x101F (Table2) | 5 | 5 | PV over voltage
0x101F (Table2) | 6 | 6 | PV insulation abnormal
0x101F (Table2) | 7 | 7 | Leakage current abnormal
0x101F (Table2) | 8 | 8 | Inverter in power limit state
0x101F (Table2) | 9 | 9 | Internal power supply abnormal
0x101F (Table2) | 10 | 10 | PV string abnormal
0x101F (Table2) | 11 | 11 | PV under voltage
0x101F (Table2) | 12 | 12 | PV irradiation weak
0x101F (Table2) | 13 | 13 | Grid abnormal
0x101F (Table2) | 14 | 14 | Arc fault detection
0x101F (Table2) | 15 | 15 | AC moving average voltage high
0x1020 (Table3) | 0 | 32 | Reserved
0x1020 (Table3) | 1 | 33 | Logger/E-Display EEPROM fail
0x1020 (Table3) | 2 | 34 | Reserved
0x1020 (Table3) | 3 | 35 | Single tracker detect warning (PID device abnormal)
0x1020 (Table3) | 4 | 36 | AFCI lost
0x1020 (Table3) | 5 | 37 | Data logger lost
0x1020 (Table3) | 6 | 38 | Meter lost
0x1020 (Table3) | 7 | 39 | Inverter lost
0x1020 (Table3) | 8 | 40 | Grid N abnormal
0x1020 (Table3) | 9 | 41 | Surge Protection Devices (SPD) defective
0x1020 (Table3) | 10 | 42 | Parallel ID warning
0x1020 (Table3) | 11 | 43 | Parallel SYN signal warning
0x1020 (Table3) | 12 | 44 | Parallel BAT abnormal
0x1020 (Table3) | 13 | 45 | Parallel GRID abnormal
0x1020 (Table3) | 14 | 46 | Generator voltage abnormal
0x1020 (Table3) | 15 | 47 | Reserved

## Inverter_Mode
Mode Code | Description
0x00 | Initial mode
0x01 | Standby mode
0x03 | On-Grid mode
0x04 | Off-Grid mode
0x05 | Fault mode
0x09 | Shutdown mode

## Regulation_Codes
No. | Code (Hex) | Region | Standard
0 | 0xFFFF | UNKNOWN | UNKNOWN
1 | 0x0001 | AU | AS/NZS 4777.2 Region B
2 | 0x0002 | DE | VDE 0126-1-1/A1
3 | 0x0003 | TW | TW GRID
4 | 0x0004 | DE | VDE-AR-N 4105:2011
5 | 0x0005 | JP | JETGR0002-1-2.0
6 | 0x0006 | IT | CEI 0-21
7 | 0x0007 | SE | EIFS-2
8 | 0x0008 | UK | G98
9 | 0x0009 | UL | UL
10 | 0x000A | TH | PEA
11 | 0x000B | SE | SWEDEN GRID 2007
12 | 0x000C | NL | EN50549-1 2019
13 | 0x000D | TH | MEA
14 | 0x000E | CN | NB/T 32004
15 | 0x000F | IN | IEC61727
16 | 0x0010 | AU | AS/NZS 4777.2 Region A
17 | 0x0011 | NZ | AS/NZS 4777.2 New Zealand
18 | 0x0012 | US | IEEE1547
19 | 0x0013 | UA | VDE-AR-N 4105
20 | 0x0014 | TW | CNS 15382:2018
24 | 0x0018 | UK | G99 Type A
29 | 0x001D | DE | VDE-AR-N 4105:2018
31 | 0x001F | EU | EN50549-1:2019
43 | 0x002B | UK | G99 Type B
72 | 0x0048 | IRL | EN50549-1: Ireland

## Protocol_Cmd
Function Code | Command | Description | Example (Hex)
0x03 | Read Register | Read 1~124 registers. Host→Slave→Host | Host: 01 03 10 01 00 01 D1 0A Reply: 01 03 02 08 FC BF C5 Error: 01 83 02 C0 F1
0x06 | Write Single Register | Write one register. Host→Slave echo | Host: 01 06 51 01 00 01 09 36 Reply: 01 06 51 01 00 01 09 36 Error: 01 86 04 43 A3
0x10 | Write Multiple Registers | Write 1~122 registers | Host: 01 10 30 00 00 04 08 07 E1 01 01 00 00 00 00 7B 73 Reply: 01 10 30 00 00 04 CE CA
0x7E | REMS Read Register | REMS specific read. No slave address in query frame | Host: 7E 01 07 51 8A Reply: 7E 01 08 00 26 ... (38 bytes data)