## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Kstar
프로토콜 버전 | V3.5
설비 타입 | inverter
MPPT | 6
String | 24
String 모니터링 | Yes
IV Scan | Yes
IV Data Points | 100
IV Trackers | 2
원본 파일 | Kstar-PV_KSG1250K_Modbus_Protocol_v35.pdf
추출 일시 | 2026-04-09 12:07
H01 매칭 | 54/54
DER 매칭 | 33/33
추출 레지스터 | 432
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | PBUS_VOLTAGE | 0x0BC4 | 04 | U16 | V 0.1 | RO |  | PBUS voltage
2 | NBUS_VOLTAGE | 0x0BC5 | 04 | U16 | V 0.1 | RO |  | 1-5K not have. ¦ 1-5K not have.
3 | INNER_TEMP | 0x0BD1 | 04 | S16 |  | RO | temperature | Radiator temperature
4 | INNER_TEMP | 0x0BD2 | 04 | S16 |  | RO | temperature | Module temperature ¦ 1-5K not have.
5 | Daily energy yield | 0x0BE2 | 04 | U16 | Kwh | RO | cumulative_energy
6 | APPARENT_POWER | 0x0BEC | 04 | S32 | VA 1 | RO |  | Apparent power
7 | DC_INSULATION_RESISTANCE | 0x0BF1 | 04 | U16 |  | RO |  | DC insulation resistance ¦ 1-5K not have.
8 | R_PHASE_VOLTAGE_CALIBRATION_FACTOR | 0x0C3D | 04 | U16 |  | RO |  | R-phase VoltageCalibration Factor ¦ Default：4096
9 | S_PHASE_VOLTAGE_CALIBRATION_FACTOR | 0x0C3E | 04 | U16 |  | RO |  | S-phase VoltageCalibration Factor ¦ Default：4096
10 | T_PHASE_VOLTAGE_CALIBRATION_FACTOR | 0x0C3F | 04 | U16 |  | RO |  | T-phase VoltageCalibration Factor ¦ Default：4096
11 | R_PHASE_CURRENT_CALIBRATION_FACTOR | 0x0C40 | 04 | U16 |  | RO |  | R-phase CurrentCalibration Factor ¦ Default：4096
12 | S-phase Calibration Factor | 0x0C41 | 04 | U16 |  | RO |  | Default：4096
13 | SETTING_VALUE_OF_RATEDPOWER_FOR_ANTI_BACKFLOW | 0x0C7C | 04 | U16 |  | RO |  | Setting value of ratedpower for anti backflow
14 | Machine model | 0x0C80 | 04 | ASCII |  | RO |  | ASCII code
15 | LCD Model Setting | 0x0C94 | 04 | U16 |  | RO |  | Table 3.3.5
16 | Inverter Model（New） | 0x0C95 | 04 | ASCII |  | RO |  | ASCII character
17 | R_PHASE_VOLTAGECALIBRATIONCOEFFICIENT_2 | 0x0CB3 | 04 | U16 |  | RO |  | R-phase voltagecalibrationcoefficient 2
18 | Setting Inverter SN | 0x0CEF | 04 | ASCII |  | RO
19 | LCD Model Setting | 0x0D04 | 04 | U16 |  | RO
20 | DEVICE_MODEL | 0x0D05 | 04 | U16 |  | RO |  | Inverter Model
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INVERTER_MODE | 0x0BD6 | 04 | U16 |  | RO | inverter_status | Operating mode of theinverter ¦ Table 3.1.4
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | AC_RELAY_FAULT | 0x000E | 04 | U16 |  | RO |  | AC Relay Fault
2 | GFCI Over Fault | 0x0014 | 04 | U16 |  | RO
3 | GFCI Device Fault | 0x0015 | 04 | U16 |  | RO
4 | Voltage Consistent Fault | 0x0016 | 04 | U16 |  | RO
5 | Frequency Consistent Fault | 0x0017 | 04 | U16 |  | RO
6 | IGBT Fault | 0x001A | 04 | U16 |  | RO
7 | NPE Volte Fault | 0x001B | 04 | U16 |  | RO
8 | DC over volt serious fault | 0x001C | 04 | U16 |  | RO
9 | IGBT serious fault | 0x001D | 04 | U16 |  | RO
10 | DSP_ALARM_CODE | 0x0BD3 | 04 | U16 |  | RO |  | DSP alarm code ¦ Table 3.1.2
11 | DSP_ERROR_CODE | 0x0BD4 | 04 | U32 |  | RO |  | DSP error code ¦ Table 3.1.3
12 | ARM_ALARM_CODE | 0x0BDC | 04 | U16 |  | RO |  | ARM alarm code ¦ Table 3.1.6
13 | Default value：10: prohibit 1:permit | 0x0C44 | 04 | U16 |  | RO |  | Default value：10: prohibit 1:permit
14 | Default value：1 | 0x0C7A | 04 | U16 |  | RO
15 | 0：Default value1：HaixingCustomization Format | 0x0C7B | 04 | U16 |  | RO
16 | scope 0.60-3.00A，Default value 1.20A | 0x0C7D | 04 | U16 | A 0.01 | RO
17 | scope 0.10-0.50A，Default value 0.30A | 0x0C7E | 04 | U16 | A 0.01 | RO
18 | FUSE_ALARM_INFORMATION | 0x0C81 | 04 | U32 |  | RO |  | Fuse alarm information
19 | OVER_TEMPERATUREDERATING_WARNINGENABLE | 0x0C9B | 04 | U16 |  | RO |  | Over temperaturederating warningenable
20 | scope：0~100Default value：50 | 0x0CA3 | 04 | U16 |  | RO
21 | scope：0~100Default value：50 | 0x0CA4 | 04 | U16 |  | RO
22 | FAULT_RECOVERY_TIME | 0x0CB0 | 04 | U16 |  | RO |  | 0~1800 Default value20s
23 | 0-20 ,the default is 4 | 0x0FA9 | 04 | U16 |  | RO
24 | CLEAR_FAULT_RECORD | 0x0FC1 | 04 | U16 |  | RO |  | DATA arbitrary number
25 | CANCEL_POWER_FACTOR_CONTROL_DEFAULTPOWER_FACTOR_1 | 0xFFFF | 04 | U16 |  | RO |  | For Engineer UseOnly

## 2_H01
H01 모니터링 매칭 — 54/54
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | PDF_PHASE | O | 0x0BC6 | L1_VOLTAGE | U16 | V | 0.1 | 상전압 사용
2 | s_voltage | PDF_PHASE | O | 0x0BC7 | L2_VOLTAGE | U16 | V | 0.1 | 상전압 사용
3 | t_voltage | PDF_PHASE | O | 0x0BC8 | L3_VOLTAGE | U16 | V | 0.1 | 상전압 사용
4 | r_current | PDF_PHASE | O | 0x0BCC | L1_CURRENT | U16 | A | 0.01 | 상전압 사용
5 | s_current | PDF_PHASE | O | 0x0BCD | L2_CURRENT | U16 | A | 0.01 | 상전압 사용
6 | t_current | PDF_PHASE | O | 0x0BCE | L3_CURRENT | U16 | A | 0.01 | 상전압 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x0B96 | PV_POWER | S32 | W | 1
13 | cumulative_energy | PDF | O | 0x0BDE | CUMULATIVE_ENERGY | U32 | Kwh | 0.1 | Kwh→Wh (*1000)
14 | cumulative_energy_low | PDF_ALIAS | O | 0x0BDE | CUMULATIVE_ENERGY | U32 | Kwh | 0.1 | cumulative_energy alias (단일 레지스터에 통합값)
15 | status | PDF | O | 0x0BD6 | INVERTER_MODE | U16 |  |  | 0=System initiali, 1=Waiting, 2=Pre-detection, 3=Normal, 4=Error, 5=Permanent error... (+4)
16 | alarm1 | PDF | O | 0x0BD3 | DSP_ALARM_CODE | U16 |  |  | 16=Remote Off, 17=reserve, 18=SPI Communicati, 19=SPI2 Communicat, 20=GFCI Over Fault, 21=GFCI Device Fau... (+10)
17 | alarm2 | PDF | O | 0x0BD4 | DSP_ERROR_CODE | U32 |  |  | 2990=PV6 input power, 2991=04H, 2992=PV5 input volta, 2993=PV5 input curre, 2994=PV5 input power, 2995=04H... (+30)
18 | alarm3 | PDF | O | 0x0BDC | ARM_ALARM_CODE | U16
19 | mppt1_voltage | PDF | O | 0x0BB8 | PV1 input voltage | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x0BBB | PV1 input current | U16 | A | 0.01
21 | mppt2_voltage | PDF | O | 0x0BB9 | PV2 input voltage | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x0BBC | PV2 input current | U16 | A | 0.01
23 | mppt3_voltage | PDF | O | 0x0BBA | PV3 input voltage | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x0BBD | PV3 input current | U16 | A | 0.01
25 | mppt4_voltage | PDF | O | 0x0BB4 | PV4 input voltage | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x0BB5 | PV4 input current | S16 | A | 0.01
27 | mppt5_voltage | PDF | O | 0x0BB0 | PV5 input voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x0BB1 | PV5 input current | S16 | A | 0.01
29 | mppt6_voltage | PDF | O | 0x0BAC | PV6 input voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x0BAD | PV6 input current | S16 | A | 0.01
31 | string1_current | HANDLER | O | 0x0BBB | PV1 input current | U16 | A | 0.01
32 | string2_current | PDF | O | 0x0BF9 | PV1 String current 2 | S16 | A | 0.01
33 | string3_current | PDF | O | 0x0BFA | PV1 String current 3 | S16 | A | 0.01
34 | string4_current | PDF | O | 0x0BFB | PV1 String current 4 | S16 | A | 0.01
35 | string5_current | PDF | O | 0x0BFC | PV2 String current 1 | S16 | A | 0.01
36 | string6_current | PDF | O | 0x0BFD | PV2 String current 2 | S16 | A | 0.01
37 | string7_current | PDF | O | 0x0BFE | PV2 String current 3 | S16 | A | 0.01
38 | string8_current | PDF | O | 0x0BFF | PV2 String current 4 | S16 | A | 0.01
39 | string9_current | PDF | O | 0x0C00 | PV3 String current 1 | S16 | A | 0.01
40 | string10_current | PDF | O | 0x0C01 | PV3 String current 2 | S16 | A | 0.01
41 | string11_current | PDF | O | 0x0C02 | PV3 String current 3 | S16 | A | 0.01
42 | string12_current | PDF | O | 0x0C03 | PV3 String current 4 | S16 | A | 0.01
43 | string13_current | PDF | O | 0x0C04 | PV4 String current 1 | S16 | A | 0.01
44 | string14_current | PDF | O | 0x0C05 | PV4 String current 2 | S16 | A | 0.01
45 | string15_current | PDF | O | 0x0C06 | PV4 String current 3 | S16 | A | 0.01
46 | string16_current | PDF | O | 0x0C07 | PV4 String current 4 | S16 | A | 0.01
47 | string17_current | PDF | O | 0x0C08 | PV5 String current 1 | S16 | A | 0.01
48 | string18_current | PDF | O | 0x0C09 | PV5 String current 2 | S16 | A | 0.01
49 | string19_current | PDF | O | 0x0C0A | PV5 String current 3 | S16 | A | 0.01
50 | string20_current | PDF | O | 0x0C0B | PV5 String current 4 | S16 | A | 0.01
51 | string21_current | PDF | O | 0x0C0C | PV6 String current 1 | S16 | A | 0.01
52 | string22_current | PDF | O | 0x0C0D | PV6 String current 2 | S16 | A | 0.01
53 | string23_current | PDF | O | 0x0C0E | PV6 String current 3 | S16 | A | 0.01
54 | string24_current | PDF | O | 0x0C0F | PV6 String current 4 | S16 | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 6ch / String 24ch
MPPT 채널 수 | 6
String 채널 수 | 24
String 모니터링 | Yes
MPPT 채널 H01 매칭 (12개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x0BB8 | PV1 input voltage | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x0BBB | PV1 input current | U16 | A | 0.01
3 | mppt2_voltage | PDF | O | 0x0BB9 | PV2 input voltage | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x0BBC | PV2 input current | U16 | A | 0.01
5 | mppt3_voltage | PDF | O | 0x0BBA | PV3 input voltage | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x0BBD | PV3 input current | U16 | A | 0.01
7 | mppt4_voltage | PDF | O | 0x0BB4 | PV4 input voltage | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x0BB5 | PV4 input current | S16 | A | 0.01
9 | mppt5_voltage | PDF | O | 0x0BB0 | PV5 input voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x0BB1 | PV5 input current | S16 | A | 0.01
11 | mppt6_voltage | PDF | O | 0x0BAC | PV6 input voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x0BAD | PV6 input current | S16 | A | 0.01
String 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | 0x0BBB | PV1 input current | U16 | A | 0.01
2 | string2_current | PDF | O | 0x0BF9 | PV1 String current 2 | S16 | A | 0.01
3 | string3_current | PDF | O | 0x0BFA | PV1 String current 3 | S16 | A | 0.01
4 | string4_current | PDF | O | 0x0BFB | PV1 String current 4 | S16 | A | 0.01
5 | string5_current | PDF | O | 0x0BFC | PV2 String current 1 | S16 | A | 0.01
6 | string6_current | PDF | O | 0x0BFD | PV2 String current 2 | S16 | A | 0.01
7 | string7_current | PDF | O | 0x0BFE | PV2 String current 3 | S16 | A | 0.01
8 | string8_current | PDF | O | 0x0BFF | PV2 String current 4 | S16 | A | 0.01
9 | string9_current | PDF | O | 0x0C00 | PV3 String current 1 | S16 | A | 0.01
10 | string10_current | PDF | O | 0x0C01 | PV3 String current 2 | S16 | A | 0.01
11 | string11_current | PDF | O | 0x0C02 | PV3 String current 3 | S16 | A | 0.01
12 | string12_current | PDF | O | 0x0C03 | PV3 String current 4 | S16 | A | 0.01
13 | string13_current | PDF | O | 0x0C04 | PV4 String current 1 | S16 | A | 0.01
14 | string14_current | PDF | O | 0x0C05 | PV4 String current 2 | S16 | A | 0.01
15 | string15_current | PDF | O | 0x0C06 | PV4 String current 3 | S16 | A | 0.01
16 | string16_current | PDF | O | 0x0C07 | PV4 String current 4 | S16 | A | 0.01
17 | string17_current | PDF | O | 0x0C08 | PV5 String current 1 | S16 | A | 0.01
18 | string18_current | PDF | O | 0x0C09 | PV5 String current 2 | S16 | A | 0.01
19 | string19_current | PDF | O | 0x0C0A | PV5 String current 3 | S16 | A | 0.01
20 | string20_current | PDF | O | 0x0C0B | PV5 String current 4 | S16 | A | 0.01
21 | string21_current | PDF | O | 0x0C0C | PV6 String current 1 | S16 | A | 0.01
22 | string22_current | PDF | O | 0x0C0D | PV6 String current 2 | S16 | A | 0.01
23 | string23_current | PDF | O | 0x0C0E | PV6 String current 3 | S16 | A | 0.01
24 | string24_current | PDF | O | 0x0C0F | PV6 String current 4 | S16 | A | 0.01
MONITORING 전체 (343개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Fan A Lock | 0x0000 | 04 | U16 | A | RO | power_factor
2 | Invalid function code | 0x0001 | 04 | U16 |  | RO
3 | Bytecount | 0x0001 |  | U16 |  | RO
4 | Invalid data address | 0x0002 | 04 | U16 |  | RO
5 | PV Parallel Open | 0x0007 | 04 | U16 |  | RO
6 | NULL | 0x0008 | 04 | U16 |  | RO
7 | Hard Inverter Current Over | 0x0009 | 04 | U16 |  | RO
8 | Inverter Current Over | 0x000A | 04 | U16 |  | RO
9 | Inverter Dc Currernt Over | 0x000B | 04 | U16 |  | RO
10 | AMBIENT_TEMPERATURE_OVER | 0x000C | 04 | U16 |  | RO
11 | SINK_TEMPERATURE_OVER | 0x000D | 04 | U16 |  | RO
12 | RESERVE | 0x000F | 04 | U16 |  | RO
13 | Remote Off | 0x0010 | 04 | U16 |  | RO
14 | reserve | 0x0011 | 04 | U16 |  | RO
15 | SPI Communication Fail | 0x0012 | 04 | U16 |  | RO
16 | SPI2 Communication Fail | 0x0013 | 04 | U16 |  | RO
17 | Reserve | 0x0018 | 04 | U16 |  | RO
18 | Auxiliary power off | 0x0019 | 04 | U16 |  | RO
19 | Reserve | 0x001E | 04 | U16 |  | RO
20 | Reserve | 0x001F | 04 | U16 |  | RO
21 | BluE-G 3000D | 0x0065 | 04 | U16 |  | RO
22 | BluE-G 3600D | 0x0066 | 04 | U16 |  | RO
23 | BluE-G 4000D | 0x0067 | 04 | U16 |  | RO
24 | BluE-G 4200D | 0x0068 | 04 | U16 |  | RO
25 | BluE-G 4600D | 0x0069 | 04 | U16 |  | RO
26 | BluE-G 5000D | 0x006A | 04 | U16 |  | RO
27 | BluE-G 6000D | 0x006B | 04 | U16 |  | RO
28 | BluE-3KT-M0 | 0x006E | 04 | U16 |  | RO
29 | BluE-3KT-M1 | 0x006F | 04 | U16 |  | RO
30 | BluE-3.6KT-M0 | 0x0070 | 04 | U16 |  | RO
31 | BluE-3.6KT-M1 | 0x0071 | 04 | U16 |  | RO
32 | BluE-4KT-M0 | 0x0072 | 04 | U16 |  | RO
33 | BluE-4KT-M1 | 0x0073 | 04 | U16 |  | RO
34 | BluE-5KT-M0 | 0x0074 | 04 | U16 |  | RO
35 | BluE-5KT-M1 | 0x0075 | 04 | U16 |  | RO
36 | BluE-6KT-M0 | 0x0076 | 04 | U16 |  | RO
37 | BluE-6KT-M1 | 0x0077 | 04 | U16 |  | RO
38 | BluE-8KT-M0 | 0x0078 | 04 | U16 |  | RO
39 | BluE-8KT-M1 | 0x0079 | 04 | U16 |  | RO
40 | BluE-10KT-M0 | 0x007A | 04 | U16 |  | RO
41 | BluE-10KT-M1 | 0x007B | 04 | U16 |  | RO
42 | BluE-12KT-M0 | 0x007C | 04 | U16 |  | RO
43 | BluE-12KT-M1 | 0x007D | 04 | U16 |  | RO
44 | BluE-15KT-M0 | 0x007E | 04 | U16 |  | RO
45 | BluE-15KT-M1 | 0x007F | 04 | U16 |  | RO
46 | BluE-15KT-M2 | 0x0080 | 04 | U16 |  | RO
47 | BluE-15KT-M3 | 0x0081 | 04 | U16 |  | RO
48 | BluE-17KT-M0 | 0x0082 | 04 | U16 |  | RO
49 | BluE-17KT-M1 | 0x0083 | 04 | U16 |  | RO
50 | BluE-20KT-M0 | 0x0084 | 04 | U16 |  | RO
51 | BluE-20KT-M1 | 0x0085 | 04 | U16 |  | RO
52 | BluE-22KT-M0 | 0x0086 | 04 | U16 |  | RO
53 | BluE-22KT-M1 | 0x0087 | 04 | U16 |  | RO
54 | BluE-23KT-M0 | 0x0088 | 04 | U16 |  | RO
55 | BluE-23KT-M1 | 0x0089 | 04 | U16 |  | RO
56 | BluE-25KT-M0 | 0x008A | 04 | U16 |  | RO
57 | BluE-25KT-M1 | 0x008B | 04 | U16 |  | RO
58 | G80KT | 0x00A8 | 04 | U16 |  | RO
59 | G80KT1 | 0x00A9 | 04 | U16 |  | RO
60 | G75KT | 0x00AA | 04 | U16 |  | RO
61 | G75KT1 | 0x00AB | 04 | U16 |  | RO
62 | G70KT | 0x00AC | 04 | U16 |  | RO
63 | G70KT1 | 0x00AD | 04 | U16 |  | RO
64 | G60KT | 0x00AE | 04 | U16 |  | RO
65 | G60KT1 | 0x00AF | 04 | U16 |  | RO
66 | G50KT | 0x00B0 | 04 | U16 |  | RO
67 | G50KT1 | 0x00B1 | 04 | U16 |  | RO
68 | G40KT | 0x00B2 | 04 | U16 |  | RO
69 | G40KT1 | 0x00B3 | 04 | U16 |  | RO
70 | G40KT2 | 0x00B4 | 04 | U16 |  | RO
71 | G40KT3 | 0x00B5 | 04 | U16 |  | RO
72 | BluE-3KT-M3 | 0x00C9 | 04 | U16 |  | RO
73 | BluE-3KT-M4 | 0x00CA | 04 | U16 |  | RO
74 | BluE-3KT-M5 | 0x00CB | 04 | U16 |  | RO
75 | BluE-3.6KT-M2 | 0x00CC | 04 | U16 |  | RO
76 | BluE-3.6KT-M3 | 0x00CD | 04 | U16 |  | RO
77 | BluE-3.6KT-M4 | 0x00CE | 04 | U16 |  | RO
78 | BluE-3.6KT-M5 | 0x00CF | 04 | U16 |  | RO
79 | BluE-4KT-M2 | 0x00D0 | 04 | U16 |  | RO
80 | BluE-4KT-M3 | 0x00D1 | 04 | U16 |  | RO
81 | BluE-4KT-M4 | 0x00D2 | 04 | U16 |  | RO
82 | BluE-4KT-M5 | 0x00D3 | 04 | U16 |  | RO
83 | BluE-5KT-M2 | 0x00D4 | 04 | U16 |  | RO
84 | BluE-5KT-M3 | 0x00D5 | 04 | U16 |  | RO
85 | BluE-5KT-M4 | 0x00D6 | 04 | U16 |  | RO
86 | BluE-5KT-M5 | 0x00D7 | 04 | U16 |  | RO
87 | BluE-6KT-M2 | 0x00D8 | 04 | U16 |  | RO
88 | BluE-6KT-M3 | 0x00D9 | 04 | U16 |  | RO
89 | BluE-6KT-M4 | 0x00DA | 04 | U16 |  | RO
90 | BluE-6KT-M5 | 0x00DB | 04 | U16 |  | RO
91 | BluE-8KT-M2 | 0x00DC | 04 | U16 |  | RO
92 | BluE-8KT-M3 | 0x00DD | 04 | U16 |  | RO
93 | BluE-8KT-M4 | 0x00DE | 04 | U16 |  | RO
94 | BluE-8KT-M5 | 0x00DF | 04 | U16 |  | RO
95 | BluE-10KT-M2 | 0x00E0 | 04 | U16 |  | RO
96 | BluE-10KT-M3 | 0x00E1 | 04 | U16 |  | RO
97 | BluE-10KT-M4 | 0x00E2 | 04 | U16 |  | RO
98 | BluE-10KT-M5 | 0x00E3 | 04 | U16 |  | RO
99 | BluE-12KT-M2 | 0x00E4 | 04 | U16 |  | RO
100 | BluE-12KT-M3 | 0x00E5 | 04 | U16 |  | RO
101 | BluE-12KT-M4 | 0x00E6 | 04 | U16 |  | RO
102 | BluE-12KT-M5 | 0x00E7 | 04 | U16 |  | RO
103 | BluE-15KT-M4 | 0x00E8 | 04 | U16 |  | RO
104 | BluE-15KT-M5 | 0x00E9 | 04 | U16 |  | RO
105 | BluE-17KT-M2 | 0x00EA | 04 | U16 |  | RO
106 | BluE-17KT-M3 | 0x00EB | 04 | U16 |  | RO
107 | BluE-17KT-M4 | 0x00EC | 04 | U16 |  | RO
108 | BluE-17KT-M5 | 0x00ED | 04 | U16 |  | RO
109 | BluE-20KT-M2 | 0x00EE | 04 | U16 |  | RO
110 | BluE-20KT-M3 | 0x00EF | 04 | U16 |  | RO
111 | BluE-20KT-M4 | 0x00F0 | 04 | U16 |  | RO
112 | BluE-20KT-M5 | 0x00F1 | 04 | U16 |  | RO
113 | BluE-22KT-M2 | 0x00F2 | 04 | U16 |  | RO
114 | BluE-22KT-M3 | 0x00F3 | 04 | U16 |  | RO
115 | BluE-22KT-M4 | 0x00F4 | 04 | U16 |  | RO
116 | BluE-22KT-M5 | 0x00F5 | 04 | U16 |  | RO
117 | BluE-23KT-M2 | 0x00F6 | 04 | U16 |  | RO
118 | BluE-23KT-M3 | 0x00F7 | 04 | U16 |  | RO
119 | BluE-23KT-M4 | 0x00F8 | 04 | U16 |  | RO
120 | BluE-23KT-M5 | 0x00F9 | 04 | U16 |  | RO
121 | BluE-25KT-M2 | 0x00FA | 04 | U16 |  | RO
122 | BluE-25KT-M3 | 0x00FB | 04 | U16 |  | RO
123 | BluE-25KT-M4 | 0x00FC | 04 | U16 |  | RO
124 | BluE-25KT-M5 | 0x00FD | 04 | U16 |  | RO
125 | QV Curve Reactive PowerUndervoltage End Value | 0x02BC | 04 | U16 | % 0.1 | RO
126 | QV Curve Reactive PowerOvervoltage End Value | 0x0514 | 04 | U16 | % 0.1 | RO
127 | PV12 input voltage | 0x0B94 | 04 | U16 | V 0.1 | RO | mppt12_voltage
128 | PV12 input current | 0x0B95 | 04 | S16 | A 0.01 | RO | mppt12_current
129 | PV_POWER | 0x0B96 | 04 | S32 | W 1 | RO | pv_power
130 | PV11 input voltage | 0x0B98 | 04 | U16 | V 0.1 | RO | mppt11_voltage
131 | PV11 input current | 0x0B99 | 04 | S16 | A 0.01 | RO | mppt11_current
132 | PV11 input power | 0x0B9A | 04 | S32 | W 1 | RO | mppt11_power
133 | PV10 input voltage | 0x0B9C | 04 | U16 | V 0.1 | RO | mppt10_voltage
134 | PV10 input current | 0x0B9D | 04 | S16 | A 0.01 | RO | mppt10_current
135 | PV10 input power | 0x0B9E | 04 | S32 | W 1 | RO | mppt10_power
136 | PV9 input voltage | 0x0BA0 | 04 | U16 | V 0.1 | RO | mppt9_voltage
137 | PV9 input current | 0x0BA1 | 04 | S16 | A 0.01 | RO | mppt9_current
138 | PV9 input power | 0x0BA2 | 04 | S32 | W 1 | RO | mppt9_power
139 | PV8 input voltage | 0x0BA4 | 04 | U16 | V 0.1 | RO | mppt8_voltage
140 | PV8 input current | 0x0BA5 | 04 | S16 | A 0.01 | RO | mppt8_current
141 | PV8 input power | 0x0BA6 | 04 | S32 | W 1 | RO | mppt8_power
142 | PV7 input voltage | 0x0BA8 | 04 | U16 | V 0.1 | RO | mppt7_voltage
143 | PV7 input current | 0x0BA9 | 04 | S16 | A 0.01 | RO | mppt7_current
144 | PV7 input power | 0x0BAA | 04 | S32 | W 1 | RO | mppt7_power
145 | PV6 input voltage | 0x0BAC | 04 | U16 | V 0.1 | RO | mppt6_voltage
146 | PV6 input current | 0x0BAD | 04 | S16 | A 0.01 | RO | mppt6_current
147 | PV6 input power | 0x0BAE | 04 | S32 | W 1 | RO | mppt6_power
148 | PV5 input voltage | 0x0BB0 | 04 | U16 | V 0.1 | RO | mppt5_voltage
149 | PV5 input current | 0x0BB1 | 04 | S16 | A 0.01 | RO | mppt5_current
150 | PV5 input power | 0x0BB2 | 04 | S32 | W 1 | RO | mppt5_power
151 | PV4 input voltage | 0x0BB4 | 04 | U16 | V 0.1 | RO | mppt4_voltage
152 | PV4 input current | 0x0BB5 | 04 | S16 | A 0.01 | RO | mppt4_current
153 | PV4 input power | 0x0BB6 | 04 | S32 | W 1 | RO | mppt4_power
154 | PV1 input voltage | 0x0BB8 | 04 | U16 | V 0.1 | RO | mppt1_voltage
155 | PV2 input voltage | 0x0BB9 | 04 | U16 | V 0.1 | RO | mppt2_voltage
156 | PV3 input voltage | 0x0BBA | 04 | U16 | V 0.1 | RO | mppt3_voltage
157 | PV1 input current | 0x0BBB | 04 | U16 | A 0.01 | RO | mppt1_current
158 | PV2 input current | 0x0BBC | 04 | U16 | A 0.01 | RO | mppt2_current
159 | PV3 input current | 0x0BBD | 04 | U16 | A 0.01 | RO | mppt3_current
160 | PV1 input power | 0x0BBE | 04 | S32 | W 1 | RO | mppt1_power
161 | PV2 input power | 0x0BC0 | 04 | S32 | W 1 | RO | mppt2_power
162 | PV3 input power | 0x0BC2 | 04 | S32 | W 1 | RO | mppt3_power
163 | L1_VOLTAGE | 0x0BC6 | 04 | U16 | V 0.1 | RO | r_voltage
164 | L2_VOLTAGE | 0x0BC7 | 04 | U16 | V 0.1 | RO | s_voltage
165 | L3_VOLTAGE | 0x0BC8 | 04 | U16 | V 0.1 | RO | t_voltage
166 | FREQUENCY | 0x0BC9 | 04 | U16 | Hz 0.01 | RO | frequency
167 | L2_FREQUENCY | 0x0BCA | 04 | U16 | Hz 0.01 | RO | frequency
168 | L3_FREQUENCY | 0x0BCB | 04 | U16 | Hz 0.01 | RO | frequency
169 | L1_CURRENT | 0x0BCC | 04 | U16 | A 0.01 | RO | r_current
170 | L2_CURRENT | 0x0BCD | 04 | U16 | A 0.01 | RO | s_current
171 | L3_CURRENT | 0x0BCE | 04 | U16 | A 0.01 | RO | t_current
172 | AC_POWER | 0x0BCF | 04 | S32 | W 1 | RO | ac_power
173 | ROTATIONAL_SPEED_OF_FAN_A | 0x0BD7 | 04 | U16 | A | RO
174 | ROTATIONAL_SPEED_OF_FAN_C | 0x0BD9 | 04 | U16 |  | RO
175 | Reserve. | 0x0BDA | 04 | U32 |  | RO
176 | INPUT_MODE | 0x0BDD | 04 | U16 |  | RO
177 | CUMULATIVE_ENERGY | 0x0BDE | 04 | U32 | Kwh 0.1 | RO | cumulative_energy
178 | Annual energy yield | 0x0BE0 | 04 | U32 | Kwh | RO | cumulative_energy
179 | Power-on voltage | 0x0BE3 | 04 | U16 | V 0.1 | RO
180 | Power-on delay | 0x0BE4 | 04 | U16 |  | RO
181 | Lower grid voltagethreshold | 0x0BE5 | 04 | U16 | V 0.1 | RO
182 | Upper grid voltagethreshold | 0x0BE6 | 04 | U16 | V 0.1 | RO
183 | Lower grid frequencythreshold | 0x0BE7 | 04 | U16 | Hz 0.01 | RO
184 | Upper grid frequencythreshold | 0x0BE8 | 04 | U16 | Hz 0.01 | RO
185 | Preset power factor | 0x0BE9 | 04 | U16 |  | RO
186 | Preset active power | 0x0BEA | 04 | U16 |  | RO
187 | Preset reactive power | 0x0BEB | 04 | U16 | KVar 1 | RO
188 | REACTIVE_POWER | 0x0BEE | 04 | S32 |  | RO | reactive_power
189 | Power factor | 0x0BF0 | 04 | U16 |  | RO | power_factor
190 | Overfrequency derating | 0x0BF2 | 04 | U16 |  | RO
191 | Overfrequency deratingthreshold | 0x0BF3 | 04 | U16 |  | RO
192 | Derating rate | 0x0BF4 | 04 | U16 | Hz 0.01 | RO
193 | PV1_STRING_CURRENT_1 | 0x0BF8 | 04 | S16 | A 0.01 | RO
194 | PV1 String current 2 | 0x0BF9 | 04 | S16 | A 0.01 | RO | string2_current
195 | PV1 String current 3 | 0x0BFA | 04 | S16 | A 0.01 | RO | string3_current
196 | PV1 String current 4 | 0x0BFB | 04 | S16 | A 0.01 | RO | string4_current
197 | PV2 String current 1 | 0x0BFC | 04 | S16 | A 0.01 | RO | string5_current
198 | PV2 String current 2 | 0x0BFD | 04 | S16 | A 0.01 | RO | string6_current
199 | PV2 String current 3 | 0x0BFE | 04 | S16 | A 0.01 | RO | string7_current
200 | PV2 String current 4 | 0x0BFF | 04 | S16 | A 0.01 | RO | string8_current
201 | PV3 String current 1 | 0x0C00 | 04 | S16 | A 0.01 | RO | string9_current
202 | PV3 String current 2 | 0x0C01 | 04 | S16 | A 0.01 | RO | string10_current
203 | PV3 String current 3 | 0x0C02 | 04 | S16 | A 0.01 | RO | string11_current
204 | PV3 String current 4 | 0x0C03 | 04 | S16 | A 0.01 | RO | string12_current
205 | PV4 String current 1 | 0x0C04 | 04 | S16 | A 0.01 | RO | string13_current
206 | PV4 String current 2 | 0x0C05 | 04 | S16 | A 0.01 | RO | string14_current
207 | PV4 String current 3 | 0x0C06 | 04 | S16 | A 0.01 | RO | string15_current
208 | PV4 String current 4 | 0x0C07 | 04 | S16 | A 0.01 | RO | string16_current
209 | PV5 String current 1 | 0x0C08 | 04 | S16 | A 0.01 | RO | string17_current
210 | PV5 String current 2 | 0x0C09 | 04 | S16 | A 0.01 | RO | string18_current
211 | PV5 String current 3 | 0x0C0A | 04 | S16 | A 0.01 | RO | string19_current
212 | PV5 String current 4 | 0x0C0B | 04 | S16 | A 0.01 | RO | string20_current
213 | PV6 String current 1 | 0x0C0C | 04 | S16 | A 0.01 | RO | string21_current
214 | PV6 String current 2 | 0x0C0D | 04 | S16 | A 0.01 | RO | string22_current
215 | PV6 String current 3 | 0x0C0E | 04 | S16 | A 0.01 | RO | string23_current
216 | PV6 String current 4 | 0x0C0F | 04 | S16 | A 0.01 | RO | string24_current
217 | Reserve | 0x0C10 | 04 | U16 |  | RO
218 | Reserve | 0x0C11 | 04 | U16 |  | RO
219 | RUNNING_TIME | 0x0C12 | 04 | U32 |  | RO
220 | Generating Time | 0x0C14 | 04 | U32 |  | RO
221 | NUMBER_OF_GRIDCONNECTION | 0x0C16 | 04 | U32 |  | RO
222 | Power Peak After Starting | 0x0C18 | 04 | U32 | W | RO
223 | Day Generation | 0x0C1A | 04 | U32 | W | RO | frequency
224 | Week Generation | 0x0C1C | 04 | U32 | Kwh | RO
225 | Month Generation | 0x0C1E | 04 | U32 | Kwh | RO
226 | Last N days Generation | 0x0C20 | 04 | U32 | Kwh | RO
227 | Value of N | 0x0C22 | 04 | U16 |  | RO
228 | Year | 0x0C23 | 04 | U16 |  | RO
229 | Month | 0x0C24 | 04 | U16 |  | RO
230 | Date | 0x0C25 | 04 | U16 |  | RO
231 | Hour | 0x0C26 | 04 | U16 |  | RO
232 | Minute | 0x0C27 | 04 | U16 |  | RO
233 | Second | 0x0C28 | 04 | U16 |  | RO
234 | Week | 0x0C29 | 04 | U16 |  | RO
235 | Back-current Power LimitSetting | 0x0C2A | 04 | U16 |  | RO
236 | Reserve | 0x0C2C | 04 | U16 |  | RO
237 | 485Address(2) | 0x0C2D | 04 | U16 |  | RO
238 | 485 Agreement | 0x0C2F | 04 | U16 |  | RO
239 | 485 Address(1) | 0x0C30 | 04 | U16 |  | RO
240 | Three-phase System | 0x0C32 | 04 | U16 |  | RO
241 | Remote Control Enable | 0x0C33 | 04 | U16 |  | RO
242 | L1_CURRENT | 0x0C34 | 04 | U16 | A | RO
243 | Setting Value ofSelf-check | 0x0C35 | 04 | U16 |  | RO
244 | Table 3.3.4 | 0x0C37 | 04 | U16 |  | RO
245 | T-phase CurrentCalibration Factor | 0x0C42 | 04 | U16 |  | RO
246 | Battery VoltageCalibration Factor | 0x0C43 | 04 | U16 |  | RO
247 | Underfrequencyincrease slope | 0x0C4A | 04 | U16 |  | RO
248 | FrozenUpFreqEnbUnder frequencyincrease | 0x0C4B | 04 | U16 |  | RO
249 | Slow increase in power | 0x0C4D | 04 | U16 |  | RO
250 | AC_POWER | 0x0C4E | 04 | U16 |  | RO | ac_power
251 | FrozenUpVoltStartStarting value ofovervoltage derating | 0x0C4F | 04 | U16 | V 0.1 | RO
252 | FrozenUpVoltEndEnd value ofovervoltage derating | 0x0C50 | 04 | U16 | V 0.1 | RO
253 | 0-23 bits valid，Enable by setting 1,disable by setting 0 | 0x0C7F | 04 | U32 |  | RO
254 | Correction value ofanti reverse currentmeter | 0x0C84 | 04 | S16 |  | RO
255 | CT ratio | 0x0C85 | 04 | U16 |  | RO
256 | ASCII character | 0x0C86 | 04 | ASCII |  | RO
257 | PV1 currentcalibrationcoefficient | 0x0C8E | 04 | U16 |  | RO
258 | PV2 currentcalibrationcoefficient | 0x0C8F | 04 | U16 |  | RO
259 | PV3~PV12 currentcalibrationcoefficient | 0x0C90 | 04 | U16 |  | RO
260 | PLC MAC Address | 0x0C91 | 04 | U16 |  | RO
261 | Power change rate | 0x0C9A | 04 | U16 |  | RO
262 | Upper limit offrequency responsedead band | 0x0C9F | 04 | U16 | Hz 0.01 | RO
263 | Lower limit offrequency responsedead band | 0x0CA0 | 04 | U16 | Hz 0.01 | RO
264 | Over frequencyderating coefficient | 0x0CA1 | 04 | U16 |  | RO
265 | Underfrequencyamplificationcoefficient | 0x0CA2 | 04 | U16 |  | RO
266 | Daily power generation(0.1Kwh) | 0x0CA9 | 04 | U16 | Kwh 0.1 | RO
267 | Accumulated loadelectricityconsumption on the gridside | 0x0CAA | 04 | U32 |  | RO
268 | Enable: 0, Prohibit: 1 | 0x0CAD | 04 | U16 |  | RO
269 | GRID_PROTECTED_MODE | 0x0CAE | 04 | U16 |  | RO
270 | 0: Distributionnetwork1: Transmissionnetwork | 0x0CAF | 04 | U16 |  | RO
271 | Enable: 0, Prohibit: 1 | 0x0CB1 | 04 | U16 |  | RO
272 | Reserve (860 Register) | 0x0CB4 | 04 | U16 |  | RO
273 | Clock information | 0x0CE4 | 04 | U16 |  | RO
274 | ASCII code | 0x0CEA | 04 | ASCII |  | RO
275 | QV Active Factor | 0x0CEB | 04 | U16 |  | RO
276 | Setting PLC MAC | 0x0CFB | 04 | U16 |  | RO
277 | QV Curve (2) | 0x0CFE | 04 | U16 |  | RO
278 | DATA arbitrary number | 0x0FA1 | 04 | U16 |  | RO
279 | Revoke remotepower-off | 0x0FA2 | 04 | U16 |  | RO
280 | Set the powerfactor | 0x0FA3 | 04 | U16 |  | RO
281 | Set the activepower | 0x0FA4 | 04 | U16 |  | RO
282 | Set the reactivepower | 0x0FA5 | 04 | S16 | KVar 1 | RO
283 | SET_THE_REACTIVECONTROL_MODE | 0x0FA6 | 04 | U16 |  | RO
284 | Overfrequencyderating | 0x0FA7 | 04 | U16 |  | RO
285 | Overfrequency | 0x0FA8 | 04 | U16 | Hz 0.01 | RO
286 | Set the activepower | 0x0FAA | 04 | U16 |  | RO
287 | LOGO Settings | 0x0FAB | 04 | U16 |  | RO
288 | INPUT_MODE_SETTINGS | 0x0FAC | 04 | U16 |  | RO
289 | GridConnectionStandardSettings | 0x0FAD | 04 | U16 |  | RO
290 | Start DelaySettings | 0x0FAF | 04 | U16 |  | RO
291 | Grid VoltageLower LimitSettings | 0x0FB0 | 04 | U16 |  | RO
292 | Grid VoltageUpper LimitSettings | 0x0FB1 | 04 | U16 |  | RO
293 | Grid FrequencyLower LimitSettings | 0x0FB2 | 04 | U16 |  | RO
294 | GridFrequencyUpper LimitSettings | 0x0FB3 | 04 | U16 |  | RO
295 | Back CurrentPower LimitSettings | 0x0FB4 | 04 | U16 |  | RO
296 | OvervoltageDeratingThresholdValue | 0x0FB5 | 04 | U16 | % 0.1 | RO
297 | Reserve | 0x0FB6 | 04 | U16 |  | RO
298 | 485 AddressSettings(U2) | 0x0FB7 | 04 | U16 |  | RO
299 | 485 ProtocolSettings | 0x0FB9 | 04 | U16 |  | RO
300 | 485 AddressSettings(U4) | 0x0FBA | 04 | U16 |  | RO
301 | Three-phaseSettings | 0x0FBC | 04 | U16 |  | RO
302 | RemoteControlSettings | 0x0FBD | 04 | U16 |  | RO
303 | String TestThresholdValue Settings | 0x0FBE | 04 | STRINGING |  | RO
304 | Self-check(Enable) | 0x0FBF | 04 | U16 |  | RO
305 | Self-check(Disable) | 0x0FC0 | 04 | U16 |  | RO
306 | DATA arbitrary number | 0x0FC2 | 04 | U16 |  | RO
307 | The machine comeswith saturationcalculation. | 0x0FC4 | 04 | S16 |  | RO
308 | The machine comes | 0x0FC5 | 04 | S16 |  | RO
309 | Active PowerSettings(Decimals) | 0x0FC7 | 04 | U16 | % 0.1 | RO
310 | R-phaseVoltageCalibrationFactor | 0x0FC8 | 04 | U16 |  | RO
311 | S-phaseVoltageCalibrationFactor | 0x0FC9 | 04 | U16 |  | RO
312 | T-phaseVoltageCalibrationFactor | 0x0FCA | 04 | U16 |  | RO
313 | R-phaseCurrentCalibrationFactor | 0x0FCB | 04 | U16 |  | RO
314 | S-phaseCalibrationFactor | 0x0FCC | 04 | U16 |  | RO
315 | T-phaseCurrentCalibrationFactor | 0x0FCD | 04 | U16 |  | RO
316 | Battery VoltageCalibrationFactor | 0x0FCE | 04 | U16 |  | RO
317 | Reserve(358registers) | 0x0FCF | 04 | U16 |  | RO
318 | Table 3.1.16 | 0x112F | 04 | U16 |  | RO
319 | LN:2000LL:3460 | 0x12F2 | 04 | U16 |  | RO
320 | PV1 Current Point 1 | 0x1389 | 04 | S16 | A 0.01 | RO
321 | PV1 Voltage Point 2 | 0x138A | 04 | U16 | V 0.1 | RO
322 | PV1_CURRENT_POINT_2 | 0x138B | 04 | S16 | A 0.01 | RO
323 | PV1 Voltage Point 99 | 0x144C | 04 | U16 | V 0.1 | RO
324 | PV1 Current Point 99 | 0x144D | 04 | S16 | A 0.01 | RO
325 | PV1 Voltage Point 100 | 0x144E | 04 | U16 | V 0.1 | RO
326 | PV1 Current Point 100 | 0x144F | 04 | S16 | A 0.01 | RO
327 | PV2 Current Point 1 | 0x1451 | 04 | S16 | A 0.01 | RO
328 | PV2 Voltage Point 2 | 0x1452 | 04 | U16 | V 0.1 | RO
329 | PV2 Current Point 2 | 0x1453 | 04 | S16 | A 0.01 | RO
330 | PV2 Voltage Point 99 | 0x1514 | 04 | U16 | V 0.1 | RO
331 | PV2 Current Point 99 | 0x1515 | 04 | S16 | A 0.01 | RO
332 | PV2 Voltage Point 100 | 0x1516 | 04 | U16 | V 0.1 | RO
333 | PV2 Current Point 100 | 0x1517 | 04 | S16 | A 0.01 | RO
334 | PV4 Voltage and CurrentPoint | 0x15E0 | 04 | U16 |  | RO
335 | PV5 Voltage and CurrentPoint | 0x16A8 | 04 | U16 |  | RO
336 | PV6 Voltage and CurrentPoint | 0x1770 | 04 | U16 |  | RO
337 | PV7 Voltage and CurrentPoint | 0x1838 | 04 | U16 |  | RO
338 | PV8 Voltage and CurrentPoint | 0x1900 | 04 | U16 |  | RO
339 | PV9 Voltage and CurrentPoint | 0x19C8 | 04 | U16 |  | RO
340 | PV10 Voltage and CurrentPoint | 0x1A90 | 04 | U16 |  | RO
341 | PV11 Voltage and CurrentPoint | 0x1B58 | 04 | U16 |  | RO
342 | PV12 Voltage and CurrentPoint | 0x1C20 | 04 | U16 |  | RO
343 | 0:Disable 1:Enable | 0x2328 | 04 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## 5_IV
IV Scan 매핑 — data_points=100
IV Scan Command | 0x0CB2
Data Points | 100
Trackers | 2
Strings/Tracker | 0
IV Scan Command
Name | Address | Type | R/W | Description
IV_CURVE_SCAN | 0x0CB2 | U16 | RW | W: 0=Stop, 1=Start / R: 0=Idle, 1=Running, 2=Finished
IV Data 레지스터 매핑
No | Type | Name | Address | Regs | Data Type | Scale
1 | Tracker Voltage | Tracker 1 voltage | 0x138A | 100 | U16 | 0.1V
2 | Tracker Voltage | Tracker 2 voltage | 0x1450 | 100 | U16 | 0.1V

## INFO_MAPPING
INFO_MAPPING — Model / Serial Number 수동 매핑
※ D열에서 매핑할 레지스터를 선택하세요. E~G열은 추천 후보, H열은 전체 INFO 후보 목록.
No | Field | 설명 | 매칭된 레지스터 (주소) | 추천 후보 1 | 추천 후보 2 | 추천 후보 3 | 전체 레지스터 목록 | FC
1 | model | Model 정보 (제조사/타입/제품명) | MACHINE_MODEL (0x0C80) |  |  |  | ACCUMULATED_LOADELECTRICITYCONSUMPTION_ON_THE_GRIDSIDE | 3 | ACCUMULATED_LOADELECTRICITYCONSUMPTION_ON_THE_GRIDSIDE | 3 | 0x0CAA | pdf
2 | sn | Serial Number / Firmware Version | SETTING_INVERTER_SN (0x0CEF) |  |  |  | ACTIVE_POWER_SETTINGS_DECIMALS | 3 | ACTIVE_POWER_SETTINGS_DECIMALS | 3 | 0x0FC7 | pdf
[7 empty] | AC_POWER |  | AC_POWER | 3 | 0x0BCF
[7 empty] | AC_RELAY_FAULT |  | AC_RELAY_FAULT | 3 | 0x000E
[7 empty] | AMBIENT_TEMPERATURE_OVER |  | AMBIENT_TEMPERATURE_OVER | 3 | 0x000C
[7 empty] | ANNUAL_ENERGY_YIELD |  | ANNUAL_ENERGY_YIELD | 3 | 0x0BE0
[7 empty] | APPARENT_POWER |  | APPARENT_POWER | 3 | 0x0BEC
[7 empty] | ARM_ALARM_CODE |  | ARM_ALARM_CODE | 3 | 0x0BDC
[7 empty] | ASCII_CHARACTER |  | ASCII_CHARACTER | 3 | 0x0C86
[7 empty] | ASCII_CODE |  | ASCII_CODE | 3 | 0x0CEA
[7 empty] | AUXILIARY_POWER_OFF |  | AUXILIARY_POWER_OFF | 3 | 0x0019
[7 empty] | BACK_CURRENT_POWER_LIMIT_SETTING |  | BACK_CURRENT_POWER_LIMIT_SETTING | 3 | 0x0C2A
[7 empty] | BACK_CURRENT_POWER_LIMIT_SETTINGS |  | BACK_CURRENT_POWER_LIMIT_SETTINGS | 3 | 0x0FB4
[7 empty] | BATTERY_VOLTAGE_CALIBRATION_FACTOR |  | BATTERY_VOLTAGE_CALIBRATION_FACTOR | 3 | 0x0C43
[7 empty] | BLU_E_10KT_M0 |  | BLU_E_10KT_M0 | 3 | 0x007A
[7 empty] | BLU_E_10KT_M1 |  | BLU_E_10KT_M1 | 3 | 0x007B
[7 empty] | BLU_E_10KT_M2 |  | BLU_E_10KT_M2 | 3 | 0x00E0
[7 empty] | BLU_E_10KT_M3 |  | BLU_E_10KT_M3 | 3 | 0x00E1
[7 empty] | BLU_E_10KT_M4 |  | BLU_E_10KT_M4 | 3 | 0x00E2
[7 empty] | BLU_E_10KT_M5 |  | BLU_E_10KT_M5 | 3 | 0x00E3
[7 empty] | BLU_E_12KT_M0 |  | BLU_E_12KT_M0 | 3 | 0x007C
[7 empty] | BLU_E_12KT_M1 |  | BLU_E_12KT_M1 | 3 | 0x007D
[7 empty] | BLU_E_12KT_M2 |  | BLU_E_12KT_M2 | 3 | 0x00E4
[7 empty] | BLU_E_12KT_M3 |  | BLU_E_12KT_M3 | 3 | 0x00E5
[7 empty] | BLU_E_12KT_M4 |  | BLU_E_12KT_M4 | 3 | 0x00E6
[7 empty] | BLU_E_12KT_M5 |  | BLU_E_12KT_M5 | 3 | 0x00E7
[7 empty] | BLU_E_15KT_M0 |  | BLU_E_15KT_M0 | 3 | 0x007E
[7 empty] | BLU_E_15KT_M1 |  | BLU_E_15KT_M1 | 3 | 0x007F
[7 empty] | BLU_E_15KT_M2 |  | BLU_E_15KT_M2 | 3 | 0x0080
[7 empty] | BLU_E_15KT_M3 |  | BLU_E_15KT_M3 | 3 | 0x0081
[7 empty] | BLU_E_15KT_M4 |  | BLU_E_15KT_M4 | 3 | 0x00E8
[7 empty] | BLU_E_15KT_M5 |  | BLU_E_15KT_M5 | 3 | 0x00E9
[7 empty] | BLU_E_17KT_M0 |  | BLU_E_17KT_M0 | 3 | 0x0082
[7 empty] | BLU_E_17KT_M1 |  | BLU_E_17KT_M1 | 3 | 0x0083
[7 empty] | BLU_E_17KT_M2 |  | BLU_E_17KT_M2 | 3 | 0x00EA
[7 empty] | BLU_E_17KT_M3 |  | BLU_E_17KT_M3 | 3 | 0x00EB
[7 empty] | BLU_E_17KT_M4 |  | BLU_E_17KT_M4 | 3 | 0x00EC
[7 empty] | BLU_E_17KT_M5 |  | BLU_E_17KT_M5 | 3 | 0x00ED
[7 empty] | BLU_E_20KT_M0 |  | BLU_E_20KT_M0 | 3 | 0x0084
[7 empty] | BLU_E_20KT_M1 |  | BLU_E_20KT_M1 | 3 | 0x0085
[7 empty] | BLU_E_20KT_M2 |  | BLU_E_20KT_M2 | 3 | 0x00EE
[7 empty] | BLU_E_20KT_M3 |  | BLU_E_20KT_M3 | 3 | 0x00EF
[7 empty] | BLU_E_20KT_M4 |  | BLU_E_20KT_M4 | 3 | 0x00F0
[7 empty] | BLU_E_20KT_M5 |  | BLU_E_20KT_M5 | 3 | 0x00F1
[7 empty] | BLU_E_22KT_M0 |  | BLU_E_22KT_M0 | 3 | 0x0086
[7 empty] | BLU_E_22KT_M1 |  | BLU_E_22KT_M1 | 3 | 0x0087
[7 empty] | BLU_E_22KT_M2 |  | BLU_E_22KT_M2 | 3 | 0x00F2
[7 empty] | BLU_E_22KT_M3 |  | BLU_E_22KT_M3 | 3 | 0x00F3
[7 empty] | BLU_E_22KT_M4 |  | BLU_E_22KT_M4 | 3 | 0x00F4
[7 empty] | BLU_E_22KT_M5 |  | BLU_E_22KT_M5 | 3 | 0x00F5
[7 empty] | BLU_E_23KT_M0 |  | BLU_E_23KT_M0 | 3 | 0x0088
[7 empty] | BLU_E_23KT_M1 |  | BLU_E_23KT_M1 | 3 | 0x0089
[7 empty] | BLU_E_23KT_M2 |  | BLU_E_23KT_M2 | 3 | 0x00F6
[7 empty] | BLU_E_23KT_M3 |  | BLU_E_23KT_M3 | 3 | 0x00F7
[7 empty] | BLU_E_23KT_M4 |  | BLU_E_23KT_M4 | 3 | 0x00F8
[7 empty] | BLU_E_23KT_M5 |  | BLU_E_23KT_M5 | 3 | 0x00F9
[7 empty] | BLU_E_25KT_M0 |  | BLU_E_25KT_M0 | 3 | 0x008A
[7 empty] | BLU_E_25KT_M1 |  | BLU_E_25KT_M1 | 3 | 0x008B
[7 empty] | BLU_E_25KT_M2 |  | BLU_E_25KT_M2 | 3 | 0x00FA
[7 empty] | BLU_E_25KT_M3 |  | BLU_E_25KT_M3 | 3 | 0x00FB
[7 empty] | BLU_E_25KT_M4 |  | BLU_E_25KT_M4 | 3 | 0x00FC
[7 empty] | BLU_E_25KT_M5 |  | BLU_E_25KT_M5 | 3 | 0x00FD
[7 empty] | BLU_E_3KT_M0 |  | BLU_E_3KT_M0 | 3 | 0x006E
[7 empty] | BLU_E_3KT_M1 |  | BLU_E_3KT_M1 | 3 | 0x006F
[7 empty] | BLU_E_3KT_M3 |  | BLU_E_3KT_M3 | 3 | 0x00C9
[7 empty] | BLU_E_3KT_M4 |  | BLU_E_3KT_M4 | 3 | 0x00CA
[7 empty] | BLU_E_3KT_M5 |  | BLU_E_3KT_M5 | 3 | 0x00CB
[7 empty] | BLU_E_3_6KT_M0 |  | BLU_E_3_6KT_M0 | 3 | 0x0070
[7 empty] | BLU_E_3_6KT_M1 |  | BLU_E_3_6KT_M1 | 3 | 0x0071
[7 empty] | BLU_E_3_6KT_M2 |  | BLU_E_3_6KT_M2 | 3 | 0x00CC
[7 empty] | BLU_E_3_6KT_M3 |  | BLU_E_3_6KT_M3 | 3 | 0x00CD
[7 empty] | BLU_E_3_6KT_M4 |  | BLU_E_3_6KT_M4 | 3 | 0x00CE
[7 empty] | BLU_E_3_6KT_M5 |  | BLU_E_3_6KT_M5 | 3 | 0x00CF
[7 empty] | BLU_E_4KT_M0 |  | BLU_E_4KT_M0 | 3 | 0x0072
[7 empty] | BLU_E_4KT_M1 |  | BLU_E_4KT_M1 | 3 | 0x0073
[7 empty] | BLU_E_4KT_M2 |  | BLU_E_4KT_M2 | 3 | 0x00D0
[7 empty] | BLU_E_4KT_M3 |  | BLU_E_4KT_M3 | 3 | 0x00D1
[7 empty] | BLU_E_4KT_M4 |  | BLU_E_4KT_M4 | 3 | 0x00D2
[7 empty] | BLU_E_4KT_M5 |  | BLU_E_4KT_M5 | 3 | 0x00D3
[7 empty] | BLU_E_5KT_M0 |  | BLU_E_5KT_M0 | 3 | 0x0074
[7 empty] | BLU_E_5KT_M1 |  | BLU_E_5KT_M1 | 3 | 0x0075
[7 empty] | BLU_E_5KT_M2 |  | BLU_E_5KT_M2 | 3 | 0x00D4
[7 empty] | BLU_E_5KT_M3 |  | BLU_E_5KT_M3 | 3 | 0x00D5
[7 empty] | BLU_E_5KT_M4 |  | BLU_E_5KT_M4 | 3 | 0x00D6
[7 empty] | BLU_E_5KT_M5 |  | BLU_E_5KT_M5 | 3 | 0x00D7
[7 empty] | BLU_E_6KT_M0 |  | BLU_E_6KT_M0 | 3 | 0x0076
[7 empty] | BLU_E_6KT_M1 |  | BLU_E_6KT_M1 | 3 | 0x0077
[7 empty] | BLU_E_6KT_M2 |  | BLU_E_6KT_M2 | 3 | 0x00D8
[7 empty] | BLU_E_6KT_M3 |  | BLU_E_6KT_M3 | 3 | 0x00D9
[7 empty] | BLU_E_6KT_M4 |  | BLU_E_6KT_M4 | 3 | 0x00DA
[7 empty] | BLU_E_6KT_M5 |  | BLU_E_6KT_M5 | 3 | 0x00DB
[7 empty] | BLU_E_8KT_M0 |  | BLU_E_8KT_M0 | 3 | 0x0078
[7 empty] | BLU_E_8KT_M1 |  | BLU_E_8KT_M1 | 3 | 0x0079
[7 empty] | BLU_E_8KT_M2 |  | BLU_E_8KT_M2 | 3 | 0x00DC
[7 empty] | BLU_E_8KT_M3 |  | BLU_E_8KT_M3 | 3 | 0x00DD
[7 empty] | BLU_E_8KT_M4 |  | BLU_E_8KT_M4 | 3 | 0x00DE
[7 empty] | BLU_E_8KT_M5 |  | BLU_E_8KT_M5 | 3 | 0x00DF
[7 empty] | BLU_E_G_3000D |  | BLU_E_G_3000D | 3 | 0x0065
[7 empty] | BLU_E_G_3600D |  | BLU_E_G_3600D | 3 | 0x0066
[7 empty] | BLU_E_G_4000D |  | BLU_E_G_4000D | 3 | 0x0067
[7 empty] | BLU_E_G_4200D |  | BLU_E_G_4200D | 3 | 0x0068
[7 empty] | BLU_E_G_4600D |  | BLU_E_G_4600D | 3 | 0x0069
[7 empty] | BLU_E_G_5000D |  | BLU_E_G_5000D | 3 | 0x006A
[7 empty] | BLU_E_G_6000D |  | BLU_E_G_6000D | 3 | 0x006B
[7 empty] | BYTECOUNT |  | BYTECOUNT | 3 | 0x0001
[7 empty] | CANCEL_POWER_FACTOR_CONTROL_DEFAULTPOWER_FACTOR_1 |  | CANCEL_POWER_FACTOR_CONTROL_DEFAULTPOWER_FACTOR_1 | 3 | 0xFFFF
[7 empty] | CLEAR_FAULT_RECORD |  | CLEAR_FAULT_RECORD | 3 | 0x0FC1
[7 empty] | CLOCK_INFORMATION |  | CLOCK_INFORMATION | 3 | 0x0CE4
[7 empty] | CORRECTION_VALUE_OFANTI_REVERSE_CURRENTMETER |  | CORRECTION_VALUE_OFANTI_REVERSE_CURRENTMETER | 3 | 0x0C84
[7 empty] | CT_RATIO |  | CT_RATIO | 3 | 0x0C85
[7 empty] | CUMULATIVE_ENERGY |  | CUMULATIVE_ENERGY | 3 | 0x0BDE
[7 empty] | DAILY_ENERGY_YIELD |  | DAILY_ENERGY_YIELD | 3 | 0x0BE2
[7 empty] | DAILY_POWER_GENERATION0_1KWH |  | DAILY_POWER_GENERATION0_1KWH | 3 | 0x0CA9
[7 empty] | DATA_ARBITRARY_NUMBER |  | DATA_ARBITRARY_NUMBER | 3 | 0x0FA1
[7 empty] | DATE |  | DATE | 3 | 0x0C25
[7 empty] | DAY_GENERATION |  | DAY_GENERATION | 3 | 0x0C1A
[7 empty] | DC_INSULATION_RESISTANCE |  | DC_INSULATION_RESISTANCE | 3 | 0x0BF1
[7 empty] | DC_OVER_VOLT_SERIOUS_FAULT |  | DC_OVER_VOLT_SERIOUS_FAULT | 3 | 0x001C
[7 empty] | DEFAULT_VALUE1 |  | DEFAULT_VALUE1 | 3 | 0x0C7A
[7 empty] | DEFAULT_VALUE10_PROHIBIT_1_PERMIT |  | DEFAULT_VALUE10_PROHIBIT_1_PERMIT | 3 | 0x0C44
[7 empty] | DERATING_RATE |  | DERATING_RATE | 3 | 0x0BF4
[7 empty] | DEVICE_MODEL |  | DEVICE_MODEL | 3 | 0x0D05
[7 empty] | DSP_ALARM_CODE |  | DSP_ALARM_CODE | 3 | 0x0BD3
[7 empty] | DSP_ERROR_CODE |  | DSP_ERROR_CODE | 3 | 0x0BD4
[7 empty] | ENABLE_0_PROHIBIT_1 |  | ENABLE_0_PROHIBIT_1 | 3 | 0x0CAD
[7 empty] | FAN_A_LOCK |  | FAN_A_LOCK | 3 | 0x0000
[7 empty] | FAULT_RECOVERY_TIME |  | FAULT_RECOVERY_TIME | 3 | 0x0CB0
[7 empty] | FREQUENCY |  | FREQUENCY | 3 | 0x0BC9
[7 empty] | FREQUENCY_CONSISTENT_FAULT |  | FREQUENCY_CONSISTENT_FAULT | 3 | 0x0017
[7 empty] | FROZEN_UP_FREQ_ENB_UNDER_FREQUENCYINCREASE |  | FROZEN_UP_FREQ_ENB_UNDER_FREQUENCYINCREASE | 3 | 0x0C4B
[7 empty] | FROZEN_UP_VOLT_END_END_VALUE_OFOVERVOLTAGE_DERATING |  | FROZEN_UP_VOLT_END_END_VALUE_OFOVERVOLTAGE_DERATING | 3 | 0x0C50
[7 empty] | FROZEN_UP_VOLT_START_STARTING_VALUE_OFOVERVOLTAGE_DERATING |  | FROZEN_UP_VOLT_START_STARTING_VALUE_OFOVERVOLTAGE_DERATING | 3 | 0x0C4F
[7 empty] | FUSE_ALARM_INFORMATION |  | FUSE_ALARM_INFORMATION | 3 | 0x0C81
[7 empty] | G40KT |  | G40KT | 3 | 0x00B2
[7 empty] | G40KT1 |  | G40KT1 | 3 | 0x00B3
[7 empty] | G40KT2 |  | G40KT2 | 3 | 0x00B4
[7 empty] | G40KT3 |  | G40KT3 | 3 | 0x00B5
[7 empty] | G50KT |  | G50KT | 3 | 0x00B0
[7 empty] | G50KT1 |  | G50KT1 | 3 | 0x00B1
[7 empty] | G60KT |  | G60KT | 3 | 0x00AE
[7 empty] | G60KT1 |  | G60KT1 | 3 | 0x00AF
[7 empty] | G70KT |  | G70KT | 3 | 0x00AC
[7 empty] | G70KT1 |  | G70KT1 | 3 | 0x00AD
[7 empty] | G75KT |  | G75KT | 3 | 0x00AA
[7 empty] | G75KT1 |  | G75KT1 | 3 | 0x00AB
[7 empty] | G80KT |  | G80KT | 3 | 0x00A8
[7 empty] | G80KT1 |  | G80KT1 | 3 | 0x00A9
[7 empty] | GENERATING_TIME |  | GENERATING_TIME | 3 | 0x0C14
[7 empty] | GFCI_DEVICE_FAULT |  | GFCI_DEVICE_FAULT | 3 | 0x0015
[7 empty] | GFCI_OVER_FAULT |  | GFCI_OVER_FAULT | 3 | 0x0014
[7 empty] | GRID_CONNECTION_STANDARD_SETTINGS |  | GRID_CONNECTION_STANDARD_SETTINGS | 3 | 0x0FAD
[7 empty] | GRID_FREQUENCY_LOWER_LIMIT_SETTINGS |  | GRID_FREQUENCY_LOWER_LIMIT_SETTINGS | 3 | 0x0FB2
[7 empty] | GRID_FREQUENCY_UPPER_LIMIT_SETTINGS |  | GRID_FREQUENCY_UPPER_LIMIT_SETTINGS | 3 | 0x0FB3
[7 empty] | GRID_PROTECTED_MODE |  | GRID_PROTECTED_MODE | 3 | 0x0CAE
[7 empty] | GRID_VOLTAGE_LOWER_LIMIT_SETTINGS |  | GRID_VOLTAGE_LOWER_LIMIT_SETTINGS | 3 | 0x0FB0
[7 empty] | GRID_VOLTAGE_UPPER_LIMIT_SETTINGS |  | GRID_VOLTAGE_UPPER_LIMIT_SETTINGS | 3 | 0x0FB1
[7 empty] | HARD_INVERTER_CURRENT_OVER |  | HARD_INVERTER_CURRENT_OVER | 3 | 0x0009
[7 empty] | HOUR |  | HOUR | 3 | 0x0C26
[7 empty] | IGBT_FAULT |  | IGBT_FAULT | 3 | 0x001A
[7 empty] | IGBT_SERIOUS_FAULT |  | IGBT_SERIOUS_FAULT | 3 | 0x001D
[7 empty] | INNER_TEMP |  | INNER_TEMP | 3 | 0x0BD1
[7 empty] | INPUT_MODE |  | INPUT_MODE | 3 | 0x0BDD
[7 empty] | INPUT_MODE_SETTINGS |  | INPUT_MODE_SETTINGS | 3 | 0x0FAC
[7 empty] | INVALID_DATA_ADDRESS |  | INVALID_DATA_ADDRESS | 3 | 0x0002
[7 empty] | INVALID_FUNCTION_CODE |  | INVALID_FUNCTION_CODE | 3 | 0x0001
[7 empty] | INVERTER_CURRENT_OVER |  | INVERTER_CURRENT_OVER | 3 | 0x000A
[7 empty] | INVERTER_DC_CURRERNT_OVER |  | INVERTER_DC_CURRERNT_OVER | 3 | 0x000B
[7 empty] | INVERTER_MODE |  | INVERTER_MODE | 3 | 0x0BD6
[7 empty] | INVERTER_MODEL_NEW |  | INVERTER_MODEL_NEW | 3 | 0x0C95
[7 empty] | L1_CURRENT |  | L1_CURRENT | 3 | 0x0BCC
[7 empty] | L1_VOLTAGE |  | L1_VOLTAGE | 3 | 0x0BC6
[7 empty] | L2_CURRENT |  | L2_CURRENT | 3 | 0x0BCD
[7 empty] | L2_FREQUENCY |  | L2_FREQUENCY | 3 | 0x0BCA
[7 empty] | L2_VOLTAGE |  | L2_VOLTAGE | 3 | 0x0BC7
[7 empty] | L3_CURRENT |  | L3_CURRENT | 3 | 0x0BCE
[7 empty] | L3_FREQUENCY |  | L3_FREQUENCY | 3 | 0x0BCB
[7 empty] | L3_VOLTAGE |  | L3_VOLTAGE | 3 | 0x0BC8
[7 empty] | LAST_N_DAYS_GENERATION |  | LAST_N_DAYS_GENERATION | 3 | 0x0C20
[7 empty] | LCD_MODEL_SETTING |  | LCD_MODEL_SETTING | 3 | 0x0C94
[7 empty] | LN_2000LL_3460 |  | LN_2000LL_3460 | 3 | 0x12F2
[7 empty] | LOGO_SETTINGS |  | LOGO_SETTINGS | 3 | 0x0FAB
[7 empty] | LOWER_GRID_FREQUENCYTHRESHOLD |  | LOWER_GRID_FREQUENCYTHRESHOLD | 3 | 0x0BE7
[7 empty] | LOWER_GRID_VOLTAGETHRESHOLD |  | LOWER_GRID_VOLTAGETHRESHOLD | 3 | 0x0BE5
[7 empty] | LOWER_LIMIT_OFFREQUENCY_RESPONSEDEAD_BAND |  | LOWER_LIMIT_OFFREQUENCY_RESPONSEDEAD_BAND | 3 | 0x0CA0
[7 empty] | MACHINE_MODEL |  | MACHINE_MODEL | 3 | 0x0C80
[7 empty] | MINUTE |  | MINUTE | 3 | 0x0C27
[7 empty] | MONTH |  | MONTH | 3 | 0x0C24
[7 empty] | MONTH_GENERATION |  | MONTH_GENERATION | 3 | 0x0C1E
[7 empty] | NBUS_VOLTAGE |  | NBUS_VOLTAGE | 3 | 0x0BC5
[7 empty] | NPE_VOLTE_FAULT |  | NPE_VOLTE_FAULT | 3 | 0x001B
[7 empty] | NULL |  | NULL | 3 | 0x0008
[7 empty] | NUMBER_OF_GRIDCONNECTION |  | NUMBER_OF_GRIDCONNECTION | 3 | 0x0C16
[7 empty] | OVERFREQUENCY |  | OVERFREQUENCY | 3 | 0x0FA8
[7 empty] | OVERFREQUENCYDERATING |  | OVERFREQUENCYDERATING | 3 | 0x0FA7
[7 empty] | OVERFREQUENCY_DERATING |  | OVERFREQUENCY_DERATING | 3 | 0x0BF2
[7 empty] | OVERFREQUENCY_DERATINGTHRESHOLD |  | OVERFREQUENCY_DERATINGTHRESHOLD | 3 | 0x0BF3
[7 empty] | OVERVOLTAGE_DERATING_THRESHOLD_VALUE |  | OVERVOLTAGE_DERATING_THRESHOLD_VALUE | 3 | 0x0FB5
[7 empty] | OVER_FREQUENCYDERATING_COEFFICIENT |  | OVER_FREQUENCYDERATING_COEFFICIENT | 3 | 0x0CA1
[7 empty] | OVER_TEMPERATUREDERATING_WARNINGENABLE |  | OVER_TEMPERATUREDERATING_WARNINGENABLE | 3 | 0x0C9B
[7 empty] | PBUS_VOLTAGE |  | PBUS_VOLTAGE | 3 | 0x0BC4
[7 empty] | PLC_MAC_ADDRESS |  | PLC_MAC_ADDRESS | 3 | 0x0C91
[7 empty] | POWER_CHANGE_RATE |  | POWER_CHANGE_RATE | 3 | 0x0C9A
[7 empty] | POWER_FACTOR |  | POWER_FACTOR | 3 | 0x0BF0
[7 empty] | POWER_ON_DELAY |  | POWER_ON_DELAY | 3 | 0x0BE4
[7 empty] | POWER_ON_VOLTAGE |  | POWER_ON_VOLTAGE | 3 | 0x0BE3
[7 empty] | POWER_PEAK_AFTER_STARTING |  | POWER_PEAK_AFTER_STARTING | 3 | 0x0C18
[7 empty] | PRESET_ACTIVE_POWER |  | PRESET_ACTIVE_POWER | 3 | 0x0BEA
[7 empty] | PRESET_POWER_FACTOR |  | PRESET_POWER_FACTOR | 3 | 0x0BE9
[7 empty] | PRESET_REACTIVE_POWER |  | PRESET_REACTIVE_POWER | 3 | 0x0BEB
[7 empty] | PV10_INPUT_CURRENT |  | PV10_INPUT_CURRENT | 3 | 0x0B9D
[7 empty] | PV10_INPUT_POWER |  | PV10_INPUT_POWER | 3 | 0x0B9E
[7 empty] | PV10_INPUT_VOLTAGE |  | PV10_INPUT_VOLTAGE | 3 | 0x0B9C
[7 empty] | PV10_VOLTAGE_AND_CURRENT_POINT |  | PV10_VOLTAGE_AND_CURRENT_POINT | 3 | 0x1A90
[7 empty] | PV11_INPUT_CURRENT |  | PV11_INPUT_CURRENT | 3 | 0x0B99
[7 empty] | PV11_INPUT_POWER |  | PV11_INPUT_POWER | 3 | 0x0B9A
[7 empty] | PV11_INPUT_VOLTAGE |  | PV11_INPUT_VOLTAGE | 3 | 0x0B98
[7 empty] | PV11_VOLTAGE_AND_CURRENT_POINT |  | PV11_VOLTAGE_AND_CURRENT_POINT | 3 | 0x1B58
[7 empty] | PV12_INPUT_CURRENT |  | PV12_INPUT_CURRENT | 3 | 0x0B95
[7 empty] | PV12_INPUT_VOLTAGE |  | PV12_INPUT_VOLTAGE | 3 | 0x0B94
[7 empty] | PV12_VOLTAGE_AND_CURRENT_POINT |  | PV12_VOLTAGE_AND_CURRENT_POINT | 3 | 0x1C20
[7 empty] | PV1_CURRENTCALIBRATIONCOEFFICIENT |  | PV1_CURRENTCALIBRATIONCOEFFICIENT | 3 | 0x0C8E
[7 empty] | PV1_CURRENT_POINT_1 |  | PV1_CURRENT_POINT_1 | 3 | 0x1389
[7 empty] | PV1_CURRENT_POINT_100 |  | PV1_CURRENT_POINT_100 | 3 | 0x144F
[7 empty] | PV1_CURRENT_POINT_2 |  | PV1_CURRENT_POINT_2 | 3 | 0x138B
[7 empty] | PV1_CURRENT_POINT_99 |  | PV1_CURRENT_POINT_99 | 3 | 0x144D
[7 empty] | PV1_INPUT_CURRENT |  | PV1_INPUT_CURRENT | 3 | 0x0BBB
[7 empty] | PV1_INPUT_POWER |  | PV1_INPUT_POWER | 3 | 0x0BBE
[7 empty] | PV1_INPUT_VOLTAGE |  | PV1_INPUT_VOLTAGE | 3 | 0x0BB8
[7 empty] | PV1_STRING_CURRENT_1 |  | PV1_STRING_CURRENT_1 | 3 | 0x0BF8
[7 empty] | PV1_STRING_CURRENT_2 |  | PV1_STRING_CURRENT_2 | 3 | 0x0BF9
[7 empty] | PV1_STRING_CURRENT_3 |  | PV1_STRING_CURRENT_3 | 3 | 0x0BFA
[7 empty] | PV1_STRING_CURRENT_4 |  | PV1_STRING_CURRENT_4 | 3 | 0x0BFB
[7 empty] | PV1_VOLTAGE_POINT_100 |  | PV1_VOLTAGE_POINT_100 | 3 | 0x144E
[7 empty] | PV1_VOLTAGE_POINT_2 |  | PV1_VOLTAGE_POINT_2 | 3 | 0x138A
[7 empty] | PV1_VOLTAGE_POINT_99 |  | PV1_VOLTAGE_POINT_99 | 3 | 0x144C
[7 empty] | PV2_CURRENTCALIBRATIONCOEFFICIENT |  | PV2_CURRENTCALIBRATIONCOEFFICIENT | 3 | 0x0C8F
[7 empty] | PV2_CURRENT_POINT_1 |  | PV2_CURRENT_POINT_1 | 3 | 0x1451
[7 empty] | PV2_CURRENT_POINT_100 |  | PV2_CURRENT_POINT_100 | 3 | 0x1517
[7 empty] | PV2_CURRENT_POINT_2 |  | PV2_CURRENT_POINT_2 | 3 | 0x1453
[7 empty] | PV2_CURRENT_POINT_99 |  | PV2_CURRENT_POINT_99 | 3 | 0x1515
[7 empty] | PV2_INPUT_CURRENT |  | PV2_INPUT_CURRENT | 3 | 0x0BBC
[7 empty] | PV2_INPUT_POWER |  | PV2_INPUT_POWER | 3 | 0x0BC0
[7 empty] | PV2_INPUT_VOLTAGE |  | PV2_INPUT_VOLTAGE | 3 | 0x0BB9
[7 empty] | PV2_STRING_CURRENT_1 |  | PV2_STRING_CURRENT_1 | 3 | 0x0BFC
[7 empty] | PV2_STRING_CURRENT_2 |  | PV2_STRING_CURRENT_2 | 3 | 0x0BFD
[7 empty] | PV2_STRING_CURRENT_3 |  | PV2_STRING_CURRENT_3 | 3 | 0x0BFE
[7 empty] | PV2_STRING_CURRENT_4 |  | PV2_STRING_CURRENT_4 | 3 | 0x0BFF
[7 empty] | PV2_VOLTAGE_POINT_100 |  | PV2_VOLTAGE_POINT_100 | 3 | 0x1516
[7 empty] | PV2_VOLTAGE_POINT_2 |  | PV2_VOLTAGE_POINT_2 | 3 | 0x1452
[7 empty] | PV2_VOLTAGE_POINT_99 |  | PV2_VOLTAGE_POINT_99 | 3 | 0x1514
[7 empty] | PV3PV12_CURRENTCALIBRATIONCOEFFICIENT |  | PV3PV12_CURRENTCALIBRATIONCOEFFICIENT | 3 | 0x0C90
[7 empty] | PV3_INPUT_CURRENT |  | PV3_INPUT_CURRENT | 3 | 0x0BBD
[7 empty] | PV3_INPUT_POWER |  | PV3_INPUT_POWER | 3 | 0x0BC2
[7 empty] | PV3_INPUT_VOLTAGE |  | PV3_INPUT_VOLTAGE | 3 | 0x0BBA
[7 empty] | PV3_STRING_CURRENT_1 |  | PV3_STRING_CURRENT_1 | 3 | 0x0C00
[7 empty] | PV3_STRING_CURRENT_2 |  | PV3_STRING_CURRENT_2 | 3 | 0x0C01
[7 empty] | PV3_STRING_CURRENT_3 |  | PV3_STRING_CURRENT_3 | 3 | 0x0C02
[7 empty] | PV3_STRING_CURRENT_4 |  | PV3_STRING_CURRENT_4 | 3 | 0x0C03
[7 empty] | PV4_INPUT_CURRENT |  | PV4_INPUT_CURRENT | 3 | 0x0BB5
[7 empty] | PV4_INPUT_POWER |  | PV4_INPUT_POWER | 3 | 0x0BB6
[7 empty] | PV4_INPUT_VOLTAGE |  | PV4_INPUT_VOLTAGE | 3 | 0x0BB4
[7 empty] | PV4_STRING_CURRENT_1 |  | PV4_STRING_CURRENT_1 | 3 | 0x0C04
[7 empty] | PV4_STRING_CURRENT_2 |  | PV4_STRING_CURRENT_2 | 3 | 0x0C05
[7 empty] | PV4_STRING_CURRENT_3 |  | PV4_STRING_CURRENT_3 | 3 | 0x0C06
[7 empty] | PV4_STRING_CURRENT_4 |  | PV4_STRING_CURRENT_4 | 3 | 0x0C07
[7 empty] | PV4_VOLTAGE_AND_CURRENT_POINT |  | PV4_VOLTAGE_AND_CURRENT_POINT | 3 | 0x15E0
[7 empty] | PV5_INPUT_CURRENT |  | PV5_INPUT_CURRENT | 3 | 0x0BB1
[7 empty] | PV5_INPUT_POWER |  | PV5_INPUT_POWER | 3 | 0x0BB2
[7 empty] | PV5_INPUT_VOLTAGE |  | PV5_INPUT_VOLTAGE | 3 | 0x0BB0
[7 empty] | PV5_STRING_CURRENT_1 |  | PV5_STRING_CURRENT_1 | 3 | 0x0C08
[7 empty] | PV5_STRING_CURRENT_2 |  | PV5_STRING_CURRENT_2 | 3 | 0x0C09
[7 empty] | PV5_STRING_CURRENT_3 |  | PV5_STRING_CURRENT_3 | 3 | 0x0C0A
[7 empty] | PV5_STRING_CURRENT_4 |  | PV5_STRING_CURRENT_4 | 3 | 0x0C0B
[7 empty] | PV5_VOLTAGE_AND_CURRENT_POINT |  | PV5_VOLTAGE_AND_CURRENT_POINT | 3 | 0x16A8
[7 empty] | PV6_INPUT_CURRENT |  | PV6_INPUT_CURRENT | 3 | 0x0BAD
[7 empty] | PV6_INPUT_POWER |  | PV6_INPUT_POWER | 3 | 0x0BAE
[7 empty] | PV6_INPUT_VOLTAGE |  | PV6_INPUT_VOLTAGE | 3 | 0x0BAC
[7 empty] | PV6_STRING_CURRENT_1 |  | PV6_STRING_CURRENT_1 | 3 | 0x0C0C
[7 empty] | PV6_STRING_CURRENT_2 |  | PV6_STRING_CURRENT_2 | 3 | 0x0C0D
[7 empty] | PV6_STRING_CURRENT_3 |  | PV6_STRING_CURRENT_3 | 3 | 0x0C0E
[7 empty] | PV6_STRING_CURRENT_4 |  | PV6_STRING_CURRENT_4 | 3 | 0x0C0F
[7 empty] | PV6_VOLTAGE_AND_CURRENT_POINT |  | PV6_VOLTAGE_AND_CURRENT_POINT | 3 | 0x1770
[7 empty] | PV7_INPUT_CURRENT |  | PV7_INPUT_CURRENT | 3 | 0x0BA9
[7 empty] | PV7_INPUT_POWER |  | PV7_INPUT_POWER | 3 | 0x0BAA
[7 empty] | PV7_INPUT_VOLTAGE |  | PV7_INPUT_VOLTAGE | 3 | 0x0BA8
[7 empty] | PV7_VOLTAGE_AND_CURRENT_POINT |  | PV7_VOLTAGE_AND_CURRENT_POINT | 3 | 0x1838
[7 empty] | PV8_INPUT_CURRENT |  | PV8_INPUT_CURRENT | 3 | 0x0BA5
[7 empty] | PV8_INPUT_POWER |  | PV8_INPUT_POWER | 3 | 0x0BA6
[7 empty] | PV8_INPUT_VOLTAGE |  | PV8_INPUT_VOLTAGE | 3 | 0x0BA4
[7 empty] | PV8_VOLTAGE_AND_CURRENT_POINT |  | PV8_VOLTAGE_AND_CURRENT_POINT | 3 | 0x1900
[7 empty] | PV9_INPUT_CURRENT |  | PV9_INPUT_CURRENT | 3 | 0x0BA1
[7 empty] | PV9_INPUT_POWER |  | PV9_INPUT_POWER | 3 | 0x0BA2
[7 empty] | PV9_INPUT_VOLTAGE |  | PV9_INPUT_VOLTAGE | 3 | 0x0BA0
[7 empty] | PV9_VOLTAGE_AND_CURRENT_POINT |  | PV9_VOLTAGE_AND_CURRENT_POINT | 3 | 0x19C8
[7 empty] | PV_PARALLEL_OPEN |  | PV_PARALLEL_OPEN | 3 | 0x0007
[7 empty] | PV_POWER |  | PV_POWER | 3 | 0x0B96
[7 empty] | QV_ACTIVE_FACTOR |  | QV_ACTIVE_FACTOR | 3 | 0x0CEB
[7 empty] | QV_CURVE_2 |  | QV_CURVE_2 | 3 | 0x0CFE
[7 empty] | QV_CURVE_REACTIVE_POWER_OVERVOLTAGE_END_VALUE |  | QV_CURVE_REACTIVE_POWER_OVERVOLTAGE_END_VALUE | 3 | 0x0514
[7 empty] | QV_CURVE_REACTIVE_POWER_UNDERVOLTAGE_END_VALUE |  | QV_CURVE_REACTIVE_POWER_UNDERVOLTAGE_END_VALUE | 3 | 0x02BC
[7 empty] | REACTIVE_POWER |  | REACTIVE_POWER | 3 | 0x0BEE
[7 empty] | REG_0DEFAULT_VALUE1HAIXING_CUSTOMIZATION_FORMAT |  | REG_0DEFAULT_VALUE1HAIXING_CUSTOMIZATION_FORMAT | 3 | 0x0C7B
[7 empty] | REG_0_20_THE_DEFAULT_IS_4 |  | REG_0_20_THE_DEFAULT_IS_4 | 3 | 0x0FA9
[7 empty] | REG_0_23_BITS_VALIDENABLE_BY_SETTING_1DISABLE_BY_SETTING_0 |  | REG_0_23_BITS_VALIDENABLE_BY_SETTING_1DISABLE_BY_SETTING_0 | 3 | 0x0C7F
[7 empty] | REG_0_DISABLE_1_ENABLE |  | REG_0_DISABLE_1_ENABLE | 3 | 0x2328
[7 empty] | REG_0_DISTRIBUTIONNETWORK1_TRANSMISSIONNETWORK |  | REG_0_DISTRIBUTIONNETWORK1_TRANSMISSIONNETWORK | 3 | 0x0CAF
[7 empty] | REG_485ADDRESS2 |  | REG_485ADDRESS2 | 3 | 0x0C2D
[7 empty] | REG_485_ADDRESS1 |  | REG_485_ADDRESS1 | 3 | 0x0C30
[7 empty] | REG_485_ADDRESS_SETTINGS_U2 |  | REG_485_ADDRESS_SETTINGS_U2 | 3 | 0x0FB7
[7 empty] | REG_485_ADDRESS_SETTINGS_U4 |  | REG_485_ADDRESS_SETTINGS_U4 | 3 | 0x0FBA
[7 empty] | REG_485_AGREEMENT |  | REG_485_AGREEMENT | 3 | 0x0C2F
[7 empty] | REG_485_PROTOCOL_SETTINGS |  | REG_485_PROTOCOL_SETTINGS | 3 | 0x0FB9
[7 empty] | REMOTE_CONTROL_ENABLE |  | REMOTE_CONTROL_ENABLE | 3 | 0x0C33
[7 empty] | REMOTE_CONTROL_SETTINGS |  | REMOTE_CONTROL_SETTINGS | 3 | 0x0FBD
[7 empty] | REMOTE_OFF |  | REMOTE_OFF | 3 | 0x0010
[7 empty] | RESERVE |  | RESERVE | 3 | 0x0BDA
[7 empty] | RESERVE358REGISTERS |  | RESERVE358REGISTERS | 3 | 0x0FCF
[7 empty] | RESERVE_860_REGISTER |  | RESERVE_860_REGISTER | 3 | 0x0CB4
[7 empty] | REVOKE_REMOTEPOWER_OFF |  | REVOKE_REMOTEPOWER_OFF | 3 | 0x0FA2
[7 empty] | ROTATIONAL_SPEED_OF_FAN_A |  | ROTATIONAL_SPEED_OF_FAN_A | 3 | 0x0BD7
[7 empty] | ROTATIONAL_SPEED_OF_FAN_C |  | ROTATIONAL_SPEED_OF_FAN_C | 3 | 0x0BD9
[7 empty] | RUNNING_TIME |  | RUNNING_TIME | 3 | 0x0C12
[7 empty] | R_PHASE_CURRENT_CALIBRATION_FACTOR |  | R_PHASE_CURRENT_CALIBRATION_FACTOR | 3 | 0x0C40
[7 empty] | R_PHASE_VOLTAGECALIBRATIONCOEFFICIENT_2 |  | R_PHASE_VOLTAGECALIBRATIONCOEFFICIENT_2 | 3 | 0x0CB3
[7 empty] | R_PHASE_VOLTAGE_CALIBRATION_FACTOR |  | R_PHASE_VOLTAGE_CALIBRATION_FACTOR | 3 | 0x0C3D
[7 empty] | SCOPE0100DEFAULT_VALUE50 |  | SCOPE0100DEFAULT_VALUE50 | 3 | 0x0CA3
[7 empty] | SCOPE_0_10_0_50ADEFAULT_VALUE_0_30A |  | SCOPE_0_10_0_50ADEFAULT_VALUE_0_30A | 3 | 0x0C7E
[7 empty] | SCOPE_0_60_3_00ADEFAULT_VALUE_1_20A |  | SCOPE_0_60_3_00ADEFAULT_VALUE_1_20A | 3 | 0x0C7D
[7 empty] | SECOND |  | SECOND | 3 | 0x0C28
[7 empty] | SELF_CHECK_DISABLE |  | SELF_CHECK_DISABLE | 3 | 0x0FC0
[7 empty] | SELF_CHECK_ENABLE |  | SELF_CHECK_ENABLE | 3 | 0x0FBF
[7 empty] | SETTING_INVERTER_SN |  | SETTING_INVERTER_SN | 3 | 0x0CEF
[7 empty] | SETTING_PLC_MAC |  | SETTING_PLC_MAC | 3 | 0x0CFB
[7 empty] | SETTING_VALUE_OF_RATEDPOWER_FOR_ANTI_BACKFLOW |  | SETTING_VALUE_OF_RATEDPOWER_FOR_ANTI_BACKFLOW | 3 | 0x0C7C
[7 empty] | SETTING_VALUE_OF_SELF_CHECK |  | SETTING_VALUE_OF_SELF_CHECK | 3 | 0x0C35
[7 empty] | SET_THE_ACTIVEPOWER |  | SET_THE_ACTIVEPOWER | 3 | 0x0FA4
[7 empty] | SET_THE_POWERFACTOR |  | SET_THE_POWERFACTOR | 3 | 0x0FA3
[7 empty] | SET_THE_REACTIVECONTROL_MODE |  | SET_THE_REACTIVECONTROL_MODE | 3 | 0x0FA6
[7 empty] | SET_THE_REACTIVEPOWER |  | SET_THE_REACTIVEPOWER | 3 | 0x0FA5
[7 empty] | SINK_TEMPERATURE_OVER |  | SINK_TEMPERATURE_OVER | 3 | 0x000D
[7 empty] | SLOW_INCREASE_IN_POWER |  | SLOW_INCREASE_IN_POWER | 3 | 0x0C4D
[7 empty] | SPI2_COMMUNICATION_FAIL |  | SPI2_COMMUNICATION_FAIL | 3 | 0x0013
[7 empty] | SPI_COMMUNICATION_FAIL |  | SPI_COMMUNICATION_FAIL | 3 | 0x0012
[7 empty] | START_DELAY_SETTINGS |  | START_DELAY_SETTINGS | 3 | 0x0FAF
[7 empty] | STRING_TEST_THRESHOLD_VALUE_SETTINGS |  | STRING_TEST_THRESHOLD_VALUE_SETTINGS | 3 | 0x0FBE
[7 empty] | S_PHASE_CALIBRATION_FACTOR |  | S_PHASE_CALIBRATION_FACTOR | 3 | 0x0C41
[7 empty] | S_PHASE_VOLTAGE_CALIBRATION_FACTOR |  | S_PHASE_VOLTAGE_CALIBRATION_FACTOR | 3 | 0x0C3E
[7 empty] | TABLE_3_1_16 |  | TABLE_3_1_16 | 3 | 0x112F
[7 empty] | TABLE_3_3_4 |  | TABLE_3_3_4 | 3 | 0x0C37
[7 empty] | THE_MACHINE_COMES |  | THE_MACHINE_COMES | 3 | 0x0FC5
[7 empty] | THE_MACHINE_COMESWITH_SATURATIONCALCULATION |  | THE_MACHINE_COMESWITH_SATURATIONCALCULATION | 3 | 0x0FC4
[7 empty] | THREE_PHASE_SETTINGS |  | THREE_PHASE_SETTINGS | 3 | 0x0FBC
[7 empty] | THREE_PHASE_SYSTEM |  | THREE_PHASE_SYSTEM | 3 | 0x0C32
[7 empty] | T_PHASE_CURRENT_CALIBRATION_FACTOR |  | T_PHASE_CURRENT_CALIBRATION_FACTOR | 3 | 0x0C42
[7 empty] | T_PHASE_VOLTAGE_CALIBRATION_FACTOR |  | T_PHASE_VOLTAGE_CALIBRATION_FACTOR | 3 | 0x0C3F
[7 empty] | UNDERFREQUENCYAMPLIFICATIONCOEFFICIENT |  | UNDERFREQUENCYAMPLIFICATIONCOEFFICIENT | 3 | 0x0CA2
[7 empty] | UNDERFREQUENCYINCREASE_SLOPE |  | UNDERFREQUENCYINCREASE_SLOPE | 3 | 0x0C4A
[7 empty] | UPPER_GRID_FREQUENCYTHRESHOLD |  | UPPER_GRID_FREQUENCYTHRESHOLD | 3 | 0x0BE8
[7 empty] | UPPER_GRID_VOLTAGETHRESHOLD |  | UPPER_GRID_VOLTAGETHRESHOLD | 3 | 0x0BE6
[7 empty] | UPPER_LIMIT_OFFREQUENCY_RESPONSEDEAD_BAND |  | UPPER_LIMIT_OFFREQUENCY_RESPONSEDEAD_BAND | 3 | 0x0C9F
[7 empty] | VALUE_OF_N |  | VALUE_OF_N | 3 | 0x0C22
[7 empty] | VOLTAGE_CONSISTENT_FAULT |  | VOLTAGE_CONSISTENT_FAULT | 3 | 0x0016
[7 empty] | WEEK |  | WEEK | 3 | 0x0C29
[7 empty] | WEEK_GENERATION |  | WEEK_GENERATION | 3 | 0x0C1C
[7 empty] | YEAR |  | YEAR | 3 | 0x0C23