## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Solarize
프로토콜 버전
설비 타입 | inverter
MPPT | 9
String | 24
String 모니터링 | Yes
IV Scan | Yes
IV Data Points | 64
IV Trackers | 9
원본 파일 | Solarize-PV_Modbus_Protocol-Korea-V1.2.4.pdf
추출 일시 | 2026-04-09 12:07
H01 매칭 | 60/60
DER 매칭 | 33/33
추출 레지스터 | 316
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INNER_TEMP | 0x101C | 03 | S16 | °C 1 | RO | temperature | Inner Temperature
2 | DAILY_ENERGY | 0x1027 | 03 | U32 | Wh | RO | daily_energy | Today Energy
3 | DECIMALS_OF_TOTAL_ENERGY | 0x104C | 03 | U16 |  | RO | cumulative_energy_low | Decimals of total energy ¦ Wh
4 | L1_N_PHASE_VOLTAGE_OF_GRID | 0x131A | 03 | U16 | V 0.1 | RO |  | L1-N phase voltage of grid
5 | L2_N_PHASE_VOLTAGE_OF_GRID | 0x131B | 03 | U16 | V 0.1 | RO |  | L2-N phase voltage of grid
6 | L3_N_PHASE_VOLTAGE_OF_GRID | 0x131C | 03 | U16 | V 0.1 | RO |  | L3-N phase voltage of grid
7 | L1_N_PHASE_VOLTAGE_OF_LOAD | 0x1323 | 03 | U16 | V 0.1 | RO |  | L1-N phase voltage of load
8 | L2_N_PHASE_VOLTAGE_OF_LOAD | 0x1324 | 03 | U16 | V 0.1 | RO |  | L2-N phase voltage of load
9 | L3_N_PHASE_VOLTAGE_OF_LOAD | 0x1325 | 03 | U16 | V 0.1 | RO |  | L3-N phase voltage of load
10 | Device Model name | 0x1A00 | 03 | STRINGING |  | RO |  | Ex.：PV 30KTL
11 | Device Serial number | 0x1A10 | 03 | STRINGING |  | RO |  | Ex.：1234-123456789
12 | Master firmware version | 0x1A1C | 03 | STRINGING |  | RO |  | Ex.：123456
13 | Slave firmware version | 0x1A26 | 03 | STRINGING |  | RO |  | Ex.：123456
14 | NOMINAL_VOLTAGE | 0x1A44 | 03 | U16 |  | RO |  | Nominal Voltage ¦ Ex.：2200 = 220V
15 | NOMINAL_FREQUENCY | 0x1A45 | 03 | U16 |  | RO |  | Nominal Frequency ¦ Ex.：5000 = 50Hz
16 | Nominal Active Power(Low word) | 0x1A46 | 03 | U16 | W 1 | RO |  | Ex.：1500 = 1500W
17 | GRID_PHASE_NUMBER | 0x1A48 | 03 | U16 |  | RO |  | Grid Phase Number ¦ 1=single phase2=split phase3=three phases
18 | Nominal Active Power(High word) | 0x1A4E | 03 | U16 | W 1 | RO |  | Ex.：1 = (1*65536)W
19 | EMS Firmware Version | 0x1A60 | 03 | STRINGING |  | RO |  | Ex.：123456
20 | LCD firmware version | 0x1A8E | 03 | STRINGING |  | RO |  | Ex.：123456
21 | [0, Pnom]Pnom : nominal power | 0x30B9 | 03 | U32 |  | RW
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INVERTER_MODE | 0x101D | 03 | U16 |  | RO | inverter_status | Inverter Mode ¦ Inverter Mode Table
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | ERROR_CODE1 | 0x101E | 03 | U16 |  | RO |  | Error Code1 ¦ Error Code Table 1
2 | ERROR_CODE2 | 0x101F | 03 | U16 |  | RO |  | Error Code2 ¦ Error Code Table 2
3 | ERROR_CODE3 | 0x1020 | 03 | U16 |  | RO |  | Error Code3 ¦ Error Code Table 3

## 2_H01
H01 모니터링 매칭 — 60/60
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | PDF_PHASE | O | 0x1001 | L1 Voltage | U16 | V | 0.1 | 상전압 사용
2 | s_voltage | PDF_PHASE | O | 0x1006 | L2 Voltage | U16 | V | 0.1 | 상전압 사용
3 | t_voltage | PDF_PHASE | O | 0x100B | L3 Voltage | U16 | V | 0.1 | 상전압 사용
4 | r_current | PDF_PHASE | O | 0x1002 | L1_CURRENT | U16 | A | 0.01 | 상전압 사용
5 | s_current | PDF_PHASE | O | 0x1007 | L2_CURRENT | U16 | A | 0.01 | 상전압 사용
6 | t_current | PDF_PHASE | O | 0x100C | L3_CURRENT | U16 | A | 0.01 | 상전압 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x1048 | PV_POWER | U32 | W | 0.1
13 | cumulative_energy | PDF | O | 0x1021 | CUMULATIVE_ENERGY | U32 | kWh |  | kWh→Wh (*1000)
14 | cumulative_energy_low | PDF | O | 0x104C | DECIMALS_OF_TOTAL_ENERGY | U16
15 | status | PDF | O | 0x101D | INVERTER_MODE | U16 |  |  | 6=PV6 fuse open d, 7=PV7 fuse open d, 8=PV8 fuse open d
16 | alarm1 | PDF | O | 0x101E | ERROR_CODE1 | U16 |  |  | 0=Inverter over d, 1=Inverter relay , 2=Remote off, 3=Inverter over t, 4=GFCI abnormal, 5=PV string rever... (+10)
17 | alarm2 | PDF | O | 0x101F | ERROR_CODE2 | U16 |  |  | 136=String 1-2 curr, 137=String 1-3 curr, 138=String 1-4 curr, 139=Tracker 2 volta, 140=String 2-1 curr, 141=String 2-2 curr... (+33)
18 | alarm3 | PDF | O | 0x1020 | ERROR_CODE3 | U16
19 | mppt1_voltage | PDF | O | 0x1010 | MPPT1_VOLTAGE | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x1011 | MPPT1_CURRENT | S16 | A | 0.01
21 | mppt2_voltage | PDF | O | 0x1014 | MPPT2_VOLTAGE | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x1015 | MPPT2_CURRENT | S16 | A | 0.01
23 | mppt3_voltage | PDF | O | 0x1018 | MPPT3_VOLTAGE | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x1019 | MPPT3_CURRENT | S16 | A | 0.01
25 | mppt4_voltage | PDF | O | 0x103E | MPPT4_VOLTAGE | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x103F | MPPT4_CURRENT | S16 | A | 0.01
27 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
29 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
31 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
33 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
35 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
36 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
37 | string1_current | PDF | O | 0x1051 | STRING1_CURRENT | S16 | A | 0.01
38 | string2_current | PDF | O | 0x1053 | STRING2_CURRENT | S16 | A | 0.01
39 | string3_current | PDF | O | 0x1055 | STRING3_CURRENT | S16 | A | 0.01
40 | string4_current | PDF | O | 0x1057 | STRING4_CURRENT | S16 | A | 0.01
41 | string5_current | PDF | O | 0x1059 | STRING5_CURRENT | S16 | A | 0.01
42 | string6_current | PDF | O | 0x105B | STRING6_CURRENT | S16 | A | 0.01
43 | string7_current | PDF | O | 0x105D | STRING7_CURRENT | S16 | A | 0.01
44 | string8_current | PDF | O | 0x105F | STRING8_CURRENT | S16 | A | 0.01
45 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
46 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
47 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
48 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
49 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
50 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
51 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
52 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
53 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
54 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
55 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
56 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
57 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
58 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
59 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
60 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 9ch / String 24ch
MPPT 채널 수 | 9
String 채널 수 | 24
String 모니터링 | Yes
MPPT 채널 H01 매칭 (18개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x1010 | MPPT1_VOLTAGE | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x1011 | MPPT1_CURRENT | S16 | A | 0.01
3 | mppt2_voltage | PDF | O | 0x1014 | MPPT2_VOLTAGE | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x1015 | MPPT2_CURRENT | S16 | A | 0.01
5 | mppt3_voltage | PDF | O | 0x1018 | MPPT3_VOLTAGE | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x1019 | MPPT3_CURRENT | S16 | A | 0.01
7 | mppt4_voltage | PDF | O | 0x103E | MPPT4_VOLTAGE | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x103F | MPPT4_CURRENT | S16 | A | 0.01
9 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
11 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
13 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
15 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
17 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
18 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
String 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x1051 | STRING1_CURRENT | S16 | A | 0.01
2 | string2_current | PDF | O | 0x1053 | STRING2_CURRENT | S16 | A | 0.01
3 | string3_current | PDF | O | 0x1055 | STRING3_CURRENT | S16 | A | 0.01
4 | string4_current | PDF | O | 0x1057 | STRING4_CURRENT | S16 | A | 0.01
5 | string5_current | PDF | O | 0x1059 | STRING5_CURRENT | S16 | A | 0.01
6 | string6_current | PDF | O | 0x105B | STRING6_CURRENT | S16 | A | 0.01
7 | string7_current | PDF | O | 0x105D | STRING7_CURRENT | S16 | A | 0.01
8 | string8_current | PDF | O | 0x105F | STRING8_CURRENT | S16 | A | 0.01
9 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
10 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
11 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
12 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
13 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
14 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
15 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
16 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
17 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
18 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
19 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
20 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
21 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
22 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
23 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
24 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01
MONITORING 전체 (168개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | POWER_FACTOR | 0x0000 | 03 | U16 |  | RO | power_factor
2 | START_BIT | 0x0001 | 03 | U16 |  | RO
3 | Register number | 0x0002 | 03 | U16 |  | RO
4 | READ_REGISTER_ADDRESS | 0x0003 | 03 | U16 |  | RO
5 | GFCI_ABNORMAL | 0x0004 | 03 | U16 |  | RO
6 | PV string reverse | 0x0005 | 03 | STRINGING |  | RO
7 | REG_0X07 | 0x0007 | 03 | U16 |  | RO
8 | PV_STRING_COUNT | 0x0008 | 03 | U16 |  | RO
9 | DC_LINK_OVER_VOLTAGE | 0x0009 | 03 | U16 |  | RO
10 | INTERNAL_COMMUNICATION_ERROR | 0x000A | 03 | U16 |  | RO
11 | SOFTWARE_INCOMPATIBILITY | 0x000B | 03 | U16 |  | RO
12 | INTERNAL_STORAGE_ERROR | 0x000C | 03 | U16 |  | RO
13 | L2_VOLTAGE | 0x000D | 03 | U16 |  | RO | s_voltage
14 | L3_VOLTAGE | 0x000E | 03 | U16 |  | RO
15 | FREQUENCY | 0x000F | 03 | U16 |  | RO
16 | WRITE_MULTIPLE_REGISTER_ADDRESS | 0x0010 | 03 | U16 |  | WO
17 | L1_VOLTAGE | 0x0026 | 03 | U16 |  | RO | r_voltage
18 | L1 Voltage | 0x1001 | 03 | U16 | V 0.1 | RO | r_voltage
19 | L1_CURRENT | 0x1002 | 03 | U16 | A 0.01 | RO | r_current
20 | L1_POWER | 0x1003 | 03 | S32 | W 0.1 | RO
21 | FREQUENCY | 0x1005 | 03 | U16 | Hz 0.01 | RO | frequency
22 | L2 Voltage | 0x1006 | 03 | U16 | V 0.1 | RO | s_voltage
23 | L2_CURRENT | 0x1007 | 03 | U16 | A 0.01 | RO | s_current
24 | L2_POWER | 0x1008 | 03 | S32 | W 0.1 | RO
25 | L2_FREQUENCY | 0x100A | 03 | U16 | Hz 0.01 | RO | frequency
26 | L3 Voltage | 0x100B | 03 | U16 | V 0.1 | RO | t_voltage
27 | L3_CURRENT | 0x100C | 03 | U16 | A 0.01 | RO | t_current
28 | L3_POWER | 0x100D | 03 | S32 | W 0.1 | RO
29 | L3_FREQUENCY | 0x100F | 03 | U16 | Hz 0.01 | RO | frequency
30 | MPPT1_VOLTAGE | 0x1010 | 03 | U16 | V 0.1 | RO | mppt1_voltage
31 | MPPT1_CURRENT | 0x1011 | 03 | S16 | A 0.01 | RO | mppt1_current
32 | MPPT1_POWER | 0x1012 | 03 | U32 | W 0.1 | RO | mppt1_power
33 | MPPT2_VOLTAGE | 0x1014 | 03 | U16 | V 0.1 | RO | mppt2_voltage
34 | MPPT2_CURRENT | 0x1015 | 03 | S16 | A 0.01 | RO | mppt2_current
35 | MPPT2_POWER | 0x1016 | 03 | U32 | W 0.1 | RO | mppt2_power
36 | MPPT3_VOLTAGE | 0x1018 | 03 | U16 | V 0.1 | RO | mppt3_voltage
37 | MPPT3_CURRENT | 0x1019 | 03 | S16 | A 0.01 | RO | mppt3_current
38 | MPPT3_POWER | 0x101A | 03 | U32 | W 0.1 | RO | mppt3_power
39 | CUMULATIVE_ENERGY | 0x1021 | 03 | U32 | kWh | RO | cumulative_energy
40 | TOTAL_GENERATION_TIME | 0x1023 | 03 | U32 |  | RO
41 | AC_POWER | 0x1037 | 03 | S32 | W 0.1 | RO | ac_power
42 | GRID_TOTAL_REACTIVE_POWER | 0x1039 | 03 | S32 |  | RO | ac_power
43 | PV_TODAY_PEAK_POWER | 0x103B | 03 | S32 | W 0.1 | RO
44 | Power Factor | 0x103D | 03 | S16 |  | RO | power_factor
45 | MPPT4_VOLTAGE | 0x103E | 03 | U16 | V 0.1 | RO | mppt4_voltage
46 | MPPT4_CURRENT | 0x103F | 03 | S16 | A 0.01 | RO | mppt4_current
47 | MPPT4_POWER | 0x1040 | 03 | U32 | W 0.1 | RO | mppt4_power
48 | PV_POWER | 0x1048 | 03 | U32 | W 0.1 | RO | pv_power
49 | STRING1_VOLTAGE | 0x1050 | 03 | U16 | V 0.1 | RO | string1_voltage
50 | STRING1_CURRENT | 0x1051 | 03 | S16 | A 0.01 | RO | string1_current
51 | STRING2_VOLTAGE | 0x1052 | 03 | U16 | V 0.1 | RO | string2_voltage
52 | STRING2_CURRENT | 0x1053 | 03 | S16 | A 0.01 | RO | string2_current
53 | STRING3_VOLTAGE | 0x1054 | 03 | U16 | V 0.1 | RO | string3_voltage
54 | STRING3_CURRENT | 0x1055 | 03 | S16 | A 0.01 | RO | string3_current
55 | STRING4_VOLTAGE | 0x1056 | 03 | U16 | V 0.1 | RO | string4_voltage
56 | STRING4_CURRENT | 0x1057 | 03 | S16 | A 0.01 | RO | string4_current
57 | STRING5_VOLTAGE | 0x1058 | 03 | U16 | V 0.1 | RO | string5_voltage
58 | STRING5_CURRENT | 0x1059 | 03 | S16 | A 0.01 | RO | string5_current
59 | STRING6_VOLTAGE | 0x105A | 03 | U16 | V 0.1 | RO | string6_voltage
60 | STRING6_CURRENT | 0x105B | 03 | S16 | A 0.01 | RO | string6_current
61 | STRING7_VOLTAGE | 0x105C | 03 | U16 | V 0.1 | RO | string7_voltage
62 | STRING7_CURRENT | 0x105D | 03 | S16 | A 0.01 | RO | string7_current
63 | STRING8_VOLTAGE | 0x105E | 03 | U16 | V 0.1 | RO | string8_voltage
64 | STRING8_CURRENT | 0x105F | 03 | S16 | A 0.01 | RO | string8_current
65 | String9 input voltage | 0x1060 | 03 | U16 | V 0.1 | RO | string9_voltage
66 | String9 input current | 0x1061 | 03 | S16 | A 0.01 | RO | string9_current
67 | String10 input voltage | 0x1062 | 03 | U16 | V 0.1 | RO | string10_voltage
68 | String10 input current | 0x1063 | 03 | S16 | A 0.01 | RO | string10_current
69 | String11 input voltage | 0x1064 | 03 | U16 | V 0.1 | RO | string11_voltage
70 | String11 input current | 0x1065 | 03 | S16 | A 0.01 | RO | string11_current
71 | String12 input voltage | 0x1066 | 03 | U16 | V 0.1 | RO | string12_voltage
72 | String12 input current | 0x1067 | 03 | S16 | A 0.01 | RO | string12_current
73 | String13 input voltage | 0x1068 | 03 | U16 | V 0.1 | RO | string13_voltage
74 | String13 input current | 0x1069 | 03 | S16 | A 0.01 | RO | string13_current
75 | String14 input voltage | 0x106A | 03 | U16 | V 0.1 | RO | string14_voltage
76 | String14 input current | 0x106B | 03 | S16 | A 0.01 | RO | string14_current
77 | String15 input voltage | 0x106C | 03 | U16 | V 0.1 | RO | string15_voltage
78 | String15 input current | 0x106D | 03 | S16 | A 0.01 | RO | string15_current
79 | String16 input voltage | 0x106E | 03 | U16 | V 0.1 | RO | string16_voltage
80 | String16 input current | 0x106F | 03 | S16 | A 0.01 | RO | string16_current
81 | String17 input voltage | 0x1070 | 03 | U16 | V 0.1 | RO | string17_voltage
82 | String17 input current | 0x1071 | 03 | S16 | A 0.01 | RO | string17_current
83 | String18 input voltage | 0x1072 | 03 | U16 | V 0.1 | RO | string18_voltage
84 | String18 input current | 0x1073 | 03 | S16 | A 0.01 | RO | string18_current
85 | String19 input voltage | 0x1074 | 03 | U16 | V 0.1 | RO | string19_voltage
86 | String19 input current | 0x1075 | 03 | S16 | A 0.01 | RO | string19_current
87 | String20 input voltage | 0x1076 | 03 | U16 | V 0.1 | RO | string20_voltage
88 | String20 input current | 0x1077 | 03 | S16 | A 0.01 | RO | string20_current
89 | String21 input voltage | 0x1078 | 03 | U16 | V 0.1 | RO | string21_voltage
90 | String21 input current | 0x1079 | 03 | S16 | A 0.01 | RO | string21_current
91 | String22 input voltage | 0x107A | 03 | U16 | V 0.1 | RO | string22_voltage
92 | String22 input current | 0x107B | 03 | S16 | A 0.01 | RO | string22_current
93 | String23 input voltage | 0x107C | 03 | U16 | V 0.1 | RO | string23_voltage
94 | String23 input current | 0x107D | 03 | S16 | A 0.01 | RO | string23_current
95 | String24 input voltage | 0x107E | 03 | U16 | V 0.1 | RO | string24_voltage
96 | String24 input current | 0x107F | 03 | S16 | A 0.01 | RO | string24_current
97 | MPPT5 Voltage | 0x1080 | 03 | U16 | V 0.1 | RO | mppt5_voltage
98 | MPPT5 Current | 0x1081 | 03 | S16 | A 0.01 | RO | mppt5_current
99 | MPPT5 Power | 0x1082 | 03 | U32 | W 0.1 | RO | mppt5_power
100 | MPPT6 Voltage | 0x1084 | 03 | U16 | V 0.1 | RO | mppt6_voltage
101 | MPPT6 Current | 0x1085 | 03 | S16 | A 0.01 | RO | mppt6_current
102 | MPPT6 Power | 0x1086 | 03 | U32 | W 0.1 | RO | mppt6_power
103 | MPPT7 Voltage | 0x1088 | 03 | U16 | V 0.1 | RO | mppt7_voltage
104 | MPPT7 Current | 0x1089 | 03 | S16 | A 0.01 | RO | mppt7_current
105 | MPPT7 Power | 0x108A | 03 | U32 | W 0.1 | RO | mppt7_power
106 | MPPT8 Voltage | 0x108C | 03 | U16 | V 0.1 | RO | mppt8_voltage
107 | MPPT8 Current | 0x108D | 03 | S16 | A 0.01 | RO | mppt8_current
108 | MPPT8 Power | 0x108E | 03 | U32 | W 0.1 | RO | mppt8_power
109 | MPPT9 Voltage | 0x1090 | 03 | U16 | V 0.1 | RO | mppt9_voltage
110 | MPPT9 Current | 0x1091 | 03 | S16 | A 0.01 | RO | mppt9_current
111 | MPPT9 Power | 0x1092 | 03 | U32 | W 0.1 | RO | mppt9_power
112 | External fan speed dutypercentage | 0x120C | 03 | U16 |  | RO
113 | Q (Reference Output reactivepower) | 0x1226 | 03 | S16 |  | RO
114 | L1 watt of grid | 0x1300 | 03 | S32 | W 0.1 | RO
115 | L2 watt of grid | 0x1302 | 03 | S32 | W 0.1 | RO
116 | L3 watt of grid | 0x1304 | 03 | S32 | W 0.1 | RO
117 | ACCUMULATED_ENERGY_OFIMPORT | 0x1306 | 03 | U32 | Wh 10 | RO | cumulative_energy
118 | ACCUMULATED_ENERGY_OFEXPORT | 0x1308 | 03 | U32 | Wh 10 | RO | cumulative_energy
119 | L1 watt of load | 0x130A | 03 | U32 | W 0.1 | RO
120 | L2 watt of load | 0x130C | 03 | U32 | W 0.1 | RO
121 | L3 watt of load | 0x130E | 03 | U32 | W 0.1 | RO
122 | ACCUMULATED_ENERGY_OF_LOAD | 0x1310 | 03 | U32 | Wh 10 | RO | cumulative_energy
123 | L1_CURRENT_OF_GRID | 0x131D | 03 | S32 | A 0.01 | RO
124 | L2_CURRENT_OF_GRID | 0x131F | 03 | S32 | A 0.01 | RO
125 | L3_CURRENT_OF_GRID | 0x1321 | 03 | S32 | A 0.01 | RO
126 | L1_CURRENT_OF_LOAD | 0x1326 | 03 | S32 | A 0.01 | RO
127 | L2_CURRENT_OF_LOAD | 0x1328 | 03 | S32 | A 0.01 | RO
128 | L3_CURRENT_OF_LOAD | 0x132A | 03 | S32 | A 0.01 | RO
129 | Today import Energy | 0x1332 | 03 | U32 | Wh 10 | RO
130 | Today export Energy | 0x1334 | 03 | U32 | Wh 10 | RO
131 | Today load Energy | 0x1336 | 03 | U32 | Wh 10 | RO
132 | FREQUENCY | 0x1338 | 03 | U16 | Hz 0.01 | RO | frequency
133 | MPPT_NUMBER | 0x1A3B | 03 | U16 |  | RO
134 | String 1-3 current | 0x80C0 | 03 | STRINGING | A 0.01 | RO
135 | String 1-4 current | 0x8100 | 03 | STRINGING | A 0.01 | RO
136 | String 2-3 current | 0x8200 | 03 | STRINGING | A 0.01 | RO
137 | String 2-4 current | 0x8240 | 03 | STRINGING | A 0.01 | RO
138 | String 3-3 current | 0x8340 | 03 | STRINGING | A 0.01 | RO
139 | String 3-4 current | 0x8380 | 03 | STRINGING | A 0.01 | RO
140 | String 4-3 current | 0x8480 | 03 | STRINGING | A 0.01 | RO
141 | String 4-4 current | 0x84C0 | 03 | STRINGING | A 0.01 | RO
142 | Tracker 5 voltage | 0x8500 | 03 | U16 | V 0.1 | RO
143 | String 5-1 current | 0x8540 | 03 | STRINGING | A 0.01 | RO
144 | String 5-2 current | 0x8580 | 03 | STRINGING | A 0.01 | RO
145 | String 5-3 current | 0x85C0 | 03 | STRINGING | A 0.01 | RO
146 | String 5-4 current | 0x8600 | 03 | STRINGING | A 0.01 | RO
147 | Tracker 6 voltage | 0x8640 | 03 | U16 | V 0.1 | RO
148 | String 6-1 current | 0x8680 | 03 | STRINGING | A 0.01 | RO
149 | String 6-2 current | 0x86C0 | 03 | STRINGING | A 0.01 | RO
150 | String 6-3 current | 0x8700 | 03 | STRINGING | A 0.01 | RO
151 | String 6-4 current | 0x8740 | 03 | STRINGING | A 0.01 | RO
152 | Tracker 7 voltage | 0x8780 | 03 | U16 | V 0.1 | RO
153 | String 7-1 current | 0x87C0 | 03 | STRINGING | A 0.01 | RO
154 | String 7-2 current | 0x8800 | 03 | STRINGING | A 0.01 | RO
155 | String 7-3 current | 0x8840 | 03 | STRINGING | A 0.01 | RO
156 | String 7-4 current | 0x8880 | 03 | STRINGING | A 0.01 | RO
157 | Tracker 8 voltage | 0x88C0 | 03 | U16 | V 0.1 | RO
158 | String 8-1 current | 0x8900 | 03 | STRINGING | A 0.01 | RO
159 | String 8-2 current | 0x8940 | 03 | STRINGING | A 0.01 | RO
160 | String 8-3 current | 0x8980 | 03 | STRINGING | A 0.01 | RO
161 | String 8-4 current | 0x89C0 | 03 | STRINGING | A 0.01 | RO
162 | Tracker 9 voltage | 0x8A00 | 03 | U16 | V 0.1 | RO
163 | String 9-1 current | 0x8A40 | 03 | STRINGING | A 0.01 | RO
164 | String 9-2 current | 0x8A80 | 03 | STRINGING | A 0.01 | RO
165 | String 9-3 current | 0x8AC0 | 03 | STRINGING | A 0.01 | RO
166 | String 9-4 current | 0x8B00 | 03 | STRINGING | A 0.01 | RO
167 | history log 0 | 0xB600 | 03 | U16 |  | RO
168 | history log 127 | 0xB77D | 03 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## 5_IV
IV Scan 매핑 — data_points=64
IV Scan Command | 0x600D
Data Points | 64
Trackers | 9
Strings/Tracker | 4
IV Scan Command
Name | Address | Type | R/W | Description
IV_CURVE_SCAN | 0x600D | U16 | RW | W: 0=Stop, 1=Start / R: 0=Idle, 1=Running, 2=Finished
IV Data 레지스터 매핑
No | Type | Name | Address | Regs | Data Type | Scale
1 | Tracker Voltage | Tracker 1 voltage | 0x8000 | 64 | U16 | 0.1V
2 | String Current | String 1-1 current | 0x8040 | 64 | S16 | 0.01A
3 | String Current | String 1-2 current | 0x8080 | 64 | S16 | 0.01A
4 | String Current | String 1-3 current | 0x80C0 | 64 | S16 | 0.01A
5 | String Current | String 1-4 current | 0x8100 | 64 | S16 | 0.01A
6 | Tracker Voltage | Tracker 2 voltage | 0x8140 | 64 | U16 | 0.1V
7 | String Current | String 2-1 current | 0x8180 | 64 | S16 | 0.01A
8 | String Current | String 2-2 current | 0x81C0 | 64 | S16 | 0.01A
9 | String Current | String 2-3 current | 0x8200 | 64 | S16 | 0.01A
10 | String Current | String 2-4 current | 0x8240 | 64 | S16 | 0.01A
11 | Tracker Voltage | Tracker 3 voltage | 0x8280 | 64 | U16 | 0.1V
12 | String Current | String 3-1 current | 0x82C0 | 64 | S16 | 0.01A
13 | String Current | String 3-2 current | 0x8300 | 64 | S16 | 0.01A
14 | String Current | String 3-3 current | 0x8340 | 64 | S16 | 0.01A
15 | String Current | String 3-4 current | 0x8380 | 64 | S16 | 0.01A
16 | Tracker Voltage | Tracker 4 voltage | 0x83C0 | 64 | U16 | 0.1V
17 | String Current | String 4-1 current | 0x8400 | 64 | S16 | 0.01A
18 | String Current | String 4-2 current | 0x8440 | 64 | S16 | 0.01A
19 | String Current | String 4-3 current | 0x8480 | 64 | S16 | 0.01A
20 | String Current | String 4-4 current | 0x84C0 | 64 | S16 | 0.01A
21 | Tracker Voltage | Tracker 5 voltage | 0x8500 | 64 | U16 | 0.1V
22 | String Current | String 5-1 current | 0x8540 | 64 | S16 | 0.01A
23 | String Current | String 5-2 current | 0x8580 | 64 | S16 | 0.01A
24 | String Current | String 5-3 current | 0x85C0 | 64 | S16 | 0.01A
25 | String Current | String 5-4 current | 0x8600 | 64 | S16 | 0.01A
26 | Tracker Voltage | Tracker 6 voltage | 0x8640 | 64 | U16 | 0.1V
27 | String Current | String 6-1 current | 0x8680 | 64 | S16 | 0.01A
28 | String Current | String 6-2 current | 0x86C0 | 64 | S16 | 0.01A
29 | String Current | String 6-3 current | 0x8700 | 64 | S16 | 0.01A
30 | String Current | String 6-4 current | 0x8740 | 64 | S16 | 0.01A
31 | Tracker Voltage | Tracker 7 voltage | 0x8780 | 64 | U16 | 0.1V
32 | String Current | String 7-1 current | 0x87C0 | 64 | S16 | 0.01A
33 | String Current | String 7-2 current | 0x8800 | 64 | S16 | 0.01A
34 | String Current | String 7-3 current | 0x8840 | 64 | S16 | 0.01A
35 | String Current | String 7-4 current | 0x8880 | 64 | S16 | 0.01A
36 | Tracker Voltage | Tracker 8 voltage | 0x88C0 | 64 | U16 | 0.1V
37 | String Current | String 8-1 current | 0x8900 | 64 | S16 | 0.01A
38 | String Current | String 8-2 current | 0x8940 | 64 | S16 | 0.01A
39 | String Current | String 8-3 current | 0x8980 | 64 | S16 | 0.01A
40 | String Current | String 8-4 current | 0x89C0 | 64 | S16 | 0.01A
41 | Tracker Voltage | Tracker 9 voltage | 0x8A00 | 64 | U16 | 0.1V
42 | String Current | String 9-1 current | 0x8A40 | 64 | S16 | 0.01A
43 | String Current | String 9-2 current | 0x8A80 | 64 | S16 | 0.01A
44 | String Current | String 9-3 current | 0x8AC0 | 64 | S16 | 0.01A
45 | String Current | String 9-4 current | 0x8B00 | 64 | S16 | 0.01A

## INFO_MAPPING
INFO_MAPPING — Model / Serial Number 수동 매핑
※ D열에서 매핑할 레지스터를 선택하세요. E~G열은 추천 후보, H열은 전체 INFO 후보 목록.
No | Field | 설명 | 매칭된 레지스터 (주소) | 추천 후보 1 | 추천 후보 2 | 추천 후보 3 | 전체 레지스터 목록 | FC
1 | model | Model 정보 (제조사/타입/제품명) | DEVICE_MODEL_NAME (0x1A00) |  |  |  | ACCUMULATED_ENERGY_OFEXPORT | 3 | ACCUMULATED_ENERGY_OFEXPORT | 3 | 0x1308 | pdf
2 | sn | Serial Number / Firmware Version | DEVICE_SERIAL_NUMBER (0x1A10) |  |  |  | ACCUMULATED_ENERGY_OFIMPORT | 3 | ACCUMULATED_ENERGY_OFIMPORT | 3 | 0x1306 | pdf
[7 empty] | ACCUMULATED_ENERGY_OF_LOAD |  | ACCUMULATED_ENERGY_OF_LOAD | 3 | 0x1310
[7 empty] | AC_POWER |  | AC_POWER | 3 | 0x1037
[7 empty] | CUMULATIVE_ENERGY |  | CUMULATIVE_ENERGY | 3 | 0x1021
[7 empty] | DAILY_ENERGY |  | DAILY_ENERGY | 3 | 0x1027
[7 empty] | DC_LINK_OVER_VOLTAGE |  | DC_LINK_OVER_VOLTAGE | 3 | 0x0009
[7 empty] | DECIMALS_OF_TOTAL_ENERGY |  | DECIMALS_OF_TOTAL_ENERGY | 3 | 0x104C
[7 empty] | DEVICE_MODEL_NAME |  | DEVICE_MODEL_NAME | 3 | 0x1A00
[7 empty] | DEVICE_SERIAL_NUMBER |  | DEVICE_SERIAL_NUMBER | 3 | 0x1A10
[7 empty] | EMS_FIRMWARE_VERSION |  | EMS_FIRMWARE_VERSION | 3 | 0x1A60
[7 empty] | ERROR_CODE1 |  | ERROR_CODE1 | 3 | 0x101E
[7 empty] | ERROR_CODE2 |  | ERROR_CODE2 | 3 | 0x101F
[7 empty] | ERROR_CODE3 |  | ERROR_CODE3 | 3 | 0x1020
[7 empty] | EXTERNAL_FAN_SPEED_DUTYPERCENTAGE |  | EXTERNAL_FAN_SPEED_DUTYPERCENTAGE | 3 | 0x120C
[7 empty] | FREQUENCY |  | FREQUENCY | 3 | 0x1005
[7 empty] | GFCI_ABNORMAL |  | GFCI_ABNORMAL | 3 | 0x0004
[7 empty] | GRID_PHASE_NUMBER |  | GRID_PHASE_NUMBER | 3 | 0x1A48
[7 empty] | GRID_TOTAL_REACTIVE_POWER |  | GRID_TOTAL_REACTIVE_POWER | 3 | 0x1039
[7 empty] | HISTORY_LOG_0 |  | HISTORY_LOG_0 | 3 | 0xB600
[7 empty] | HISTORY_LOG_127 |  | HISTORY_LOG_127 | 3 | 0xB77D
[7 empty] | INNER_TEMP |  | INNER_TEMP | 3 | 0x101C
[7 empty] | INTERNAL_COMMUNICATION_ERROR |  | INTERNAL_COMMUNICATION_ERROR | 3 | 0x000A
[7 empty] | INTERNAL_STORAGE_ERROR |  | INTERNAL_STORAGE_ERROR | 3 | 0x000C
[7 empty] | INVERTER_MODE |  | INVERTER_MODE | 3 | 0x101D
[7 empty] | L1_CURRENT |  | L1_CURRENT | 3 | 0x1002
[7 empty] | L1_CURRENT_OF_GRID |  | L1_CURRENT_OF_GRID | 3 | 0x131D
[7 empty] | L1_CURRENT_OF_LOAD |  | L1_CURRENT_OF_LOAD | 3 | 0x1326
[7 empty] | L1_N_PHASE_VOLTAGE_OF_GRID |  | L1_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131A
[7 empty] | L1_N_PHASE_VOLTAGE_OF_LOAD |  | L1_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1323
[7 empty] | L1_POWER |  | L1_POWER | 3 | 0x1003
[7 empty] | L1_VOLTAGE |  | L1_VOLTAGE | 3 | 0x1001
[7 empty] | L1_WATT_OF_GRID |  | L1_WATT_OF_GRID | 3 | 0x1300
[7 empty] | L1_WATT_OF_LOAD |  | L1_WATT_OF_LOAD | 3 | 0x130A
[7 empty] | L2_CURRENT |  | L2_CURRENT | 3 | 0x1007
[7 empty] | L2_CURRENT_OF_GRID |  | L2_CURRENT_OF_GRID | 3 | 0x131F
[7 empty] | L2_CURRENT_OF_LOAD |  | L2_CURRENT_OF_LOAD | 3 | 0x1328
[7 empty] | L2_FREQUENCY |  | L2_FREQUENCY | 3 | 0x100A
[7 empty] | L2_N_PHASE_VOLTAGE_OF_GRID |  | L2_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131B
[7 empty] | L2_N_PHASE_VOLTAGE_OF_LOAD |  | L2_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1324
[7 empty] | L2_POWER |  | L2_POWER | 3 | 0x1008
[7 empty] | L2_VOLTAGE |  | L2_VOLTAGE | 3 | 0x1006
[7 empty] | L2_WATT_OF_GRID |  | L2_WATT_OF_GRID | 3 | 0x1302
[7 empty] | L2_WATT_OF_LOAD |  | L2_WATT_OF_LOAD | 3 | 0x130C
[7 empty] | L3_CURRENT |  | L3_CURRENT | 3 | 0x100C
[7 empty] | L3_CURRENT_OF_GRID |  | L3_CURRENT_OF_GRID | 3 | 0x1321
[7 empty] | L3_CURRENT_OF_LOAD |  | L3_CURRENT_OF_LOAD | 3 | 0x132A
[7 empty] | L3_FREQUENCY |  | L3_FREQUENCY | 3 | 0x100F
[7 empty] | L3_N_PHASE_VOLTAGE_OF_GRID |  | L3_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131C
[7 empty] | L3_N_PHASE_VOLTAGE_OF_LOAD |  | L3_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1325
[7 empty] | L3_POWER |  | L3_POWER | 3 | 0x100D
[7 empty] | L3_VOLTAGE |  | L3_VOLTAGE | 3 | 0x100B
[7 empty] | L3_WATT_OF_GRID |  | L3_WATT_OF_GRID | 3 | 0x1304
[7 empty] | L3_WATT_OF_LOAD |  | L3_WATT_OF_LOAD | 3 | 0x130E
[7 empty] | LCD_FIRMWARE_VERSION |  | LCD_FIRMWARE_VERSION | 3 | 0x1A8E
[7 empty] | MASTER_FIRMWARE_VERSION |  | MASTER_FIRMWARE_VERSION | 3 | 0x1A1C
[7 empty] | MPPT1_CURRENT |  | MPPT1_CURRENT | 3 | 0x1011
[7 empty] | MPPT1_POWER |  | MPPT1_POWER | 3 | 0x1012
[7 empty] | MPPT1_VOLTAGE |  | MPPT1_VOLTAGE | 3 | 0x1010
[7 empty] | MPPT2_CURRENT |  | MPPT2_CURRENT | 3 | 0x1015
[7 empty] | MPPT2_POWER |  | MPPT2_POWER | 3 | 0x1016
[7 empty] | MPPT2_VOLTAGE |  | MPPT2_VOLTAGE | 3 | 0x1014
[7 empty] | MPPT3_CURRENT |  | MPPT3_CURRENT | 3 | 0x1019
[7 empty] | MPPT3_POWER |  | MPPT3_POWER | 3 | 0x101A
[7 empty] | MPPT3_VOLTAGE |  | MPPT3_VOLTAGE | 3 | 0x1018
[7 empty] | MPPT4_CURRENT |  | MPPT4_CURRENT | 3 | 0x103F
[7 empty] | MPPT4_POWER |  | MPPT4_POWER | 3 | 0x1040
[7 empty] | MPPT4_VOLTAGE |  | MPPT4_VOLTAGE | 3 | 0x103E
[7 empty] | MPPT5_CURRENT |  | MPPT5_CURRENT | 3 | 0x1081
[7 empty] | MPPT5_POWER |  | MPPT5_POWER | 3 | 0x1082
[7 empty] | MPPT5_VOLTAGE |  | MPPT5_VOLTAGE | 3 | 0x1080
[7 empty] | MPPT6_CURRENT |  | MPPT6_CURRENT | 3 | 0x1085
[7 empty] | MPPT6_POWER |  | MPPT6_POWER | 3 | 0x1086
[7 empty] | MPPT6_VOLTAGE |  | MPPT6_VOLTAGE | 3 | 0x1084
[7 empty] | MPPT7_CURRENT |  | MPPT7_CURRENT | 3 | 0x1089
[7 empty] | MPPT7_POWER |  | MPPT7_POWER | 3 | 0x108A
[7 empty] | MPPT7_VOLTAGE |  | MPPT7_VOLTAGE | 3 | 0x1088
[7 empty] | MPPT8_CURRENT |  | MPPT8_CURRENT | 3 | 0x108D
[7 empty] | MPPT8_POWER |  | MPPT8_POWER | 3 | 0x108E
[7 empty] | MPPT8_VOLTAGE |  | MPPT8_VOLTAGE | 3 | 0x108C
[7 empty] | MPPT9_CURRENT |  | MPPT9_CURRENT | 3 | 0x1091
[7 empty] | MPPT9_POWER |  | MPPT9_POWER | 3 | 0x1092
[7 empty] | MPPT9_VOLTAGE |  | MPPT9_VOLTAGE | 3 | 0x1090
[7 empty] | MPPT_NUMBER |  | MPPT_NUMBER | 3 | 0x1A3B
[7 empty] | NOMINAL_ACTIVE_POWER_HIGH_WORD |  | NOMINAL_ACTIVE_POWER_HIGH_WORD | 3 | 0x1A4E
[7 empty] | NOMINAL_ACTIVE_POWER_LOW_WORD |  | NOMINAL_ACTIVE_POWER_LOW_WORD | 3 | 0x1A46
[7 empty] | NOMINAL_FREQUENCY |  | NOMINAL_FREQUENCY | 3 | 0x1A45
[7 empty] | NOMINAL_VOLTAGE |  | NOMINAL_VOLTAGE | 3 | 0x1A44
[7 empty] | POWER_FACTOR |  | POWER_FACTOR | 3 | 0x0000
[7 empty] | PV_POWER |  | PV_POWER | 3 | 0x1048
[7 empty] | PV_STRING_COUNT |  | PV_STRING_COUNT | 3 | 0x0008
[7 empty] | PV_STRING_REVERSE |  | PV_STRING_REVERSE | 3 | 0x0005
[7 empty] | PV_TODAY_PEAK_POWER |  | PV_TODAY_PEAK_POWER | 3 | 0x103B
[7 empty] | Q_REFERENCE_OUTPUT_REACTIVEPOWER |  | Q_REFERENCE_OUTPUT_REACTIVEPOWER | 3 | 0x1226
[7 empty] | READ_REGISTER_ADDRESS |  | READ_REGISTER_ADDRESS | 3 | 0x0003
[7 empty] | REGISTER_NUMBER |  | REGISTER_NUMBER | 3 | 0x0002
[7 empty] | REG_0X07 |  | REG_0X07 | 3 | 0x0007
[7 empty] | REG_0_PNOM_PNOM_NOMINAL_POWER |  | REG_0_PNOM_PNOM_NOMINAL_POWER | 3 | 0x30B9
[7 empty] | SLAVE_FIRMWARE_VERSION |  | SLAVE_FIRMWARE_VERSION | 3 | 0x1A26
[7 empty] | SOFTWARE_INCOMPATIBILITY |  | SOFTWARE_INCOMPATIBILITY | 3 | 0x000B
[7 empty] | START_BIT |  | START_BIT | 3 | 0x0001
[7 empty] | STRING10_INPUT_CURRENT |  | STRING10_INPUT_CURRENT | 3 | 0x1063
[7 empty] | STRING10_INPUT_VOLTAGE |  | STRING10_INPUT_VOLTAGE | 3 | 0x1062
[7 empty] | STRING11_INPUT_CURRENT |  | STRING11_INPUT_CURRENT | 3 | 0x1065
[7 empty] | STRING11_INPUT_VOLTAGE |  | STRING11_INPUT_VOLTAGE | 3 | 0x1064
[7 empty] | STRING12_INPUT_CURRENT |  | STRING12_INPUT_CURRENT | 3 | 0x1067
[7 empty] | STRING12_INPUT_VOLTAGE |  | STRING12_INPUT_VOLTAGE | 3 | 0x1066
[7 empty] | STRING13_INPUT_CURRENT |  | STRING13_INPUT_CURRENT | 3 | 0x1069
[7 empty] | STRING13_INPUT_VOLTAGE |  | STRING13_INPUT_VOLTAGE | 3 | 0x1068
[7 empty] | STRING14_INPUT_CURRENT |  | STRING14_INPUT_CURRENT | 3 | 0x106B
[7 empty] | STRING14_INPUT_VOLTAGE |  | STRING14_INPUT_VOLTAGE | 3 | 0x106A
[7 empty] | STRING15_INPUT_CURRENT |  | STRING15_INPUT_CURRENT | 3 | 0x106D
[7 empty] | STRING15_INPUT_VOLTAGE |  | STRING15_INPUT_VOLTAGE | 3 | 0x106C
[7 empty] | STRING16_INPUT_CURRENT |  | STRING16_INPUT_CURRENT | 3 | 0x106F
[7 empty] | STRING16_INPUT_VOLTAGE |  | STRING16_INPUT_VOLTAGE | 3 | 0x106E
[7 empty] | STRING17_INPUT_CURRENT |  | STRING17_INPUT_CURRENT | 3 | 0x1071
[7 empty] | STRING17_INPUT_VOLTAGE |  | STRING17_INPUT_VOLTAGE | 3 | 0x1070
[7 empty] | STRING18_INPUT_CURRENT |  | STRING18_INPUT_CURRENT | 3 | 0x1073
[7 empty] | STRING18_INPUT_VOLTAGE |  | STRING18_INPUT_VOLTAGE | 3 | 0x1072
[7 empty] | STRING19_INPUT_CURRENT |  | STRING19_INPUT_CURRENT | 3 | 0x1075
[7 empty] | STRING19_INPUT_VOLTAGE |  | STRING19_INPUT_VOLTAGE | 3 | 0x1074
[7 empty] | STRING1_CURRENT |  | STRING1_CURRENT | 3 | 0x1051
[7 empty] | STRING1_VOLTAGE |  | STRING1_VOLTAGE | 3 | 0x1050
[7 empty] | STRING20_INPUT_CURRENT |  | STRING20_INPUT_CURRENT | 3 | 0x1077
[7 empty] | STRING20_INPUT_VOLTAGE |  | STRING20_INPUT_VOLTAGE | 3 | 0x1076
[7 empty] | STRING21_INPUT_CURRENT |  | STRING21_INPUT_CURRENT | 3 | 0x1079
[7 empty] | STRING21_INPUT_VOLTAGE |  | STRING21_INPUT_VOLTAGE | 3 | 0x1078
[7 empty] | STRING22_INPUT_CURRENT |  | STRING22_INPUT_CURRENT | 3 | 0x107B
[7 empty] | STRING22_INPUT_VOLTAGE |  | STRING22_INPUT_VOLTAGE | 3 | 0x107A
[7 empty] | STRING23_INPUT_CURRENT |  | STRING23_INPUT_CURRENT | 3 | 0x107D
[7 empty] | STRING23_INPUT_VOLTAGE |  | STRING23_INPUT_VOLTAGE | 3 | 0x107C
[7 empty] | STRING24_INPUT_CURRENT |  | STRING24_INPUT_CURRENT | 3 | 0x107F
[7 empty] | STRING24_INPUT_VOLTAGE |  | STRING24_INPUT_VOLTAGE | 3 | 0x107E
[7 empty] | STRING2_CURRENT |  | STRING2_CURRENT | 3 | 0x1053
[7 empty] | STRING2_VOLTAGE |  | STRING2_VOLTAGE | 3 | 0x1052
[7 empty] | STRING3_CURRENT |  | STRING3_CURRENT | 3 | 0x1055
[7 empty] | STRING3_VOLTAGE |  | STRING3_VOLTAGE | 3 | 0x1054
[7 empty] | STRING4_CURRENT |  | STRING4_CURRENT | 3 | 0x1057
[7 empty] | STRING4_VOLTAGE |  | STRING4_VOLTAGE | 3 | 0x1056
[7 empty] | STRING5_CURRENT |  | STRING5_CURRENT | 3 | 0x1059
[7 empty] | STRING5_VOLTAGE |  | STRING5_VOLTAGE | 3 | 0x1058
[7 empty] | STRING6_CURRENT |  | STRING6_CURRENT | 3 | 0x105B
[7 empty] | STRING6_VOLTAGE |  | STRING6_VOLTAGE | 3 | 0x105A
[7 empty] | STRING7_CURRENT |  | STRING7_CURRENT | 3 | 0x105D
[7 empty] | STRING7_VOLTAGE |  | STRING7_VOLTAGE | 3 | 0x105C
[7 empty] | STRING8_CURRENT |  | STRING8_CURRENT | 3 | 0x105F
[7 empty] | STRING8_VOLTAGE |  | STRING8_VOLTAGE | 3 | 0x105E
[7 empty] | STRING9_INPUT_CURRENT |  | STRING9_INPUT_CURRENT | 3 | 0x1061
[7 empty] | STRING9_INPUT_VOLTAGE |  | STRING9_INPUT_VOLTAGE | 3 | 0x1060
[7 empty] | STRING_1_3_CURRENT |  | STRING_1_3_CURRENT | 3 | 0x80C0
[7 empty] | STRING_1_4_CURRENT |  | STRING_1_4_CURRENT | 3 | 0x8100
[7 empty] | STRING_2_3_CURRENT |  | STRING_2_3_CURRENT | 3 | 0x8200
[7 empty] | STRING_2_4_CURRENT |  | STRING_2_4_CURRENT | 3 | 0x8240
[7 empty] | STRING_3_3_CURRENT |  | STRING_3_3_CURRENT | 3 | 0x8340
[7 empty] | STRING_3_4_CURRENT |  | STRING_3_4_CURRENT | 3 | 0x8380
[7 empty] | STRING_4_3_CURRENT |  | STRING_4_3_CURRENT | 3 | 0x8480
[7 empty] | STRING_4_4_CURRENT |  | STRING_4_4_CURRENT | 3 | 0x84C0
[7 empty] | STRING_5_1_CURRENT |  | STRING_5_1_CURRENT | 3 | 0x8540
[7 empty] | STRING_5_2_CURRENT |  | STRING_5_2_CURRENT | 3 | 0x8580
[7 empty] | STRING_5_3_CURRENT |  | STRING_5_3_CURRENT | 3 | 0x85C0
[7 empty] | STRING_5_4_CURRENT |  | STRING_5_4_CURRENT | 3 | 0x8600
[7 empty] | STRING_6_1_CURRENT |  | STRING_6_1_CURRENT | 3 | 0x8680
[7 empty] | STRING_6_2_CURRENT |  | STRING_6_2_CURRENT | 3 | 0x86C0
[7 empty] | STRING_6_3_CURRENT |  | STRING_6_3_CURRENT | 3 | 0x8700
[7 empty] | STRING_6_4_CURRENT |  | STRING_6_4_CURRENT | 3 | 0x8740
[7 empty] | STRING_7_1_CURRENT |  | STRING_7_1_CURRENT | 3 | 0x87C0
[7 empty] | STRING_7_2_CURRENT |  | STRING_7_2_CURRENT | 3 | 0x8800
[7 empty] | STRING_7_3_CURRENT |  | STRING_7_3_CURRENT | 3 | 0x8840
[7 empty] | STRING_7_4_CURRENT |  | STRING_7_4_CURRENT | 3 | 0x8880
[7 empty] | STRING_8_1_CURRENT |  | STRING_8_1_CURRENT | 3 | 0x8900
[7 empty] | STRING_8_2_CURRENT |  | STRING_8_2_CURRENT | 3 | 0x8940
[7 empty] | STRING_8_3_CURRENT |  | STRING_8_3_CURRENT | 3 | 0x8980
[7 empty] | STRING_8_4_CURRENT |  | STRING_8_4_CURRENT | 3 | 0x89C0
[7 empty] | STRING_9_1_CURRENT |  | STRING_9_1_CURRENT | 3 | 0x8A40
[7 empty] | STRING_9_2_CURRENT |  | STRING_9_2_CURRENT | 3 | 0x8A80
[7 empty] | STRING_9_3_CURRENT |  | STRING_9_3_CURRENT | 3 | 0x8AC0
[7 empty] | STRING_9_4_CURRENT |  | STRING_9_4_CURRENT | 3 | 0x8B00
[7 empty] | TODAY_EXPORT_ENERGY |  | TODAY_EXPORT_ENERGY | 3 | 0x1334
[7 empty] | TODAY_IMPORT_ENERGY |  | TODAY_IMPORT_ENERGY | 3 | 0x1332
[7 empty] | TODAY_LOAD_ENERGY |  | TODAY_LOAD_ENERGY | 3 | 0x1336
[7 empty] | TOTAL_GENERATION_TIME |  | TOTAL_GENERATION_TIME | 3 | 0x1023
[7 empty] | TRACKER_5_VOLTAGE |  | TRACKER_5_VOLTAGE | 3 | 0x8500
[7 empty] | TRACKER_6_VOLTAGE |  | TRACKER_6_VOLTAGE | 3 | 0x8640
[7 empty] | TRACKER_7_VOLTAGE |  | TRACKER_7_VOLTAGE | 3 | 0x8780
[7 empty] | TRACKER_8_VOLTAGE |  | TRACKER_8_VOLTAGE | 3 | 0x88C0
[7 empty] | TRACKER_9_VOLTAGE |  | TRACKER_9_VOLTAGE | 3 | 0x8A00
[7 empty] | WRITE_MULTIPLE_REGISTER_ADDRESS |  | WRITE_MULTIPLE_REGISTER_ADDRESS | 3 | 0x0010