## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=4, STR=8)
제조사 | Solarize
용량 | 50_3
원본 파일 | test_Solarize-PV_Modbus_Protocol-Korea-V1.2.4.pdf
Phase Type | unknown
MPPT | 4
Total Strings | 8
String/MPPT (파생) | 2
H01 매칭 | 60/60
DER 매칭 | 33/33
총 레지스터 | 145
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INNER_TEMP | 0x101C | S16 | °C 1 | RO | temperature | Inner Temperature
2 | DAILY_ENERGY | 0x1027 | U32 | Wh | RO | daily_energy | Today Energy
3 | Decimals of total energy | 0x104C | U16 |  | RO | cumulative_energy_low | Wh
4 | L1_N_PHASE_VOLTAGE_OF_GRID | 0x131A | U16 | V 0.1 | RO |  | L1-N phase voltage of grid
5 | L2_N_PHASE_VOLTAGE_OF_GRID | 0x131B | U16 | V 0.1 | RO |  | L2-N phase voltage of grid
6 | L3_N_PHASE_VOLTAGE_OF_GRID | 0x131C | U16 | V 0.1 | RO |  | L3-N phase voltage of grid
7 | L1_N_PHASE_VOLTAGE_OF_LOAD | 0x1323 | U16 | V 0.1 | RO |  | L1-N phase voltage of load
8 | L2_N_PHASE_VOLTAGE_OF_LOAD | 0x1324 | U16 | V 0.1 | RO |  | L2-N phase voltage of load
9 | L3_N_PHASE_VOLTAGE_OF_LOAD | 0x1325 | U16 | V 0.1 | RO |  | L3-N phase voltage of load
10 | Device Model name | 0x1A00 | STRINGING |  | RO |  | Ex.：PV 30KTL
11 | Device Serial number | 0x1A10 | STRINGING |  | RO |  | Ex.：1234-123456789
12 | Master firmware version | 0x1A1C | STRINGING |  | RO |  | Ex.：123456
13 | Slave firmware version | 0x1A26 | STRINGING |  | RO |  | Ex.：123456
14 | NOMINAL_VOLTAGE | 0x1A44 | U16 |  | RO |  | Nominal Voltage ¦ Ex.：2200 = 220V
15 | NOMINAL_FREQUENCY | 0x1A45 | U16 |  | RO |  | Nominal Frequency ¦ Ex.：5000 = 50Hz
16 | Nominal Active Power(Low word) | 0x1A46 | U16 | W 1 | RO |  | Ex.：1500 = 1500W
17 | GRID_PHASE_NUMBER | 0x1A48 | U16 |  | RO |  | Grid Phase Number ¦ 1=single phase2=split phase3=three phases
18 | Nominal Active Power(High word) | 0x1A4E | U16 | W 1 | RO |  | Ex.：1 = (1*65536)W
19 | EMS Firmware Version | 0x1A60 | STRINGING |  | RO |  | Ex.：123456
20 | LCD firmware version | 0x1A8E | STRINGING |  | RO |  | Ex.：123456
21 | [0, Pnom]Pnom : nominal power | 0x30B9 | U32 |  | RW
H01 MONITORING (120개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | POWER_FACTOR | 0x0000 | U16 |  | RO | power_factor
2 | Start bit | 0x0001 | U16 |  | RO
3 | Register number | 0x0002 | U16 |  | RO
4 | Read register address | 0x0003 | U16 |  | RO
5 | GFCI_ABNORMAL | 0x0004 | U16 |  | RO
6 | PV string reverse | 0x0005 | STRINGING |  | RO
7 | 0x07 | 0x0007 | U16 |  | RO
8 | PV_STRING_COUNT | 0x0008 | U16 |  | RO
9 | Dc-link over voltage | 0x0009 | U16 |  | RO
10 | INTERNAL_COMMUNICATION_ERROR | 0x000A | U16 |  | RO
11 | Software incompatibility | 0x000B | U16 |  | RO
12 | INTERNAL_STORAGE_ERROR | 0x000C | U16 |  | RO
13 | L2_VOLTAGE | 0x000D | U16 |  | RO | s_voltage
14 | L3_VOLTAGE | 0x000E | U16 |  | RO
15 | FREQUENCY | 0x000F | U16 |  | RO
16 | L1_VOLTAGE | 0x0026 | U16 |  | RO | r_voltage
17 | L1 Voltage | 0x1001 | U16 | V 0.1 | RO | r_voltage
18 | L1_CURRENT | 0x1002 | U16 | A 0.01 | RO | r_current
19 | L1_POWER | 0x1003 | S32 | W 0.1 | RO
20 | FREQUENCY | 0x1005 | U16 | Hz 0.01 | RO | frequency
21 | L2 Voltage | 0x1006 | U16 | V 0.1 | RO | s_voltage
22 | L2_CURRENT | 0x1007 | U16 | A 0.01 | RO | s_current
23 | L2_POWER | 0x1008 | S32 | W 0.1 | RO
24 | L2 Frequency | 0x100A | U16 | Hz 0.01 | RO | frequency
25 | L3 Voltage | 0x100B | U16 | V 0.1 | RO | t_voltage
26 | L3_CURRENT | 0x100C | U16 | A 0.01 | RO | t_current
27 | L3_POWER | 0x100D | S32 | W 0.1 | RO
28 | L3 Frequency | 0x100F | U16 | Hz 0.01 | RO | frequency
29 | MPPT1_VOLTAGE | 0x1010 | U16 | V 0.1 | RO | mppt1_voltage
30 | MPPT1_CURRENT | 0x1011 | S16 | A 0.01 | RO | mppt1_current
31 | MPPT1_POWER | 0x1012 | U32 | W 0.1 | RO | mppt1_power
32 | MPPT2_VOLTAGE | 0x1014 | U16 | V 0.1 | RO | mppt2_voltage
33 | MPPT2_CURRENT | 0x1015 | S16 | A 0.01 | RO | mppt2_current
34 | MPPT2_POWER | 0x1016 | U32 | W 0.1 | RO | mppt2_power
35 | MPPT3_VOLTAGE | 0x1018 | U16 | V 0.1 | RO | mppt3_voltage
36 | MPPT3_CURRENT | 0x1019 | S16 | A 0.01 | RO | mppt3_current
37 | MPPT3_POWER | 0x101A | U32 | W 0.1 | RO | mppt3_power
38 | CUMULATIVE_ENERGY | 0x1021 | U32 | kWh | RO | cumulative_energy
39 | TOTAL_GENERATION_TIME | 0x1023 | U32 |  | RO
40 | AC_POWER | 0x1037 | S32 | W 0.1 | RO | ac_power
41 | Grid total Reactive Power | 0x1039 | S32 |  | RO | ac_power
42 | PV Today Peak Power | 0x103B | S32 | W 0.1 | RO
43 | Power Factor | 0x103D | S16 |  | RO | power_factor
44 | MPPT4_VOLTAGE | 0x103E | U16 | V 0.1 | RO | mppt4_voltage
45 | MPPT4_CURRENT | 0x103F | S16 | A 0.01 | RO | mppt4_current
46 | MPPT4_POWER | 0x1040 | U32 | W 0.1 | RO | mppt4_power
47 | PV_POWER | 0x1048 | U32 | W 0.1 | RO | pv_power
48 | STRING1_VOLTAGE | 0x1050 | U16 | V 0.1 | RO | string1_voltage
49 | STRING1_CURRENT | 0x1051 | S16 | A 0.01 | RO | string1_current
50 | STRING2_VOLTAGE | 0x1052 | U16 | V 0.1 | RO | string2_voltage
51 | STRING2_CURRENT | 0x1053 | S16 | A 0.01 | RO | string2_current
52 | STRING3_VOLTAGE | 0x1054 | U16 | V 0.1 | RO | string3_voltage
53 | STRING3_CURRENT | 0x1055 | S16 | A 0.01 | RO | string3_current
54 | STRING4_VOLTAGE | 0x1056 | U16 | V 0.1 | RO | string4_voltage
55 | STRING4_CURRENT | 0x1057 | S16 | A 0.01 | RO | string4_current
56 | STRING5_VOLTAGE | 0x1058 | U16 | V 0.1 | RO | string5_voltage
57 | STRING5_CURRENT | 0x1059 | S16 | A 0.01 | RO | string5_current
58 | STRING6_VOLTAGE | 0x105A | U16 | V 0.1 | RO | string6_voltage
59 | STRING6_CURRENT | 0x105B | S16 | A 0.01 | RO | string6_current
60 | STRING7_VOLTAGE | 0x105C | U16 | V 0.1 | RO | string7_voltage
61 | STRING7_CURRENT | 0x105D | S16 | A 0.01 | RO | string7_current
62 | STRING8_VOLTAGE | 0x105E | U16 | V 0.1 | RO | string8_voltage
63 | STRING8_CURRENT | 0x105F | S16 | A 0.01 | RO | string8_current
64 | External fan speed dutypercentage | 0x120C | U16 |  | RO
65 | Q (Reference Output reactivepower) | 0x1226 | S16 |  | RO
66 | L1 watt of grid | 0x1300 | S32 | W 0.1 | RO
67 | L2 watt of grid | 0x1302 | S32 | W 0.1 | RO
68 | L3 watt of grid | 0x1304 | S32 | W 0.1 | RO
69 | Accumulated energy ofimport | 0x1306 | U32 | Wh 10 | RO | cumulative_energy
70 | Accumulated energy ofexport | 0x1308 | U32 | Wh 10 | RO | cumulative_energy
71 | L1 watt of load | 0x130A | U32 | W 0.1 | RO
72 | L2 watt of load | 0x130C | U32 | W 0.1 | RO
73 | L3 watt of load | 0x130E | U32 | W 0.1 | RO
74 | Accumulated energy of load | 0x1310 | U32 | Wh 10 | RO | cumulative_energy
75 | L1_CURRENT_OF_GRID | 0x131D | S32 | A 0.01 | RO
76 | L2_CURRENT_OF_GRID | 0x131F | S32 | A 0.01 | RO
77 | L3_CURRENT_OF_GRID | 0x1321 | S32 | A 0.01 | RO
78 | L1_CURRENT_OF_LOAD | 0x1326 | S32 | A 0.01 | RO
79 | L2_CURRENT_OF_LOAD | 0x1328 | S32 | A 0.01 | RO
80 | L3_CURRENT_OF_LOAD | 0x132A | S32 | A 0.01 | RO
81 | Today import Energy | 0x1332 | U32 | Wh 10 | RO
82 | Today export Energy | 0x1334 | U32 | Wh 10 | RO
83 | Today load Energy | 0x1336 | U32 | Wh 10 | RO
84 | FREQUENCY | 0x1338 | U16 | Hz 0.01 | RO | frequency
85 | MPPT_NUMBER | 0x1A3B | U16 |  | RO
86 | String 1-3 current | 0x80C0 | STRINGING | A 0.01 | RO
87 | String 1-4 current | 0x8100 | STRINGING | A 0.01 | RO
88 | String 2-3 current | 0x8200 | STRINGING | A 0.01 | RO
89 | String 2-4 current | 0x8240 | STRINGING | A 0.01 | RO
90 | String 3-3 current | 0x8340 | STRINGING | A 0.01 | RO
91 | String 3-4 current | 0x8380 | STRINGING | A 0.01 | RO
92 | String 4-3 current | 0x8480 | STRINGING | A 0.01 | RO
93 | String 4-4 current | 0x84C0 | STRINGING | A 0.01 | RO
94 | Tracker 5 voltage | 0x8500 | U16 | V 0.1 | RO
95 | String 5-1 current | 0x8540 | STRINGING | A 0.01 | RO
96 | String 5-2 current | 0x8580 | STRINGING | A 0.01 | RO
97 | String 5-3 current | 0x85C0 | STRINGING | A 0.01 | RO
98 | String 5-4 current | 0x8600 | STRINGING | A 0.01 | RO
99 | Tracker 6 voltage | 0x8640 | U16 | V 0.1 | RO
100 | String 6-1 current | 0x8680 | STRINGING | A 0.01 | RO
101 | String 6-2 current | 0x86C0 | STRINGING | A 0.01 | RO
102 | String 6-3 current | 0x8700 | STRINGING | A 0.01 | RO
103 | String 6-4 current | 0x8740 | STRINGING | A 0.01 | RO
104 | Tracker 7 voltage | 0x8780 | U16 | V 0.1 | RO
105 | String 7-1 current | 0x87C0 | STRINGING | A 0.01 | RO
106 | String 7-2 current | 0x8800 | STRINGING | A 0.01 | RO
107 | String 7-3 current | 0x8840 | STRINGING | A 0.01 | RO
108 | String 7-4 current | 0x8880 | STRINGING | A 0.01 | RO
109 | Tracker 8 voltage | 0x88C0 | U16 | V 0.1 | RO
110 | String 8-1 current | 0x8900 | STRINGING | A 0.01 | RO
111 | String 8-2 current | 0x8940 | STRINGING | A 0.01 | RO
112 | String 8-3 current | 0x8980 | STRINGING | A 0.01 | RO
113 | String 8-4 current | 0x89C0 | STRINGING | A 0.01 | RO
114 | Tracker 9 voltage | 0x8A00 | U16 | V 0.1 | RO
115 | String 9-1 current | 0x8A40 | STRINGING | A 0.01 | RO
116 | String 9-2 current | 0x8A80 | STRINGING | A 0.01 | RO
117 | String 9-3 current | 0x8AC0 | STRINGING | A 0.01 | RO
118 | String 9-4 current | 0x8B00 | STRINGING | A 0.01 | RO
119 | history log 0 | 0xB600 | U16 |  | RO
120 | history log 127 | 0xB77D | U16 |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INVERTER_MODE | 0x101D | U16 |  | RO | inverter_status | Inverter Mode ¦ Inverter Mode Table
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | ERROR_CODE1 | 0x101E | U16 |  | RO |  | Error Code1 ¦ Error Code Table 1
2 | ERROR_CODE2 | 0x101F | U16 |  | RO |  | Error Code2 ¦ Error Code Table 2
3 | ERROR_CODE3 | 0x1020 | U16 |  | RO |  | Error Code3 ¦ Error Code Table 3

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | Solarize
용량 | 50_3
MPPT | 4 (PDF max 9개)
String | 총 8개 (파생 2/MPPT)
H01 매칭 | 60/60
DER 매칭 | 33/33
총 레지스터 | 145
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 21
MONITORING | 120
STATUS | 1
ALARM | 3
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | PDF_PHASE | O | 0x1001 | L1 Voltage
2 | s_voltage | PDF_PHASE | O | 0x1006 | L2 Voltage
3 | t_voltage | PDF_PHASE | O | 0x100B | L3 Voltage
4 | r_current | PDF_PHASE | O | 0x1002 | L1_CURRENT
5 | s_current | PDF_PHASE | O | 0x1007 | L2_CURRENT
6 | t_current | PDF_PHASE | O | 0x100C | L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | PDF | O | 0x1048 | PV_POWER
13 | cumulative_energy | PDF | O | 0x1021 | CUMULATIVE_ENERGY
14 | cumulative_energy_low | PDF | O | 0x104C | Decimals of total energy
15 | status | PDF | O | 0x101D | INVERTER_MODE
16 | alarm1 | PDF | O | 0x101E | ERROR_CODE1
17 | alarm2 | PDF | O | 0x101F | ERROR_CODE2
18 | alarm3 | PDF | O | 0x1020 | ERROR_CODE3
19 | mppt1_voltage | PDF | O | 0x1010 | MPPT1_VOLTAGE
20 | mppt1_current | PDF | O | 0x1011 | MPPT1_CURRENT
21 | mppt2_voltage | PDF | O | 0x1014 | MPPT2_VOLTAGE
22 | mppt2_current | PDF | O | 0x1015 | MPPT2_CURRENT
23 | mppt3_voltage | PDF | O | 0x1018 | MPPT3_VOLTAGE
24 | mppt3_current | PDF | O | 0x1019 | MPPT3_CURRENT
25 | mppt4_voltage | PDF | O | 0x103E | MPPT4_VOLTAGE
26 | mppt4_current | PDF | O | 0x103F | MPPT4_CURRENT
27 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage
28 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current
29 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage
30 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current
31 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage
32 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current
33 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage
34 | mppt8_current | PDF | O | 0x108D | MPPT8 Current
35 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage
36 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current
37 | string1_current | PDF | O | 0x1051 | STRING1_CURRENT
38 | string2_current | PDF | O | 0x1053 | STRING2_CURRENT
39 | string3_current | PDF | O | 0x1055 | STRING3_CURRENT
40 | string4_current | PDF | O | 0x1057 | STRING4_CURRENT
41 | string5_current | PDF | O | 0x1059 | STRING5_CURRENT
42 | string6_current | PDF | O | 0x105B | STRING6_CURRENT
43 | string7_current | PDF | O | 0x105D | STRING7_CURRENT
44 | string8_current | PDF | O | 0x105F | STRING8_CURRENT
45 | string9_current | PDF | O | 0x1061 | String9 input current
46 | string10_current | PDF | O | 0x1063 | String10 input current
47 | string11_current | PDF | O | 0x1065 | String11 input current
48 | string12_current | PDF | O | 0x1067 | String12 input current
49 | string13_current | PDF | O | 0x1069 | String13 input current
50 | string14_current | PDF | O | 0x106B | String14 input current
51 | string15_current | PDF | O | 0x106D | String15 input current
52 | string16_current | PDF | O | 0x106F | String16 input current
53 | string17_current | PDF | O | 0x1071 | String17 input current
54 | string18_current | PDF | O | 0x1073 | String18 input current
55 | string19_current | PDF | O | 0x1075 | String19 input current
56 | string20_current | PDF | O | 0x1077 | String20 input current
57 | string21_current | PDF | O | 0x1079 | String21 input current
58 | string22_current | PDF | O | 0x107B | String22 input current
59 | string23_current | PDF | O | 0x107D | String23 input current
60 | string24_current | PDF | O | 0x107F | String24 input current

## H01_MAPPING
H01_MAPPING — H01 필드별 레지스터 수동 매핑
※ D열에서 매핑할 레지스터명을 선택/입력하세요. E~G열은 추천 후보, H열은 전체 목록, I열은 FC코드(3 or 4).
No | H01 Field | 설명 | 매칭된 레지스터 (주소) | 추천 후보 1 | 추천 후보 2 | 추천 후보 3 | 전체 레지스터 목록 | FC
1 | pv_voltage | HANDLER 계산 (평균 MPPT 전압) | HANDLER; DC_LINK_OVER_VOLTAGE (0x0009) | MPPT1_VOLTAGE (0x1010) | MPPT2_VOLTAGE (0x1014) |  | ACCUMULATED_ENERGY_OFEXPORT | 3 | ACCUMULATED_ENERGY_OFEXPORT | 3 | 0x1308 | handler
2 | pv_current | HANDLER 계산 (합산 MPPT 전류) | HANDLER; MPPT1_CURRENT (0x1011) | MPPT2_CURRENT (0x1015) | MPPT3_CURRENT (0x1019) |  | ACCUMULATED_ENERGY_OFIMPORT | 3 | ACCUMULATED_ENERGY_OFIMPORT | 3 | 0x1306 | handler
3 | pv_power | HANDLER 계산 (합산 MPPT 전력) | PV_POWER (0x1048) |  |  |  | ACCUMULATED_ENERGY_OF_LOAD | 3 | ACCUMULATED_ENERGY_OF_LOAD | 3 | 0x1310 | pdf
4 | r_voltage | R상(L1) 전압 | L1_VOLTAGE (0x1001) |  |  |  | AC_POWER | 3 | AC_POWER | 3 | 0x1037 | pdf
5 | s_voltage | S상(L2) 전압 | L2_VOLTAGE (0x1006) | L2_N_PHASE_VOLTAGE_OF_GRID (0x131B) | L2_N_PHASE_VOLTAGE_OF_LOAD (0x1324) |  | CUMULATIVE_ENERGY | 3 | CUMULATIVE_ENERGY | 3 | 0x1021 | pdf
6 | t_voltage | T상(L3) 전압 | L3_VOLTAGE (0x100B) | L3_N_PHASE_VOLTAGE_OF_GRID (0x131C) | L3_N_PHASE_VOLTAGE_OF_LOAD (0x1325) |  | DAILY_ENERGY | 3 | DAILY_ENERGY | 3 | 0x1027 | pdf
7 | r_current | R상(L1) 전류 | L1_CURRENT (0x1002) | L1_CURRENT_OF_GRID (0x131D) | L1_CURRENT_OF_LOAD (0x1326) |  | DC_LINK_OVER_VOLTAGE | 3 | DC_LINK_OVER_VOLTAGE | 3 | 0x0009 | pdf
8 | s_current | S상(L2) 전류 | L2_CURRENT (0x1007) | L2_CURRENT_OF_GRID (0x131F) | L2_CURRENT_OF_LOAD (0x1328) |  | DECIMALS_OF_TOTAL_ENERGY | 3 | DECIMALS_OF_TOTAL_ENERGY | 3 | 0x104C | pdf
9 | t_current | T상(L3) 전류 | L3_CURRENT (0x100C) | L3_CURRENT_OF_GRID (0x1321) | L3_CURRENT_OF_LOAD (0x132A) |  | DEVICE_MODEL_NAME | 3 | DEVICE_MODEL_NAME | 3 | 0x1A00 | pdf
10 | ac_power | AC 출력 전력 | DEA_TOTAL_ACTIVE_POWER (0x03F4~0x03F5); AC_POWER (0x1037); GRID_TOTAL_REACTIVE_POWER (0x1039) | Q_REFERENCE_OUTPUT_REACTIVEPOWER (0x1226) |  |  | DEVICE_SERIAL_NUMBER | 3 | DEVICE_SERIAL_NUMBER | 3 | 0x1A10 | der
11 | power_factor | 역률 | DEA_POWER_FACTOR (0x03F8~0x03F9); POWER_FACTOR (0x0000) |  |  |  | EMS_FIRMWARE_VERSION | 3 | EMS_FIRMWARE_VERSION | 3 | 0x1A60 | der
12 | frequency | 계통 주파수 | DEA_FREQUENCY (0x03FA~0x03FB); FREQUENCY (0x1005); L2_FREQUENCY (0x100A); L3_FREQUENCY (0x100F) |  |  |  | ERROR_CODE1 | 3 | ERROR_CODE1 | 3 | 0x101E | der
13 | cumulative_energy | 누적 발전량 | CUMULATIVE_ENERGY (0x1021); ACCUMULATED_ENERGY_OFIMPORT (0x1306); ACCUMULATED_ENERGY_OFEXPORT (0x1308); ACCUMULATED_ENERGY_OF_LOAD (0x1310) | DECIMALS_OF_TOTAL_ENERGY (0x104C) |  |  | ERROR_CODE2 | 3 | ERROR_CODE2 | 3 | 0x101F | pdf
14 | status | 인버터 상태 | INVERTER_MODE (0x101D) |  |  |  | ERROR_CODE3 | 3 | ERROR_CODE3 | 3 | 0x1020 | pdf
15 | alarm1 | 경보 코드 1 | ERROR_CODE1 (0x101E) | ERROR_CODE2 (0x101F) | ERROR_CODE3 (0x1020) |  | EXTERNAL_FAN_SPEED_DUTYPERCENTAGE | 3 | EXTERNAL_FAN_SPEED_DUTYPERCENTAGE | 3 | 0x120C | pdf
16 | alarm2 | 경보 코드 2 | ERROR_CODE2 (0x101F) | ERROR_CODE1 (0x101E) | ERROR_CODE3 (0x1020) |  | FREQUENCY | 3 | FREQUENCY | 3 | 0x000F | pdf
17 | alarm3 | 경보 코드 3 | ERROR_CODE3 (0x1020) | ERROR_CODE1 (0x101E) | ERROR_CODE2 (0x101F) |  | GFCI_ABNORMAL | 3 | GFCI_ABNORMAL | 3 | 0x0004 | pdf
[7 empty] | GRID_PHASE_NUMBER |  | GRID_PHASE_NUMBER | 3 | 0x1A48
[7 empty] | GRID_TOTAL_REACTIVE_POWER |  | GRID_TOTAL_REACTIVE_POWER | 3 | 0x1039
[7 empty] | HISTORY_LOG_0 |  | HISTORY_LOG_0 | 3 | 0xB600
[7 empty] | HISTORY_LOG_127 |  | HISTORY_LOG_127 | 3 | 0xB77D
[7 empty] | INNER_TEMP |  | INNER_TEMP | 3 | 0x101C
[7 empty] | INTERNAL_COMMUNICATION_ERROR |  | INTERNAL_COMMUNICATION_ERROR | 3 | 0x000A
[7 empty] | INTERNAL_STORAGE_ERROR |  | INTERNAL_STORAGE_ERROR | 3 | 0x000C
[7 empty] | INVERTER_MODE |  | INVERTER_MODE | 3 | 0x101D
[7 empty] | L1_CURRENT |  | L1_CURRENT | 3 | 0x1002
[7 empty] | L1_CURRENT_OF_GRID |  | L1_CURRENT_OF_GRID | 3 | 0x131D
[7 empty] | L1_CURRENT_OF_LOAD |  | L1_CURRENT_OF_LOAD | 3 | 0x1326
[7 empty] | L1_N_PHASE_VOLTAGE_OF_GRID |  | L1_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131A
[7 empty] | L1_N_PHASE_VOLTAGE_OF_LOAD |  | L1_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1323
[7 empty] | L1_POWER |  | L1_POWER | 3 | 0x1003
[7 empty] | L1_VOLTAGE |  | L1_VOLTAGE | 3 | 0x0026
[7 empty] | L1_WATT_OF_GRID |  | L1_WATT_OF_GRID | 3 | 0x1300
[7 empty] | L1_WATT_OF_LOAD |  | L1_WATT_OF_LOAD | 3 | 0x130A
[7 empty] | L2_CURRENT |  | L2_CURRENT | 3 | 0x1007
[7 empty] | L2_CURRENT_OF_GRID |  | L2_CURRENT_OF_GRID | 3 | 0x131F
[7 empty] | L2_CURRENT_OF_LOAD |  | L2_CURRENT_OF_LOAD | 3 | 0x1328
[7 empty] | L2_FREQUENCY |  | L2_FREQUENCY | 3 | 0x100A
[7 empty] | L2_N_PHASE_VOLTAGE_OF_GRID |  | L2_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131B
[7 empty] | L2_N_PHASE_VOLTAGE_OF_LOAD |  | L2_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1324
[7 empty] | L2_POWER |  | L2_POWER | 3 | 0x1008
[7 empty] | L2_VOLTAGE |  | L2_VOLTAGE | 3 | 0x000D
[7 empty] | L2_WATT_OF_GRID |  | L2_WATT_OF_GRID | 3 | 0x1302
[7 empty] | L2_WATT_OF_LOAD |  | L2_WATT_OF_LOAD | 3 | 0x130C
[7 empty] | L3_CURRENT |  | L3_CURRENT | 3 | 0x100C
[7 empty] | L3_CURRENT_OF_GRID |  | L3_CURRENT_OF_GRID | 3 | 0x1321
[7 empty] | L3_CURRENT_OF_LOAD |  | L3_CURRENT_OF_LOAD | 3 | 0x132A
[7 empty] | L3_FREQUENCY |  | L3_FREQUENCY | 3 | 0x100F
[7 empty] | L3_N_PHASE_VOLTAGE_OF_GRID |  | L3_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131C
[7 empty] | L3_N_PHASE_VOLTAGE_OF_LOAD |  | L3_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1325
[7 empty] | L3_POWER |  | L3_POWER | 3 | 0x100D
[7 empty] | L3_VOLTAGE |  | L3_VOLTAGE | 3 | 0x000E
[7 empty] | L3_WATT_OF_GRID |  | L3_WATT_OF_GRID | 3 | 0x1304
[7 empty] | L3_WATT_OF_LOAD |  | L3_WATT_OF_LOAD | 3 | 0x130E
[7 empty] | LCD_FIRMWARE_VERSION |  | LCD_FIRMWARE_VERSION | 3 | 0x1A8E
[7 empty] | MASTER_FIRMWARE_VERSION |  | MASTER_FIRMWARE_VERSION | 3 | 0x1A1C
[7 empty] | MPPT1_CURRENT |  | MPPT1_CURRENT | 3 | 0x1011
[7 empty] | MPPT1_POWER |  | MPPT1_POWER | 3 | 0x1012
[7 empty] | MPPT1_VOLTAGE |  | MPPT1_VOLTAGE | 3 | 0x1010
[7 empty] | MPPT2_CURRENT |  | MPPT2_CURRENT | 3 | 0x1015
[7 empty] | MPPT2_POWER |  | MPPT2_POWER | 3 | 0x1016
[7 empty] | MPPT2_VOLTAGE |  | MPPT2_VOLTAGE | 3 | 0x1014
[7 empty] | MPPT3_CURRENT |  | MPPT3_CURRENT | 3 | 0x1019
[7 empty] | MPPT3_POWER |  | MPPT3_POWER | 3 | 0x101A
[7 empty] | MPPT3_VOLTAGE |  | MPPT3_VOLTAGE | 3 | 0x1018
[7 empty] | MPPT4_CURRENT |  | MPPT4_CURRENT | 3 | 0x103F
[7 empty] | MPPT4_POWER |  | MPPT4_POWER | 3 | 0x1040
[7 empty] | MPPT4_VOLTAGE |  | MPPT4_VOLTAGE | 3 | 0x103E
[7 empty] | MPPT_NUMBER |  | MPPT_NUMBER | 3 | 0x1A3B
[7 empty] | NOMINAL_ACTIVE_POWER_HIGH_WORD |  | NOMINAL_ACTIVE_POWER_HIGH_WORD | 3 | 0x1A4E
[7 empty] | NOMINAL_ACTIVE_POWER_LOW_WORD |  | NOMINAL_ACTIVE_POWER_LOW_WORD | 3 | 0x1A46
[7 empty] | NOMINAL_FREQUENCY |  | NOMINAL_FREQUENCY | 3 | 0x1A45
[7 empty] | NOMINAL_VOLTAGE |  | NOMINAL_VOLTAGE | 3 | 0x1A44
[7 empty] | POWER_FACTOR |  | POWER_FACTOR | 3 | 0x0000
[7 empty] | PV_POWER |  | PV_POWER | 3 | 0x1048
[7 empty] | PV_STRING_COUNT |  | PV_STRING_COUNT | 3 | 0x0008
[7 empty] | PV_STRING_REVERSE |  | PV_STRING_REVERSE | 3 | 0x0005
[7 empty] | PV_TODAY_PEAK_POWER |  | PV_TODAY_PEAK_POWER | 3 | 0x103B
[7 empty] | Q_REFERENCE_OUTPUT_REACTIVEPOWER |  | Q_REFERENCE_OUTPUT_REACTIVEPOWER | 3 | 0x1226
[7 empty] | READ_REGISTER_ADDRESS |  | READ_REGISTER_ADDRESS | 3 | 0x0003
[7 empty] | REGISTER_NUMBER |  | REGISTER_NUMBER | 3 | 0x0002
[7 empty] | REG_0X07 |  | REG_0X07 | 3 | 0x0007
[7 empty] | REG_0_PNOM_PNOM_NOMINAL_POWER |  | REG_0_PNOM_PNOM_NOMINAL_POWER | 3 | 0x30B9
[7 empty] | SLAVE_FIRMWARE_VERSION |  | SLAVE_FIRMWARE_VERSION | 3 | 0x1A26
[7 empty] | SOFTWARE_INCOMPATIBILITY |  | SOFTWARE_INCOMPATIBILITY | 3 | 0x000B
[7 empty] | START_BIT |  | START_BIT | 3 | 0x0001
[7 empty] | STRING1_CURRENT |  | STRING1_CURRENT | 3 | 0x1051
[7 empty] | STRING1_VOLTAGE |  | STRING1_VOLTAGE | 3 | 0x1050
[7 empty] | STRING2_CURRENT |  | STRING2_CURRENT | 3 | 0x1053
[7 empty] | STRING2_VOLTAGE |  | STRING2_VOLTAGE | 3 | 0x1052
[7 empty] | STRING3_CURRENT |  | STRING3_CURRENT | 3 | 0x1055
[7 empty] | STRING3_VOLTAGE |  | STRING3_VOLTAGE | 3 | 0x1054
[7 empty] | STRING4_CURRENT |  | STRING4_CURRENT | 3 | 0x1057
[7 empty] | STRING4_VOLTAGE |  | STRING4_VOLTAGE | 3 | 0x1056
[7 empty] | STRING5_CURRENT |  | STRING5_CURRENT | 3 | 0x1059
[7 empty] | STRING5_VOLTAGE |  | STRING5_VOLTAGE | 3 | 0x1058
[7 empty] | STRING6_CURRENT |  | STRING6_CURRENT | 3 | 0x105B
[7 empty] | STRING6_VOLTAGE |  | STRING6_VOLTAGE | 3 | 0x105A
[7 empty] | STRING7_CURRENT |  | STRING7_CURRENT | 3 | 0x105D
[7 empty] | STRING7_VOLTAGE |  | STRING7_VOLTAGE | 3 | 0x105C
[7 empty] | STRING8_CURRENT |  | STRING8_CURRENT | 3 | 0x105F
[7 empty] | STRING8_VOLTAGE |  | STRING8_VOLTAGE | 3 | 0x105E
[7 empty] | STRING_1_3_CURRENT |  | STRING_1_3_CURRENT | 3 | 0x80C0
[7 empty] | STRING_1_4_CURRENT |  | STRING_1_4_CURRENT | 3 | 0x8100
[7 empty] | STRING_2_3_CURRENT |  | STRING_2_3_CURRENT | 3 | 0x8200
[7 empty] | STRING_2_4_CURRENT |  | STRING_2_4_CURRENT | 3 | 0x8240
[7 empty] | STRING_3_3_CURRENT |  | STRING_3_3_CURRENT | 3 | 0x8340
[7 empty] | STRING_3_4_CURRENT |  | STRING_3_4_CURRENT | 3 | 0x8380
[7 empty] | STRING_4_3_CURRENT |  | STRING_4_3_CURRENT | 3 | 0x8480
[7 empty] | STRING_4_4_CURRENT |  | STRING_4_4_CURRENT | 3 | 0x84C0
[7 empty] | STRING_5_1_CURRENT |  | STRING_5_1_CURRENT | 3 | 0x8540
[7 empty] | STRING_5_2_CURRENT |  | STRING_5_2_CURRENT | 3 | 0x8580
[7 empty] | STRING_5_3_CURRENT |  | STRING_5_3_CURRENT | 3 | 0x85C0
[7 empty] | STRING_5_4_CURRENT |  | STRING_5_4_CURRENT | 3 | 0x8600
[7 empty] | STRING_6_1_CURRENT |  | STRING_6_1_CURRENT | 3 | 0x8680
[7 empty] | STRING_6_2_CURRENT |  | STRING_6_2_CURRENT | 3 | 0x86C0
[7 empty] | STRING_6_3_CURRENT |  | STRING_6_3_CURRENT | 3 | 0x8700
[7 empty] | STRING_6_4_CURRENT |  | STRING_6_4_CURRENT | 3 | 0x8740
[7 empty] | STRING_7_1_CURRENT |  | STRING_7_1_CURRENT | 3 | 0x87C0
[7 empty] | STRING_7_2_CURRENT |  | STRING_7_2_CURRENT | 3 | 0x8800
[7 empty] | STRING_7_3_CURRENT |  | STRING_7_3_CURRENT | 3 | 0x8840
[7 empty] | STRING_7_4_CURRENT |  | STRING_7_4_CURRENT | 3 | 0x8880
[7 empty] | STRING_8_1_CURRENT |  | STRING_8_1_CURRENT | 3 | 0x8900
[7 empty] | STRING_8_2_CURRENT |  | STRING_8_2_CURRENT | 3 | 0x8940
[7 empty] | STRING_8_3_CURRENT |  | STRING_8_3_CURRENT | 3 | 0x8980
[7 empty] | STRING_8_4_CURRENT |  | STRING_8_4_CURRENT | 3 | 0x89C0
[7 empty] | STRING_9_1_CURRENT |  | STRING_9_1_CURRENT | 3 | 0x8A40
[7 empty] | STRING_9_2_CURRENT |  | STRING_9_2_CURRENT | 3 | 0x8A80
[7 empty] | STRING_9_3_CURRENT |  | STRING_9_3_CURRENT | 3 | 0x8AC0
[7 empty] | STRING_9_4_CURRENT |  | STRING_9_4_CURRENT | 3 | 0x8B00
[7 empty] | TODAY_EXPORT_ENERGY |  | TODAY_EXPORT_ENERGY | 3 | 0x1334
[7 empty] | TODAY_IMPORT_ENERGY |  | TODAY_IMPORT_ENERGY | 3 | 0x1332
[7 empty] | TODAY_LOAD_ENERGY |  | TODAY_LOAD_ENERGY | 3 | 0x1336
[7 empty] | TOTAL_GENERATION_TIME |  | TOTAL_GENERATION_TIME | 3 | 0x1023
[7 empty] | TRACKER_5_VOLTAGE |  | TRACKER_5_VOLTAGE | 3 | 0x8500
[7 empty] | TRACKER_6_VOLTAGE |  | TRACKER_6_VOLTAGE | 3 | 0x8640
[7 empty] | TRACKER_7_VOLTAGE |  | TRACKER_7_VOLTAGE | 3 | 0x8780
[7 empty] | TRACKER_8_VOLTAGE |  | TRACKER_8_VOLTAGE | 3 | 0x88C0
[7 empty] | TRACKER_9_VOLTAGE |  | TRACKER_9_VOLTAGE | 3 | 0x8A00

## MPPT_MAPPING
MPPT_MAPPING — MPPT/String 전압·전류 수동 매핑
※ D열에서 매핑할 레지스터 선택. E~G는 추천 후보, H는 전체 레지스터.
No | Field | 설명 | 매칭된 레지스터 (주소) | 추천 후보 1 | 추천 후보 2 | 추천 후보 3 | 전체 레지스터 목록 | FC
1 | mppt1_voltage | MPPT1 전압 | MPPT1_VOLTAGE (0x1010) |  |  |  | ACCUMULATED_ENERGY_OFEXPORT | 3 | ACCUMULATED_ENERGY_OFEXPORT | 3 | 0x1308 | pdf
2 | mppt1_current | MPPT1 전류 | MPPT1_CURRENT (0x1011) |  |  |  | ACCUMULATED_ENERGY_OFIMPORT | 3 | ACCUMULATED_ENERGY_OFIMPORT | 3 | 0x1306 | pdf
3 | mppt2_voltage | MPPT2 전압 | MPPT2_VOLTAGE (0x1014) |  |  |  | ACCUMULATED_ENERGY_OF_LOAD | 3 | ACCUMULATED_ENERGY_OF_LOAD | 3 | 0x1310 | pdf
4 | mppt2_current | MPPT2 전류 | MPPT2_CURRENT (0x1015) |  |  |  | AC_POWER | 3 | AC_POWER | 3 | 0x1037 | pdf
5 | mppt3_voltage | MPPT3 전압 | MPPT3_VOLTAGE (0x1018) |  |  |  | CUMULATIVE_ENERGY | 3 | CUMULATIVE_ENERGY | 3 | 0x1021 | pdf
6 | mppt3_current | MPPT3 전류 | MPPT3_CURRENT (0x1019) |  |  |  | DAILY_ENERGY | 3 | DAILY_ENERGY | 3 | 0x1027 | pdf
7 | mppt4_voltage | MPPT4 전압 | MPPT4_VOLTAGE (0x103E) |  |  |  | DC_LINK_OVER_VOLTAGE | 3 | DC_LINK_OVER_VOLTAGE | 3 | 0x0009 | pdf
8 | mppt4_current | MPPT4 전류 | MPPT4_CURRENT (0x103F) |  |  |  | DECIMALS_OF_TOTAL_ENERGY | 3 | DECIMALS_OF_TOTAL_ENERGY | 3 | 0x104C | pdf
9 | string1_voltage | String1 전압 |  | STRING1_VOLTAGE (0x1050) |  |  | DEVICE_MODEL_NAME | 3 | DEVICE_MODEL_NAME | 3 | 0x1A00
10 | string1_current | String1 전류 | STRING1_CURRENT (0x1051) |  |  |  | DEVICE_SERIAL_NUMBER | 3 | DEVICE_SERIAL_NUMBER | 3 | 0x1A10 | pdf
11 | string2_voltage | String2 전압 |  | STRING2_VOLTAGE (0x1052) |  |  | EMS_FIRMWARE_VERSION | 3 | EMS_FIRMWARE_VERSION | 3 | 0x1A60
12 | string2_current | String2 전류 | STRING2_CURRENT (0x1053) |  |  |  | ERROR_CODE1 | 3 | ERROR_CODE1 | 3 | 0x101E | pdf
13 | string3_voltage | String3 전압 |  | STRING3_VOLTAGE (0x1054) |  |  | ERROR_CODE2 | 3 | ERROR_CODE2 | 3 | 0x101F
14 | string3_current | String3 전류 | STRING3_CURRENT (0x1055) |  |  |  | ERROR_CODE3 | 3 | ERROR_CODE3 | 3 | 0x1020 | pdf
15 | string4_voltage | String4 전압 |  | STRING4_VOLTAGE (0x1056) |  |  | EXTERNAL_FAN_SPEED_DUTYPERCENTAGE | 3 | EXTERNAL_FAN_SPEED_DUTYPERCENTAGE | 3 | 0x120C
16 | string4_current | String4 전류 | STRING4_CURRENT (0x1057) |  |  |  | FREQUENCY | 3 | FREQUENCY | 3 | 0x000F | pdf
17 | string5_voltage | String5 전압 |  | STRING5_VOLTAGE (0x1058) |  |  | GFCI_ABNORMAL | 3 | GFCI_ABNORMAL | 3 | 0x0004
18 | string5_current | String5 전류 | STRING5_CURRENT (0x1059) |  |  |  | GRID_PHASE_NUMBER | 3 | GRID_PHASE_NUMBER | 3 | 0x1A48 | pdf
19 | string6_voltage | String6 전압 |  | STRING6_VOLTAGE (0x105A) |  |  | GRID_TOTAL_REACTIVE_POWER | 3 | GRID_TOTAL_REACTIVE_POWER | 3 | 0x1039
20 | string6_current | String6 전류 | STRING6_CURRENT (0x105B) |  |  |  | HISTORY_LOG_0 | 3 | HISTORY_LOG_0 | 3 | 0xB600 | pdf
21 | string7_voltage | String7 전압 |  | STRING7_VOLTAGE (0x105C) |  |  | HISTORY_LOG_127 | 3 | HISTORY_LOG_127 | 3 | 0xB77D
22 | string7_current | String7 전류 | STRING7_CURRENT (0x105D) |  |  |  | INNER_TEMP | 3 | INNER_TEMP | 3 | 0x101C | pdf
23 | string8_voltage | String8 전압 |  | STRING8_VOLTAGE (0x105E) |  |  | INTERNAL_COMMUNICATION_ERROR | 3 | INTERNAL_COMMUNICATION_ERROR | 3 | 0x000A
24 | string8_current | String8 전류 | STRING8_CURRENT (0x105F) |  |  |  | INTERNAL_STORAGE_ERROR | 3 | INTERNAL_STORAGE_ERROR | 3 | 0x000C | pdf
[7 empty] | INVERTER_MODE |  | INVERTER_MODE | 3 | 0x101D
[7 empty] | L1_CURRENT |  | L1_CURRENT | 3 | 0x1002
[7 empty] | L1_CURRENT_OF_GRID |  | L1_CURRENT_OF_GRID | 3 | 0x131D
[7 empty] | L1_CURRENT_OF_LOAD |  | L1_CURRENT_OF_LOAD | 3 | 0x1326
[7 empty] | L1_N_PHASE_VOLTAGE_OF_GRID |  | L1_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131A
[7 empty] | L1_N_PHASE_VOLTAGE_OF_LOAD |  | L1_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1323
[7 empty] | L1_POWER |  | L1_POWER | 3 | 0x1003
[7 empty] | L1_VOLTAGE |  | L1_VOLTAGE | 3 | 0x0026
[7 empty] | L1_WATT_OF_GRID |  | L1_WATT_OF_GRID | 3 | 0x1300
[7 empty] | L1_WATT_OF_LOAD |  | L1_WATT_OF_LOAD | 3 | 0x130A
[7 empty] | L2_CURRENT |  | L2_CURRENT | 3 | 0x1007
[7 empty] | L2_CURRENT_OF_GRID |  | L2_CURRENT_OF_GRID | 3 | 0x131F
[7 empty] | L2_CURRENT_OF_LOAD |  | L2_CURRENT_OF_LOAD | 3 | 0x1328
[7 empty] | L2_FREQUENCY |  | L2_FREQUENCY | 3 | 0x100A
[7 empty] | L2_N_PHASE_VOLTAGE_OF_GRID |  | L2_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131B
[7 empty] | L2_N_PHASE_VOLTAGE_OF_LOAD |  | L2_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1324
[7 empty] | L2_POWER |  | L2_POWER | 3 | 0x1008
[7 empty] | L2_VOLTAGE |  | L2_VOLTAGE | 3 | 0x000D
[7 empty] | L2_WATT_OF_GRID |  | L2_WATT_OF_GRID | 3 | 0x1302
[7 empty] | L2_WATT_OF_LOAD |  | L2_WATT_OF_LOAD | 3 | 0x130C
[7 empty] | L3_CURRENT |  | L3_CURRENT | 3 | 0x100C
[7 empty] | L3_CURRENT_OF_GRID |  | L3_CURRENT_OF_GRID | 3 | 0x1321
[7 empty] | L3_CURRENT_OF_LOAD |  | L3_CURRENT_OF_LOAD | 3 | 0x132A
[7 empty] | L3_FREQUENCY |  | L3_FREQUENCY | 3 | 0x100F
[7 empty] | L3_N_PHASE_VOLTAGE_OF_GRID |  | L3_N_PHASE_VOLTAGE_OF_GRID | 3 | 0x131C
[7 empty] | L3_N_PHASE_VOLTAGE_OF_LOAD |  | L3_N_PHASE_VOLTAGE_OF_LOAD | 3 | 0x1325
[7 empty] | L3_POWER |  | L3_POWER | 3 | 0x100D
[7 empty] | L3_VOLTAGE |  | L3_VOLTAGE | 3 | 0x000E
[7 empty] | L3_WATT_OF_GRID |  | L3_WATT_OF_GRID | 3 | 0x1304
[7 empty] | L3_WATT_OF_LOAD |  | L3_WATT_OF_LOAD | 3 | 0x130E
[7 empty] | LCD_FIRMWARE_VERSION |  | LCD_FIRMWARE_VERSION | 3 | 0x1A8E
[7 empty] | MASTER_FIRMWARE_VERSION |  | MASTER_FIRMWARE_VERSION | 3 | 0x1A1C
[7 empty] | MPPT1_CURRENT |  | MPPT1_CURRENT | 3 | 0x1011
[7 empty] | MPPT1_POWER |  | MPPT1_POWER | 3 | 0x1012
[7 empty] | MPPT1_VOLTAGE |  | MPPT1_VOLTAGE | 3 | 0x1010
[7 empty] | MPPT2_CURRENT |  | MPPT2_CURRENT | 3 | 0x1015
[7 empty] | MPPT2_POWER |  | MPPT2_POWER | 3 | 0x1016
[7 empty] | MPPT2_VOLTAGE |  | MPPT2_VOLTAGE | 3 | 0x1014
[7 empty] | MPPT3_CURRENT |  | MPPT3_CURRENT | 3 | 0x1019
[7 empty] | MPPT3_POWER |  | MPPT3_POWER | 3 | 0x101A
[7 empty] | MPPT3_VOLTAGE |  | MPPT3_VOLTAGE | 3 | 0x1018
[7 empty] | MPPT4_CURRENT |  | MPPT4_CURRENT | 3 | 0x103F
[7 empty] | MPPT4_POWER |  | MPPT4_POWER | 3 | 0x1040
[7 empty] | MPPT4_VOLTAGE |  | MPPT4_VOLTAGE | 3 | 0x103E
[7 empty] | MPPT_NUMBER |  | MPPT_NUMBER | 3 | 0x1A3B
[7 empty] | NOMINAL_ACTIVE_POWER_HIGH_WORD |  | NOMINAL_ACTIVE_POWER_HIGH_WORD | 3 | 0x1A4E
[7 empty] | NOMINAL_ACTIVE_POWER_LOW_WORD |  | NOMINAL_ACTIVE_POWER_LOW_WORD | 3 | 0x1A46
[7 empty] | NOMINAL_FREQUENCY |  | NOMINAL_FREQUENCY | 3 | 0x1A45
[7 empty] | NOMINAL_VOLTAGE |  | NOMINAL_VOLTAGE | 3 | 0x1A44
[7 empty] | POWER_FACTOR |  | POWER_FACTOR | 3 | 0x0000
[7 empty] | PV_POWER |  | PV_POWER | 3 | 0x1048
[7 empty] | PV_STRING_COUNT |  | PV_STRING_COUNT | 3 | 0x0008
[7 empty] | PV_STRING_REVERSE |  | PV_STRING_REVERSE | 3 | 0x0005
[7 empty] | PV_TODAY_PEAK_POWER |  | PV_TODAY_PEAK_POWER | 3 | 0x103B
[7 empty] | Q_REFERENCE_OUTPUT_REACTIVEPOWER |  | Q_REFERENCE_OUTPUT_REACTIVEPOWER | 3 | 0x1226
[7 empty] | READ_REGISTER_ADDRESS |  | READ_REGISTER_ADDRESS | 3 | 0x0003
[7 empty] | REGISTER_NUMBER |  | REGISTER_NUMBER | 3 | 0x0002
[7 empty] | REG_0X07 |  | REG_0X07 | 3 | 0x0007
[7 empty] | REG_0_PNOM_PNOM_NOMINAL_POWER |  | REG_0_PNOM_PNOM_NOMINAL_POWER | 3 | 0x30B9
[7 empty] | SLAVE_FIRMWARE_VERSION |  | SLAVE_FIRMWARE_VERSION | 3 | 0x1A26
[7 empty] | SOFTWARE_INCOMPATIBILITY |  | SOFTWARE_INCOMPATIBILITY | 3 | 0x000B
[7 empty] | START_BIT |  | START_BIT | 3 | 0x0001
[7 empty] | STRING1_CURRENT |  | STRING1_CURRENT | 3 | 0x1051
[7 empty] | STRING1_VOLTAGE |  | STRING1_VOLTAGE | 3 | 0x1050
[7 empty] | STRING2_CURRENT |  | STRING2_CURRENT | 3 | 0x1053
[7 empty] | STRING2_VOLTAGE |  | STRING2_VOLTAGE | 3 | 0x1052
[7 empty] | STRING3_CURRENT |  | STRING3_CURRENT | 3 | 0x1055
[7 empty] | STRING3_VOLTAGE |  | STRING3_VOLTAGE | 3 | 0x1054
[7 empty] | STRING4_CURRENT |  | STRING4_CURRENT | 3 | 0x1057
[7 empty] | STRING4_VOLTAGE |  | STRING4_VOLTAGE | 3 | 0x1056
[7 empty] | STRING5_CURRENT |  | STRING5_CURRENT | 3 | 0x1059
[7 empty] | STRING5_VOLTAGE |  | STRING5_VOLTAGE | 3 | 0x1058
[7 empty] | STRING6_CURRENT |  | STRING6_CURRENT | 3 | 0x105B
[7 empty] | STRING6_VOLTAGE |  | STRING6_VOLTAGE | 3 | 0x105A
[7 empty] | STRING7_CURRENT |  | STRING7_CURRENT | 3 | 0x105D
[7 empty] | STRING7_VOLTAGE |  | STRING7_VOLTAGE | 3 | 0x105C
[7 empty] | STRING8_CURRENT |  | STRING8_CURRENT | 3 | 0x105F
[7 empty] | STRING8_VOLTAGE |  | STRING8_VOLTAGE | 3 | 0x105E
[7 empty] | STRING_1_3_CURRENT |  | STRING_1_3_CURRENT | 3 | 0x80C0
[7 empty] | STRING_1_4_CURRENT |  | STRING_1_4_CURRENT | 3 | 0x8100
[7 empty] | STRING_2_3_CURRENT |  | STRING_2_3_CURRENT | 3 | 0x8200
[7 empty] | STRING_2_4_CURRENT |  | STRING_2_4_CURRENT | 3 | 0x8240
[7 empty] | STRING_3_3_CURRENT |  | STRING_3_3_CURRENT | 3 | 0x8340
[7 empty] | STRING_3_4_CURRENT |  | STRING_3_4_CURRENT | 3 | 0x8380
[7 empty] | STRING_4_3_CURRENT |  | STRING_4_3_CURRENT | 3 | 0x8480
[7 empty] | STRING_4_4_CURRENT |  | STRING_4_4_CURRENT | 3 | 0x84C0
[7 empty] | STRING_5_1_CURRENT |  | STRING_5_1_CURRENT | 3 | 0x8540
[7 empty] | STRING_5_2_CURRENT |  | STRING_5_2_CURRENT | 3 | 0x8580
[7 empty] | STRING_5_3_CURRENT |  | STRING_5_3_CURRENT | 3 | 0x85C0
[7 empty] | STRING_5_4_CURRENT |  | STRING_5_4_CURRENT | 3 | 0x8600
[7 empty] | STRING_6_1_CURRENT |  | STRING_6_1_CURRENT | 3 | 0x8680
[7 empty] | STRING_6_2_CURRENT |  | STRING_6_2_CURRENT | 3 | 0x86C0
[7 empty] | STRING_6_3_CURRENT |  | STRING_6_3_CURRENT | 3 | 0x8700
[7 empty] | STRING_6_4_CURRENT |  | STRING_6_4_CURRENT | 3 | 0x8740
[7 empty] | STRING_7_1_CURRENT |  | STRING_7_1_CURRENT | 3 | 0x87C0
[7 empty] | STRING_7_2_CURRENT |  | STRING_7_2_CURRENT | 3 | 0x8800
[7 empty] | STRING_7_3_CURRENT |  | STRING_7_3_CURRENT | 3 | 0x8840
[7 empty] | STRING_7_4_CURRENT |  | STRING_7_4_CURRENT | 3 | 0x8880
[7 empty] | STRING_8_1_CURRENT |  | STRING_8_1_CURRENT | 3 | 0x8900
[7 empty] | STRING_8_2_CURRENT |  | STRING_8_2_CURRENT | 3 | 0x8940
[7 empty] | STRING_8_3_CURRENT |  | STRING_8_3_CURRENT | 3 | 0x8980
[7 empty] | STRING_8_4_CURRENT |  | STRING_8_4_CURRENT | 3 | 0x89C0
[7 empty] | STRING_9_1_CURRENT |  | STRING_9_1_CURRENT | 3 | 0x8A40
[7 empty] | STRING_9_2_CURRENT |  | STRING_9_2_CURRENT | 3 | 0x8A80
[7 empty] | STRING_9_3_CURRENT |  | STRING_9_3_CURRENT | 3 | 0x8AC0
[7 empty] | STRING_9_4_CURRENT |  | STRING_9_4_CURRENT | 3 | 0x8B00
[7 empty] | TODAY_EXPORT_ENERGY |  | TODAY_EXPORT_ENERGY | 3 | 0x1334
[7 empty] | TODAY_IMPORT_ENERGY |  | TODAY_IMPORT_ENERGY | 3 | 0x1332
[7 empty] | TODAY_LOAD_ENERGY |  | TODAY_LOAD_ENERGY | 3 | 0x1336
[7 empty] | TOTAL_GENERATION_TIME |  | TOTAL_GENERATION_TIME | 3 | 0x1023
[7 empty] | TRACKER_5_VOLTAGE |  | TRACKER_5_VOLTAGE | 3 | 0x8500
[7 empty] | TRACKER_6_VOLTAGE |  | TRACKER_6_VOLTAGE | 3 | 0x8640
[7 empty] | TRACKER_7_VOLTAGE |  | TRACKER_7_VOLTAGE | 3 | 0x8780
[7 empty] | TRACKER_8_VOLTAGE |  | TRACKER_8_VOLTAGE | 3 | 0x88C0
[7 empty] | TRACKER_9_VOLTAGE |  | TRACKER_9_VOLTAGE | 3 | 0x8A00