## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Huawei
프로토콜 버전
설비 타입 | inverter
MPPT | 8
String | 8
String 모니터링 | No (MPPT당 1 String)
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | Huawei-PV_SUN2000MC_Modbus_Interface_Definitions.pdf
추출 일시 | 2026-04-09 12:08
H01 매칭 | 42/42
DER 매칭 | 33/33
추출 레지스터 | 1060
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | SERIAL_NUMBER | 0x0014 | 03 | U16 |  | RO |  | Alias ¦ N/A
2 | FIRMWARE_VERSION | 0x001E | 03 | U16 |  | RO |  | Software version ¦ N/A
3 | LOW_INSULATION_RESISTANCE | 0x080E | 03 | U16 |  | RO |  | Low Insulation Resistance
4 | Model | 0x7530 |  | STRING |  | RO
5 | SERIAL_NUMBER | 0x753F |  | STRING |  | RO |  | SN
6 | FirmwareVersion | 0x7553 |  | STRING |  | RO
7 | Softwareversion | 0x7562 |  | STRING |  | RO
8 | Protocolversion[Modbus] | 0x7574 |  | U32 |  | RO
9 | Model ID | 0x7576 |  | U16 |  | RO
10 | RATEDPOWER | 0x7579 |  | U32 | kW 1000 | RO |  | Ratedpower
11 | ProductSoftwareVersionNumber | 0x759C |  | U16 |  | RO
12 | PowerGridStandardCodeProtocolVersion | 0x759D |  | U16 |  | RO
13 | [Third-partylabeling]SN | 0x75EF |  | STRING |  | RO
14 | [Third-partylabel]Manufacturermodel | 0x75F9 |  | U16 |  | RO
15 | MonitoringBoard SN | 0x7927 |  | STRING |  | RO
16 | Monitoringsoftwareversion | 0x7931 |  | STRING |  | RO
17 | DeviceSNfeaturecode | 0x7D0F |  | U16 |  | RO
18 | INNER_TEMP | 0x7D57 |  | S16 | 10 | RO | temperature | Internaltemperature
19 | INSULATION_IMPEDANCE | 0x7D58 |  | U16 | 1000 | RO |  | Insulationimpedance
20 | AlarmclearanceSN | 0x7D9B |  | U16 |  | RO
21 | Serialnumberofthelatestactivealarm. | 0x7DAC |  | U32 |  | RO
22 | LatestHistoricalAlarmSerialNumber | 0x7DAE |  | U32 |  | RO
23 | TOTALBUSVOLTAGE | 0x7DB0 |  | S16 | V 10 | RO |  | Totalbusvoltage
24 | MPPT3DCTOTAL_ENERGY_YIELD | 0x7DD8 |  | U32 | kWh 100 | RO | cumulative_energy | MPPT3DCTotalEnergyYield
25 | RUNNINGTIMEOFCAPACITORBANK | 0x88B8 |  | U32 | 10 | RO |  | Runningtimeofcapacitorbank
26 | INTERNALFAN1RUNNINGTIME | 0x88BA |  | U32 | 10 | RO |  | Internalfan1runningtime
27 | INTERNALTEMPERATURE7 | 0x88D3 |  | S16 | 10 | RO |  | Internaltemperature7
28 | INTERNALTEMPERATURE8 | 0x88D4 |  | S16 | 10 | RO |  | Internaltemperature8
29 | INTERNALTEMPERATURE9 | 0x88D5 |  | S16 | 10 | RO |  | Internaltemperature9
30 | INTERNALTEMPERATURE10 | 0x88D6 |  | S16 | 10 | RO |  | Internaltemperature10
31 | INTERNALTEMPERATURE11 | 0x88D7 |  | S16 | 10 | RO |  | Internaltemperature11
32 | INTERNALTEMPERATURE12 | 0x88D8 |  | S16 | 10 | RO |  | Internaltemperature12
33 | POSITIVEBUSVOLTAGE | 0x88E2 |  | S16 | V 10 | RO |  | Positivebusvoltage
34 | NEGATIVEBUSVOLTAGE | 0x88E3 |  | S16 | V 10 | RO |  | Negativebusvoltage
35 | BUSnegativevoltagetoground | 0x88E4 |  | S16 | V 10 | RO
36 | LicenseSN | 0x8949 |  | STRING | 1 | RO
37 | MeterModelCheckResult | 0x9112 |  | U16 |  | RO
38 | LayoutFileChangeSN | 0x915A |  | U16 | 1 | RO
39 | DC_MBUSNETWORKINGSTATUS | 0x9182 |  | U16 |  | RO |  | [DC-MBUS]Networkingstatus
40 | SERIAL_NUMBER | 0x9187 |  | STRING |  | RO |  | SN
41 | SERIAL_NUMBER | 0x9218 |  | STRING | 1 | RO |  | SN
42 | Softwareversion | 0x9267 |  | STRING |  | RO
43 | Replacethetargetmodel. | 0xA41C |  | U16 | 1 | RW
44 | MAXIMUMAPPARENTPOWER | 0xA425 |  | U32 | kVA 1000 | RW |  | Maximumapparentpower
45 | APPARENTPOWERREFERENCE | 0xA429 |  | U32 | 1000 | RW |  | apparentpowerreference
46 | ScienceandTechnologyJingkeProtocolVersion | 0xAC47 | 03 | U16 |  | RW
47 | INNER_TEMP | 0xAD78 | 03 | S16 | 10 | WO | temperature | Temperature1
48 | CLEAR_THERUNNINGTIMEINFORMATION | 0xAFD3 | 03 | U16 |  | WO |  | Clear therunningtimeinformation.
49 | ESNvalidationcommand | 0xAFD7 | 03 | U16 | 1 | WO
50 | Metermodel | 0xB8C7 | 03 | U16 |  | RW
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | REMOTESIGNAL_RUNNINGSTATUSMONITORING | 0x7D02 |  | U16 |  | RO |  | [Remotesignal]Runningstatus(monitoring)
2 | REMOTESIGNAL_RUNNINGSTATUSPOWERPROCESSING | 0x7D03 |  | U32 | 1 | RO |  | [Remotesignal]Runningstatus(powerprocessing)
3 | INVERTER_MODE | 0x7D59 |  | U16 |  | RO | inverter_status | DeviceStatus
4 | BUILT_IN_PIDRUNNINGSTATUS | 0x7DBE |  | U16 |  | RO |  | Built-inPIDrunningstatus
5 | String 1accessstatus | 0x7E2C |  | STRINGING |  | RO
6 | String 2accessstatus | 0x7E2D |  | STRINGING |  | RO
7 | String 3accessstatus | 0x7E2E |  | STRINGING |  | RO
8 | String 4accessstatus | 0x7E2F |  | STRINGING |  | RO
9 | String 5accessstatus | 0x7E30 |  | STRINGING |  | RO
10 | CONNECTIONSTATUS_OFSTRING_6 | 0x7E31 |  | U16 |  | RO |  | Connectionstatus ofstring 6
11 | String 7accessstatus | 0x7E32 |  | STRINGING |  | RO
12 | String 8accessstatus | 0x7E33 |  | STRINGING |  | RO
13 | STENT_SYSTEM_STATUS | 0x84D0 |  | U32 |  | RO | inverter_status | StentSystemStatus
14 | SUPPORTACCESSSTATUS | 0x84F6 |  | U32 | 1 | RO |  | Supportaccessstatus
15 | I_VSCANSTATUS | 0x8916 |  | U16 |  | RO |  | I-Vscanstatus
16 | STAWLANLISTSCANNINGSTATUS | 0x8921 |  | U16 |  | RO |  | [STA]WLANlistscanningstatus
17 | NTPLAST_NTPSYNCHRONIZATIONSTATUS | 0x8928 |  | U16 | 1 | RO |  | [NTP]LastNTPsynchronizationstatus.
18 | REG_4GTRAFFICSTATUS | 0x8932 |  | U16 |  | RO |  | [4G]Trafficstatus
19 | STAROUTERCONNECTIONSTATUS | 0x8935 |  | U16 |  | RO |  | [STA]Routerconnectionstatus
20 | FECONNECTIONSTATUS | 0x8936 |  | U16 | 1 | RO |  | [FE]Connectionstatus
21 | Smart I-V-V-Diagnosis(License)Status | 0x8942 |  | U16 | V | RO
22 | STRINGMONITORING_LICENSESTATUS | 0x8995 |  | U16 |  | RO |  | [Stringmonitoring]Licensestatus
23 | REG_4GMODULESTATUS | 0x89B1 |  | U16 |  | RO |  | [4G]Modulestatus
24 | REG_4GPINCHECKSTATUS | 0x89C2 |  | U16 |  | RO |  | [4G]PINcheckstatus
25 | ACTIVEPOWERADJUSTMENTSTATUS | 0x89E4 |  | U16 |  | RO |  | Activepoweradjustmentstatus
26 | REACTIVEPOWERADJUSTMENTSTATUS | 0x89E8 |  | U16 |  | RO |  | Reactivepoweradjustmentstatus
27 | UPGRADESTATUS_ID | 0x8CC1 |  | U16 |  | RO |  | Upgradestatus ID.
28 | MODULE1RUNNINGSTATUS_OFTHEBATTERY | 0x9088 |  | U16 |  | RO |  | [Module1]Runningstatus ofthebattery
29 | METER_STATUS | 0x90EC |  | U16 |  | RO |  | MeterStatus
30 | CURRENTSTATUS_OFTHEPHYSICALLOCATION | 0x9156 |  | U16 |  | RO |  | Currentstatus ofthephysicallocation
31 | RELATIVE_POSITIONING_STATUS | 0x9158 |  | U16 |  | RO |  | RelativePositioningStatus
32 | DISCONNECTEDSTATUS | 0x915C |  | U16 |  | RO |  | Disconnectedstatus
33 | FAST_SHUTDOWN_SELF_TEST_STATUS | 0x9185 |  | U16 |  | RO |  | FastShutdownSelfTestStatus
34 | RUNNINGSTATUS | 0x9186 |  | U16 |  | RO |  | Runningstatus
35 | SCHEDULESERVER_COMMUNICATIONSTATUS | 0x9263 |  | U16 |  | RO |  | [Scheduleserver]Communicationstatus
36 | SCHEDULESERVER_LATESTCONNECTIONSTATUS | 0x9264 |  | U16 |  | RO |  | [Scheduleserver]Latestconnectionstatus
37 | UPGRADE_STATUS | 0x9279 |  | U16 |  | RO |  | UpgradeStatus
38 | INVERTERCOMPREHENSIVESTATUS | 0x928E |  | U16 |  | RO |  | Invertercomprehensivestatus
39 | INVERTERINTEGRATEDSTATUSSUPPORTFLAG | 0x928F |  | U16 | 1 | RO |  | Inverterintegratedstatussupportflag
40 | Operatingmode | 0xA5A9 | 03 | U16 |  | RW
41 | Operatingmode | 0xABE1 | 03 | U16 |  | RW
42 | Operatingmode | 0xB79C | 03 | U16 |  | RW
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | DEVICE_FAULT | 0x0810 | 03 | U16 |  | RO |  | Device Fault
2 | FAULTY_POWER_COLLECTOR2 | 0x0813 | 03 | U16 |  | RO |  | Faulty Power Collector[2]
3 | OPTIMIZER_FAULT5 | 0x0821 | 03 | U16 |  | RO |  | Optimizer fault[5]
4 | ALARM1 | 0x7D08 |  | U16 |  | RO |  | [Remotesignal]Alarm 1
5 | ALARM2 | 0x7D09 |  | U16 |  | RO |  | [Remotesignal]Alarm 2
6 | ALARM3 | 0x7D0A |  | U16 |  | RO |  | [Remotesignal]Alarm 3
7 | ALARM4 | 0x7D0B |  | U16 |  | RO |  | [Remotesignal]Alarm 4
8 | ALARM5 | 0x7D0C |  | U16 |  | RO |  | [Remotesignal]Alarm 5
9 | ALARM6 | 0x7D0D |  | U16 |  | RO |  | [Remotesignal]Alarm 6
10 | FAULT_CODE | 0x7D5A |  | U16 |  | RO |  | FaultCode
11 | NUMBEROFCRITICALALARMS | 0x7D97 |  | U16 | 1 | RO |  | Numberofcriticalalarms
12 | NUMBEROFMAJORALARMS | 0x7D98 |  | U16 | 1 | RO |  | Numberofmajoralarms
13 | NUMBEROF_MINOR_ALARMS | 0x7D99 |  | U16 | 1 | RO |  | NumberofMinorAlarms
14 | NUMBEROF_WARNING_ALARMS | 0x7D9A |  | U16 | 1 | RO |  | NumberofWarningAlarms
15 | MONITORINGALARM_1 | 0x7DFC |  | U16 |  | RO |  | Monitoringalarm 1
16 | MONITORINGALARM_2 | 0x7DFD |  | U16 |  | RO |  | Monitoringalarm 2
17 | MONITORALARM_3 | 0x7DFE |  | U16 |  | RO |  | Monitoralarm 3
18 | EXTERNAL_POWERALARM_1 | 0x7DFF |  | U16 |  | RO |  | [External]Poweralarm 1
19 | EXTERNAL_POWERALARM_2 | 0x7E00 |  | U16 |  | RO |  | [External]Poweralarm 2
20 | EXTERNAL_POWERALARM_3 | 0x7E01 |  | U16 |  | RO |  | [External]Poweralarm 3
21 | EXTERNAL_POWERALARM_4 | 0x7E02 |  | U16 |  | RO |  | [External]Poweralarm 4
22 | EXTERNAL_POWERALARM_5 | 0x7E03 |  | U16 |  | RO |  | [External]Poweralarm 5
23 | EXTERNAL_POWERALARM_6 | 0x7E04 |  | U16 |  | RO |  | [External]Poweralarm 6
24 | EXTERNAL_POWERALARM_7 | 0x7E05 |  | U16 |  | RO |  | [External]Poweralarm 7
25 | EXTERNAL_POWERALARM_8 | 0x7E06 |  | U16 |  | RO |  | [External]Poweralarm 8
26 | EXTERNAL_POWERALARM_9 | 0x7E07 |  | U16 |  | RO |  | [External]Poweralarm 9
27 | EXTERNAL_POWERALARM10 | 0x7E08 |  | U16 |  | RO |  | [External]Poweralarm10
28 | EXTERNAL_POWERALARM11 | 0x7E09 |  | U16 |  | RO |  | [External]Poweralarm11
29 | EXTERNAL_POWERALARM12 | 0x7E0A |  | U16 |  | RO |  | [External]Poweralarm12
30 | EXTERNAL_POWERALARM13 | 0x7E0B |  | U16 |  | RO |  | [External]Poweralarm13
31 | EXTERNAL_POWERALARM14 | 0x7E0C |  | U16 |  | RO |  | [External]Poweralarm14
32 | EXTERNAL_POWERALARM15 | 0x7E0D |  | U16 |  | RO |  | [External]Poweralarm15
33 | EXTERNAL_POWERALARM16 | 0x7E0E |  | U16 |  | RO |  | [External]Poweralarm16
34 | MONITORALARM_4 | 0x7E0F |  | U16 |  | RO |  | Monitoralarm 4
35 | MONITORALARM_5 | 0x7E10 |  | U16 |  | RO |  | Monitoralarm 5
36 | EXTERNAL_POWERALARM17 | 0x7E11 |  | U16 |  | RO |  | [External]Poweralarm17
37 | SUPPORT_1GENERAL_FAULT_STATUS | 0x851B |  | U16 |  | RO |  | Support 1GeneralFaultStatus
38 | SUPPORT_1USER_DEFINEDFAULTSTATUS | 0x851C |  | U16 | 1 | RO |  | Support 1user-definedfaultstatus
39 | SUPPORT_2GENERAL_FAULT_STATUS | 0x851D |  | U16 | 1 | RO |  | Support 2GeneralFaultStatus
40 | SUPPORT_2CUSTOM_FAULT_STATUS | 0x851E |  | U16 | 1 | RO |  | Support 2CustomFaultStatus
41 | SUPPORT_3GENERAL_FAULT_STATUS | 0x851F |  | U16 | 1 | RO |  | Support 3GeneralFaultStatus
42 | SUPPORT_3USER_DEFINEDFAULTSTATUS | 0x8520 |  | U16 | 1 | RO |  | Support 3user-definedfaultstatus
43 | SUPPORT_4GENERAL_FAULT_STATUS | 0x8521 |  | U16 | 1 | RO |  | Support 4GeneralFaultStatus
44 | SUPPORT_4CUSTOM_FAULT_STATUS | 0x8522 |  | U16 | 1 | RO |  | Support 4CustomFaultStatus
45 | SUPPORT_5GENERAL_FAULT_STATUS | 0x8523 |  | U16 | 1 | RO |  | Support 5GeneralFaultStatus
46 | SUPPORT_5CUSTOM_FAULT_STATUS | 0x8524 |  | U16 | 1 | RO |  | Support 5CustomFaultStatus
47 | SUPPORT_6GENERAL_FAULT_STATUS | 0x8525 |  | U16 | 1 | RO |  | Support 6GeneralFaultStatus
48 | SUPPORT_6CUSTOM_FAULT_STATUS | 0x8526 |  | U16 | 1 | RO |  | Support 6CustomFaultStatus
49 | SUPPORT_7GENERAL_FAULT_STATUS | 0x8527 |  | U16 | 1 | RO |  | Support 7GeneralFaultStatus
50 | SUPPORT_7CUSTOM_FAULT_STATUS | 0x8528 |  | U16 | 1 | RO |  | Support 7CustomFaultStatus
51 | SUPPORT_8GENERAL_FAULT_STATUS | 0x8529 |  | U16 | 1 | RO |  | Support 8GeneralFaultStatus
52 | SUPPORT_8CUSTOM_FAULT_STATUS | 0x852A |  | U16 | 1 | RO |  | Support 8CustomFaultStatus
53 | SUPPORT_9GENERAL_FAULT_STATUS | 0x852B |  | U16 | 1 | RO |  | Support 9GeneralFaultStatus
54 | SUPPORT_9CUSTOM_FAULT_STATUS | 0x852C |  | U16 | 1 | RO |  | Support 9CustomFaultStatus
55 | SUPPORT10GENERAL_FAULT_STATUS | 0x852D |  | U16 | 1 | RO |  | Support10GeneralFaultStatus
56 | SUPPORT10CUSTOM_FAULT_STATUS | 0x852E |  | U16 | 1 | RO |  | Support10CustomFaultStatus
57 | SUPPORT11GENERAL_FAULT_STATUS | 0x852F |  | U16 | 1 | RO |  | Support11GeneralFaultStatus
58 | SUPPORT11CUSTOM_FAULT_STATUS | 0x8530 |  | U16 | 1 | RO |  | Support11CustomFaultStatus
59 | SUPPORT12GENERAL_FAULT_STATUS | 0x8531 |  | U16 | 1 | RO |  | Support12GeneralFaultStatus
60 | SUPPORT12CUSTOM_FAULT_STATUS | 0x8532 |  | U16 | 1 | RO |  | Support12CustomFaultStatus
61 | SUPPORT13GENERAL_FAULT_STATUS | 0x8533 |  | U16 | 1 | RO |  | Support13GeneralFaultStatus
62 | SUPPORT13CUSTOM_FAULT_STATUS | 0x8534 |  | U16 | 1 | RO |  | Support13CustomFaultStatus
63 | SUPPORT14GENERAL_FAULT_STATUS | 0x8535 |  | U16 | 1 | RO |  | Support14GeneralFaultStatus
64 | SUPPORT14CUSTOM_FAULT_STATUS | 0x8536 |  | U16 | 1 | RO |  | Support14CustomFaultStatus
65 | SUPPORT15GENERAL_FAULT_STATUS | 0x8537 |  | U16 | 1 | RO |  | Support15GeneralFaultStatus
66 | SUPPORT15CUSTOM_FAULT_STATUS | 0x8538 |  | U16 | 1 | RO |  | Support15CustomFaultStatus
67 | SUPPORT16GENERAL_FAULT_STATUS | 0x8539 |  | U16 | 1 | RO |  | Support16GeneralFaultStatus
68 | SUPPORT16CUSTOM_FAULT_STATUS | 0x853A |  | U16 | 1 | RO |  | Support16CustomFaultStatus
69 | Internalalarm | 0x88C2 |  | U16 | V 1 | RO
70 | AUDIBLEANDVISUALALARM | 0xA432 |  | U16 |  | RW |  | Audibleandvisualalarm
71 | POWERGRIDFAULTRECOVERYAUTOMATICSTARTUP | 0xA44D | 03 | U16 |  | RW |  | Powergridfaultrecoveryautomaticstartup
72 | POWER_ONSOFTSTARTTIMEDUETOPOWERGRIDFAULTS | 0xA474 | 03 | U16 | 1 | RW |  | Power-onsoftstarttimeduetopowergridfaults
73 | POWERGRIDFAULTRECOVERYTIME | 0xA478 | 03 | U16 | 1 | RW |  | Powergridfaultrecoverytime
74 | GRIDFAULTZEROCURRENTMODE | 0xA47E | 03 | U16 |  | RW |  | Gridfaultzerocurrentmode
75 | REG_4GDEFAULT_IDENTITYAUTHENTICATIONTYPE | 0xA9A9 | 03 | U16 |  | RW |  | [4G][Default]Identityauthenticationtype
76 | [4G][Default]APN | 0xA9AA | 03 | STRING | 1 | RW
77 | [4G][Default]APNusername | 0xA9CA | 03 | STRING | 1 | RW
78 | SUPPORT_FAULT_CLEARANCE | 0xAC32 | 03 | U16 | 1 | WO |  | SupportFaultClearance
79 | SupportFaultClearance | 0xAD10 | 03 | U16 |  | WO
80 | CLEARINGACTIVEALARMS | 0xAFC9 | 03 | U16 |  | WO |  | Clearingactivealarms
81 | ALARMSETTING | 0xAFCB | 03 | U16 |  | WO |  | Alarmsetting
82 | ALARMCLEARANCE | 0xAFCD | 03 | U16 |  | WO |  | Alarmclearance
83 | ALARMMASKING | 0xAFCE | 03 | U16 |  | WO |  | Alarmmasking
84 | ALARMPORTSELF_CHECKSTART | 0xAFED | 03 | U16 | 1 | WO |  | Alarmportself-checkstart
85 | AUDIBLEANDVISUALALARMCONFIRMATION | 0xAFF0 | 03 | U16 | 1 | WO |  | Audibleandvisualalarmconfirmation
86 | MAXIMUM_FEED_GRID_POWER_DEFAULT | 0xBA3B | 03 | S32 | kW 1000 | RW |  | MaximumFeedGridPowerDefault
87 | DEFAULTACTIVEPOWERCHANGEGRADIENT | 0xBA3D | 03 | U32 | 1000 | RW |  | Defaultactivepowerchangegradient
88 | FAULTY_MONITORING_UNIT | 0xF000 | 03 | U16 |  | RO |  | Faulty Monitoring Unit

## 2_H01
H01 모니터링 매칭 — 42/42
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | PDF_PHASE | O | 0x90ED | Gridvoltage(phase Avoltage) | S32 | V | 10 | 상전압 사용
2 | s_voltage | PDF_PHASE | O | 0x90EF | Phase Bvoltage | S32 | V | 10 | 상전압 사용
3 | t_voltage | PDF_PHASE | O | 0x90F1 | Phase Cvoltage | S32 | V | 10 | 상전압 사용
4 | r_current | PDF_PHASE | O | 0x90F3 | Gridcurrent(phase Acurrent) | S32 | A | 100 | 상전압 사용
5 | s_current | PDF_PHASE | O | 0x90F5 | Phase Bcurrent | S32 | A | 100 | 상전압 사용
6 | t_current | PDF_PHASE | O | 0x90F7 | Phase Ccurrent | S32 | A | 100 | 상전압 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x7D40 | PV_POWER | S32 | kW | 1000 | kW→W (*1000)
13 | cumulative_energy | PDF | O | 0x7D6A | Accumulatedpowergeneration | U32 | kWh | 100 | kWh→Wh (*1000)
14 | cumulative_energy_low | PDF_ALIAS | O | 0x7D6A | Accumulatedpowergeneration | U32 | kWh | 100 | cumulative_energy alias (단일 레지스터에 통합값)
15 | status | PDF | O | 0x7D59 | INVERTER_MODE | U16 |  |  | 0=Standby: initia, 1=Standby: detect, 2=Standby: detect, 3=Standby: drid, 512=On-grid, 768=Shutdown: fault... (+9)
16 | alarm1 | PDF | O | 0x7D5A | FAULT_CODE | U16
17 | alarm2 | PDF | O | 0x7D5A | FAULT_CODE | U16
18 | alarm3 | PDF | O | 0x7D5A | FAULT_CODE | U16
19 | mppt1_voltage | PDF | O | 0x7D10 | PV1voltage | S16 | V | 10
20 | mppt1_current | PDF | O | 0x7D11 | PV1current | S16 | A | 100
21 | mppt2_voltage | PDF | O | 0x7D12 | PV2Voltage | S16 | V | 10
22 | mppt2_current | PDF | O | 0x7D13 | PV2current | S16 | A | 100
23 | mppt3_voltage | PDF | O | 0x7D14 | PV3Voltage | S16 | V | 10
24 | mppt3_current | PDF | O | 0x7D15 | PV3current | S16 | A | 100
25 | mppt4_voltage | PDF | O | 0x7D16 | PV4Voltage | S16 | V | 10
26 | mppt4_current | PDF | O | 0x7D17 | PV4current | S16 | A | 100
27 | mppt5_voltage | PDF | O | 0x7D18 | PV5voltage | S16 | V | 10
28 | mppt5_current | PDF | O | 0x7D19 | PV5current | S16 | A | 100
29 | mppt6_voltage | PDF | O | 0x7D1A | PV6voltage | S16 | V | 10
30 | mppt6_current | PDF | O | 0x7D1B | PV6current | S16 | A | 100
31 | mppt7_voltage | PDF | O | 0x7D1C | PV7Voltage | S16 | V | 10
32 | mppt7_current | PDF | O | 0x7D1D | PV7current | S16 | A | 100
33 | mppt8_voltage | PDF | O | 0x7D1E | PV8Voltage | S16 | V | 10
34 | mppt8_current | PDF | O | 0x7D1F | PV8current | S16 | A | 100
35 | string1_current | HANDLER | O | 0x7D11 | PV1current | S16 | A | 100
36 | string2_current | HANDLER | O | 0x7D13 | PV2current | S16 | A | 100
37 | string3_current | HANDLER | O | 0x7D15 | PV3current | S16 | A | 100
38 | string4_current | HANDLER | O | 0x7D17 | PV4current | S16 | A | 100
39 | string5_current | HANDLER | O | 0x7D19 | PV5current | S16 | A | 100
40 | string6_current | HANDLER | O | 0x7D1B | PV6current | S16 | A | 100
41 | string7_current | HANDLER | O | 0x7D1D | PV7current | S16 | A | 100
42 | string8_current | HANDLER | O | 0x7D1F | PV8current | S16 | A | 100

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 8ch / String 8ch
MPPT 채널 수 | 8
String 채널 수 | 8
String 모니터링 | No (MPPT당 1 String)
MPPT 채널 H01 매칭 (16개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x7D10 | PV1voltage | S16 | V | 10
2 | mppt1_current | PDF | O | 0x7D11 | PV1current | S16 | A | 100
3 | mppt2_voltage | PDF | O | 0x7D12 | PV2Voltage | S16 | V | 10
4 | mppt2_current | PDF | O | 0x7D13 | PV2current | S16 | A | 100
5 | mppt3_voltage | PDF | O | 0x7D14 | PV3Voltage | S16 | V | 10
6 | mppt3_current | PDF | O | 0x7D15 | PV3current | S16 | A | 100
7 | mppt4_voltage | PDF | O | 0x7D16 | PV4Voltage | S16 | V | 10
8 | mppt4_current | PDF | O | 0x7D17 | PV4current | S16 | A | 100
9 | mppt5_voltage | PDF | O | 0x7D18 | PV5voltage | S16 | V | 10
10 | mppt5_current | PDF | O | 0x7D19 | PV5current | S16 | A | 100
11 | mppt6_voltage | PDF | O | 0x7D1A | PV6voltage | S16 | V | 10
12 | mppt6_current | PDF | O | 0x7D1B | PV6current | S16 | A | 100
13 | mppt7_voltage | PDF | O | 0x7D1C | PV7Voltage | S16 | V | 10
14 | mppt7_current | PDF | O | 0x7D1D | PV7current | S16 | A | 100
15 | mppt8_voltage | PDF | O | 0x7D1E | PV8Voltage | S16 | V | 10
16 | mppt8_current | PDF | O | 0x7D1F | PV8current | S16 | A | 100
String 채널 H01 매칭 (8개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | 0x7D11 | PV1current | S16 | A | 100
2 | string2_current | HANDLER | O | 0x7D13 | PV2current | S16 | A | 100
3 | string3_current | HANDLER | O | 0x7D15 | PV3current | S16 | A | 100
4 | string4_current | HANDLER | O | 0x7D17 | PV4current | S16 | A | 100
5 | string5_current | HANDLER | O | 0x7D19 | PV5current | S16 | A | 100
6 | string6_current | HANDLER | O | 0x7D1B | PV6current | S16 | A | 100
7 | string7_current | HANDLER | O | 0x7D1D | PV7current | S16 | A | 100
8 | string8_current | HANDLER | O | 0x7D1F | PV8current | S16 | A | 100
MONITORING 전체 (590개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | POWER_FACTOR | 0x0000 | 03 | U16 |  | RO | power_factor
2 | Feature data sequencenumber | 0x0002 | 03 | U16 |  | RO
3 | UTE C 15-712-1(B) | 0x0003 | 03 | U16 |  | RO
4 | File version | 0x0004 | 03 | U16 |  | RO
5 | VDE 0126-1-1-BU | 0x0005 | 03 | U16 |  | RO
6 | VDE 0126-1-1-GR(A) | 0x0006 | 03 | U16 | A | RO
7 | VDE 0126-1-1-GR(B) | 0x0007 | 03 | U16 |  | RO
8 | BDEW-MV | 0x0008 | 03 | U16 |  | RO
9 | G59-England | 0x0009 | 03 | U16 |  | RO
10 | P/P value at point 1n | 0x000A | 03 | U16 | 10 | RO
11 | G83-England | 0x000B | 03 | U16 |  | RO
12 | G83_SCOTLAND | 0x000C | 03 | U16 |  | RO
13 | CEI0_21 | 0x000D | 03 | U16 |  | RO
14 | REG_0X0E | 0x000E | 03 | U16 |  | RO
15 | RD1699_661 | 0x000F | 03 | U16 |  | RO
16 | RD1699/661-MV480 | 0x0010 | 03 | U16 |  | RO
17 | Netherlands | 0x0011 | 03 | U16 |  | RO
18 | Custom (50 Hz) | 0x0015 | 03 | U16 | Hz | RO
19 | Custom (60 Hz) | 0x0016 | 03 | U16 | Hz | RO
20 | CEI0-16 | 0x0017 | 03 | U16 |  | RO
21 | BDEW-MV480 | 0x001C | 03 | U16 |  | RO
22 | Custom MV480 (50 Hz) | 0x001D | 03 | U16 | Hz | RO
23 | G59-England-MV480 | 0x001F | 03 | U16 |  | RO
24 | UTE C 15-712-1-MV480 | 0x0021 | 03 | U16 |  | RO
25 | TAI-PEA-MV480 | 0x0022 | 03 | U16 |  | RO
26 | TAI-MEA-MV480 | 0x0023 | 03 | U16 |  | RO
27 | C11/C10-MV480 | 0x0029 | 03 | U16 |  | RO
28 | 0x2B | 0x002B | 03 | U16 |  | RO
29 | NRS-097-2-1-MV480 | 0x002E | 03 | U16 |  | RO
30 | South Korea | 0x002F | 03 | U16 |  | RO
31 | IEEE 1547-MV480 | 0x0030 | 03 | U16 |  | RO
32 | ANRE-MV480 | 0x0035 | 03 | U16 |  | RO
33 | ELECTRIC_RULE_NO_21_MV480 | 0x0036 | 03 | U16 |  | RO
34 | Hawaii, USA | 0x0037 | 03 | U16 |  | RO
35 | PRC 024 Eastern-MV480_ _ | 0x0038 | 03 | U16 |  | RO
36 | PRC 024 Western-_ _MV480 | 0x0039 | 03 | U16 |  | RO
37 | PRC 024 Quebec-MV480_ _ | 0x003A | 03 | U16 |  | RO
38 | PRC 024 ERCOT-MV480_ _ | 0x003B | 03 | U16 |  | RO
39 | PO12.3-MV480 | 0x003C | 03 | U16 |  | RO
40 | EN50438 IE-MV480_ | 0x003D | 03 | U16 |  | RO
41 | EN50438 IE_ | 0x003E | 03 | U16 |  | RO
42 | IEEE 1547a-MV480 | 0x003F | 03 | U16 |  | RO
43 | 0x41 | 0x0041 | 03 | U16 |  | RO
44 | CEI0-16-MV480 | 0x0046 | 03 | U16 |  | RO
45 | PO12.3 | 0x0047 | 03 | U16 |  | RO
46 | CEI0-21-MV480 | 0x004A | 03 | U16 |  | RO
47 | IEEE 1547-MV600 | 0x004F | 03 | U16 |  | RO
48 | AC_POWER | 0x0050 | 03 | U16 |  | RO | ac_power
49 | Hawaii, USA | 0x0051 | 03 | U16 |  | RO
50 | PRC 024 Eastern-MV600_ _ | 0x0052 | 03 | U16 |  | RO
51 | PRC 024 Western-_ _MV600 | 0x0053 | 03 | U16 |  | RO
52 | PRC 024 Quebec-MV600_ _ | 0x0054 | 03 | U16 |  | RO
53 | PRC 024 ERCOT-MV600_ _ | 0x0055 | 03 | U16 |  | RO
54 | IEEE 1547a-MV600 | 0x0056 | 03 | U16 |  | RO
55 | Function code | 0x005A | 03 | U16 |  | RO
56 | NAMIBIA | 0x005B | 03 | U16 |  | RO
57 | ABNT NBR 16149 | 0x005C | 03 | U16 |  | RO
58 | ABNT NBR 16149-MV480 | 0x005D | 03 | U16 |  | RO
59 | SA RPPs-MV480_ | 0x005F | 03 | U16 |  | RO
60 | ZAMBIA | 0x0062 | 03 | U16 |  | RO
61 | ZAMBIA-MV480 | 0x0063 | 03 | U16 |  | RO
62 | KENYA ETHIOPIA_ | 0x006B | 03 | U16 |  | RO
63 | G59-England-MV800 | 0x006D | 03 | U16 |  | RO
64 | NIGERIA | 0x006E | 03 | U16 |  | RO
65 | NIGERIA-MV480 | 0x006F | 03 | U16 |  | RO
66 | L1_VOLTAGE | 0x0070 | 03 | U16 |  | RO | r_voltage
67 | L2_VOLTAGE | 0x0071 | 03 | U16 |  | RO | s_voltage
68 | L3_VOLTAGE | 0x0072 | 03 | U16 |  | RO | t_voltage
69 | L1_CURRENT | 0x0073 | 03 | U16 |  | RO | r_current
70 | L2_CURRENT | 0x0074 | 03 | U16 |  | RO | s_current
71 | L3_CURRENT | 0x0075 | 03 | U16 |  | RO | t_current
72 | Custom MV600-50 Hz | 0x0078 | 03 | U16 | Hz | RO
73 | BDEW-MV800 | 0x007C | 03 | U16 |  | RO
74 | ABNT NBR 16149-MV800 | 0x007D | 03 | U16 |  | RO
75 | UTE C 15-712-1-MV800 | 0x007E | 03 | U16 |  | RO
76 | No permission | 0x0080 | 03 | U16 |  | RO
77 | TAI-PEA-MV800 | 0x0082 | 03 | U16 |  | RO
78 | 0x83 | 0x0083 | 03 | U16 |  | RO
79 | NRS-097-2-1-MV800 | 0x0085 | 03 | U16 |  | RO
80 | SA RPPs-MV800_ | 0x0086 | 03 | U16 |  | RO
81 | 0x87 | 0x0087 | 03 | U16 |  | RO
82 | Description aboutthe first device | 0x0088 | 03 | ASCII |  | RO
83 | DUBAI_MV800 | 0x008A | 03 | U16 |  | RO
84 | EN50438 IE-MV800_ | 0x008C | 03 | U16 |  | RO
85 | NORTHERN_IRELAND_MV800 | 0x008E | 03 | U16 |  | RO
86 | CEI0-21-MV800 | 0x008F | 03 | U16 |  | RO
87 | IEC 61727-MV800-60Hz | 0x0090 | 03 | U16 |  | RO
88 | NAMIBIA MV480_ | 0x0091 | 03 | U16 |  | RO
89 | Pakistan-MV800 | 0x0094 | 03 | U16 |  | RO
90 | BRASIL-ANEEL-MV800 | 0x0095 | 03 | U16 |  | RO
91 | CEI0-16-MV800 | 0x0097 | 03 | U16 |  | RO
92 | ZAMBIA-MV800 | 0x0098 | 03 | U16 |  | RO
93 | KENYA ETHIOPIA-_MV800 | 0x0099 | 03 | U16 |  | RO
94 | NAMIBIA MV800_ | 0x009A | 03 | U16 |  | RO
95 | CAMEROON_MV800 | 0x009B | 03 | U16 |  | RO
96 | NIGERIA-MV800 | 0x009C | 03 | U16 |  | RO
97 | ABUDHABI-MV800 | 0x009D | 03 | U16 |  | RO
98 | LEBANON | 0x009E | 03 | U16 |  | RO
99 | LEBANON-MV480 | 0x009F | 03 | U16 |  | RO
100 | LEBANON-MV800 | 0x00A0 | 03 | U16 |  | RO
101 | TUNISIA | 0x00A6 | 03 | U16 |  | RO
102 | TUNISIA-MV480 | 0x00A7 | 03 | U16 |  | RO
103 | TUNISIA-MV800 | 0x00A8 | 03 | U16 |  | RO
104 | JAMAICA-MV800 | 0x00A9 | 03 | U16 |  | RO
105 | Ghana-MV480 | 0x00AF | 03 | U16 |  | RO
106 | VDE_AR_N4120_HV | 0x00B4 | 03 | U16 |  | RO
107 | VDE_AR_N4120_HV480 | 0x00B5 | 03 | U16 |  | RO
108 | VDE_AR_N4120_HV800 | 0x00B6 | 03 | U16 |  | RO
109 | IEEE 1547-MV800 | 0x00B7 | 03 | U16 |  | RO
110 | Nicaragua-MV800 | 0x00B8 | 03 | U16 |  | RO
111 | IEEE 1547a-MV800 | 0x00B9 | 03 | U16 |  | RO
112 | ELECTRIC_RULE_NO_21_MV800 | 0x00BA | 03 | U16 |  | RO
113 | Hawaii, USA | 0x00BB | 03 | U16 |  | RO
114 | PRC 024 Eastern-MV800_ _ | 0x00BC | 03 | U16 |  | RO
115 | PRC 024 Western-_ _MV800 | 0x00BD | 03 | U16 |  | RO
116 | PRC 024 Quebec-MV800_ _ | 0x00BE | 03 | U16 |  | RO
117 | PRC 024 ERCOT-MV800_ _ | 0x00BF | 03 | U16 |  | RO
118 | Custom-MV800-50Hz | 0x00C0 | 03 | U16 |  | RO
119 | RD1699/661-MV800 | 0x00C1 | 03 | U16 |  | RO
120 | PO12.3-MV800 | 0x00C2 | 03 | U16 |  | RO
121 | Dedicated | 0x00C6 | 03 | U16 |  | RO
122 | Ghana-MV800 | 0x00CA | 03 | U16 |  | RO
123 | TAIPOWER | 0x00CB | 03 | U16 |  | RO
124 | TAIPOWER-MV480 | 0x00CC | 03 | U16 |  | RO
125 | TAIPOWER-MV800 | 0x00CD | 03 | U16 |  | RO
126 | IEEE 1547-LV208 | 0x00CE | 03 | U16 |  | RO
127 | IEEE 1547-LV240 | 0x00CF | 03 | U16 |  | RO
128 | IEEE 1547a-LV208 | 0x00D0 | 03 | U16 |  | RO
129 | IEEE 1547a-LV240 | 0x00D1 | 03 | U16 |  | RO
130 | ELECTRIC_RULE_NO_21_LV208 | 0x00D2 | 03 | U16 |  | RO
131 | ELECTRIC_RULE_NO_21_LV240 | 0x00D3 | 03 | U16 |  | RO
132 | HECO-O+M+H-LV208 | 0x00D4 | 03 | U16 |  | RO
133 | HECO-O+M+H-LV240 | 0x00D5 | 03 | U16 |  | RO
134 | PRC 024 Eastern-LV208_ _ | 0x00D6 | 03 | U16 |  | RO
135 | PRC 024 Eastern-LV240_ _ | 0x00D7 | 03 | U16 |  | RO
136 | PRC 024 Western-LV208_ _ | 0x00D8 | 03 | U16 |  | RO
137 | PRC 024 Western-LV240_ _ | 0x00D9 | 03 | U16 |  | RO
138 | PRC 024 ERCOT-LV208_ _ | 0x00DA | 03 | U16 |  | RO
139 | PRC 024 ERCOT-LV240_ _ | 0x00DB | 03 | U16 |  | RO
140 | PRC 024 Quebec-LV208_ _ | 0x00DC | 03 | U16 |  | RO
141 | PRC 024 Quebec-LV240_ _ | 0x00DD | 03 | U16 |  | RO
142 | Bangladesh | 0x00E5 | 03 | U16 |  | RO
143 | Bangladesh-MV480 | 0x00E6 | 03 | U16 |  | RO
144 | Bangladesh-MV800 | 0x00E7 | 03 | U16 |  | RO
145 | Bahrain | 0x00EA | 03 | U16 |  | RO
146 | Bahrain-MV480 | 0x00EB | 03 | U16 |  | RO
147 | Bahrain-MV800 | 0x00EC | 03 | U16 |  | RO
148 | KAZAKHSTAN-MV800 | 0x00F2 | 03 | U16 |  | RO
149 | Mauritius | 0x00F3 | 03 | U16 |  | RO
150 | TAI-MEA-MV800 | 0x00F8 | 03 | U16 |  | RO
151 | Pakistan | 0x00F9 | 03 | U16 |  | RO
152 | Pakistan-MV480 | 0x00FA | 03 | U16 |  | RO
153 | HECO-L+M-LV208 | 0x00FC | 03 | U16 |  | RO
154 | HECO-L+M-LV240 | 0x00FD | 03 | U16 |  | RO
155 | C10/11-MV800 | 0x00FE | 03 | U16 |  | RO
156 | Description aboutthe 120th device | 0x00FF | 03 | U16 |  | RO
157 | G99-TYPEA-LV | 0x0102 | 03 | U16 |  | RO
158 | G99-TYPEB-LV | 0x0103 | 03 | U16 |  | RO
159 | G99-TYPEB-HV | 0x0104 | 03 | U16 |  | RO
160 | G99-TYPEB-HV-MV480 | 0x0105 | 03 | U16 |  | RO
161 | G99-TYPEB-HV-MV800 | 0x0106 | 03 | U16 |  | RO
162 | G99-TYPEC-HV-MV800 | 0x0107 | 03 | U16 |  | RO
163 | G99-TYPED-MV800 | 0x0108 | 03 | U16 |  | RO
164 | G99-TYPEA-HV | 0x0109 | 03 | U16 |  | RO
165 | CEA-MV800 | 0x010A | 03 | U16 |  | RO
166 | VDE_AR_N4110 | 0x010C | 03 | U16 |  | RO
167 | VDE_AR_N4110_MV480 | 0x010D | 03 | U16 |  | RO
168 | VDE_AR_N4110_MV800 | 0x010E | 03 | U16 |  | RO
169 | Panama-MV800 | 0x010F | 03 | U16 |  | RO
170 | North Macedonia-MV800 | 0x0110 | 03 | U16 |  | RO
171 | NTS-MV480 | 0x0112 | 03 | U16 |  | RO
172 | NTS-MV800 | 0x0113 | 03 | U16 |  | RO
173 | String Reverse Connection | 0x07DB | 03 | STRINGING |  | RO
174 | String Current Backfeed | 0x07DC | 03 | STRINGING |  | RO
175 | Abnormal String Power | 0x07DD | 03 | STRINGING |  | RO
176 | High input string voltage toground. | 0x07DE | 03 | STRINGING |  | RO
177 | PV String Loss | 0x07DF | 03 | STRINGING |  | RO
178 | AFCI Self-Check Fail.[1] | 0x07E5 | 03 | U16 |  | RO
179 | Phase Wire Short-Circuitedto PE | 0x07EF | 03 | U16 |  | RO
180 | Grid Loss | 0x07F0 | 03 | U16 |  | RO
181 | Grid Undervoltage | 0x07F1 | 03 | U16 |  | RO
182 | Grid Overvoltage | 0x07F2 | 03 | U16 |  | RO | frequency
183 | Grid Volt. Imbalance | 0x07F3 | 03 | U16 |  | RO
184 | Grid Overfrequency | 0x07F4 | 03 | U16 |  | RO
185 | Grid Underfrequency | 0x07F5 | 03 | U16 |  | RO
186 | Unstable Grid Frequency | 0x07F6 | 03 | U16 |  | RO
187 | Output Overcurrent | 0x07F7 | 03 | U16 |  | RO
188 | Output DC ComponentOverhigh | 0x07F8 | 03 | U16 |  | RO
189 | Abnormal Residual Current | 0x0803 | 03 | U16 |  | RO
190 | ABNORMAL_GROUNDING | 0x080D | 03 | U16 |  | RO
191 | Overtemperature | 0x080F | 03 | U16 |  | RO
192 | Upgrade Failed or VersionMismatch | 0x0811 | 03 | U16 |  | RO
193 | License Expired | 0x0812 | 03 | U16 |  | RO
194 | BATTERY_ABNORMAL | 0x0814 | 03 | U16 |  | RO
195 | Battery ReverseConnection[7] | 0x0815 | 03 | U16 |  | RO
196 | Active Islanding | 0x0816 | 03 | U16 |  | RO
197 | Passive Islanding | 0x0817 | 03 | U16 |  | RO
198 | Transient AC Overvoltage | 0x0818 | 03 | U16 |  | RO
199 | Peripheral port shortcircuit[3] | 0x081B | 03 | U16 |  | RO
200 | ABNORMAL_PV_MODULECONFIGURATION | 0x0820 | 03 | U16 |  | RO
201 | ON_GRID_OFF_GRID_CONTROLLERABNORMAL4 | 0x0822 | 03 | U16 |  | RO
202 | BUILT_IN_PID_OPERATIONABNORMAL6 | 0x0825 | 03 | U16 |  | RO
203 | EXTERNAL_FAN_ABNORMAL | 0x0826 | 03 | U16 |  | RO
204 | INTERNAL_FAN_ABNORMAL | 0x0827 | 03 | U16 |  | RO
205 | DC_PROTECTION_UNIT_ABNORMAL8 | 0x0828 | 03 | U16 |  | RO
206 | NumberofPVstrings | 0x7577 |  | U16 | 1 | RO
207 | NUMBEROF_MPPTS | 0x7578 |  | U16 | 1 | RO
208 | Maximumactivepower(Pmax) | 0x757B |  | U32 | kW 1000 | RO
209 | Maximumapparent(Smax) | 0x757D |  | U32 | kVA 1000 | RO
210 | Real-timemaximumreactivepower(Qmax,fedtothepowergrid) | 0x757F |  | S32 | 1000 | RO
211 | Real-timemaximumreactivepower (-Qmax,absorbedfromthepowergrid) | 0x7581 |  | S32 | 1000 | RO
212 | Maximumactivepower(Pmax r_eal) | 0x7583 |  | U32 | kW 1000 | RO
213 | Maximumapparentcapability(Smax r_eal) | 0x7585 |  | U32 | kVA 1000 | RO
214 | Productsalesarea | 0x7599 |  | STRING |  | RO
215 | ProductsoftwareID | 0x759B |  | U16 |  | RO
216 | UniqueID ofthesoftware. | 0x759E |  | U16 |  | RO
217 | Numberofupgradepackages | 0x759F |  | U16 | 1 | RO
218 | Informationaboutsubpackage 1 | 0x75A0 |  | U32 |  | RO
219 | Subpackage 2information | 0x75A2 |  | U32 |  | RO
220 | Informationaboutsubpackage 3 | 0x75A4 |  | U32 |  | RO
221 | Subpackage 4information | 0x75A6 |  | U32 |  | RO
222 | Subpackage 5information | 0x75A8 |  | U32 |  | RO
223 | Informationaboutsubpackage 6 | 0x75AA |  | U32 |  | RO
224 | Subpackage 7information | 0x75AC |  | U32 |  | RO
225 | Subpackage 8information | 0x75AE |  | U32 |  | RO
226 | Subpackage 9information | 0x75B0 |  | U32 |  | RO
227 | Informationaboutsubpackage10 | 0x75B2 |  | U32 |  | RO
228 | SubdeviceSupportID | 0x75FF |  | U32 |  | RO
229 | Subdevicepresenceflag. | 0x7601 |  | U32 |  | RO
230 | NumberofuniquesouthboundsoftwareIDs | 0x7724 |  | U16 | 1 | RO
231 | UniqueID 1ofthesouthboundsoftware. | 0x7725 |  | U16 |  | RO
232 | UniqueID 2ofthesouthboundsoftware | 0x7726 |  | U16 |  | RO
233 | Numberofupgradepackagesforsouthbounddevice 1 | 0x772A |  | U16 | 1 | RO
234 | Informationaboutsubpackage 1ofsouthbounddevice 1 | 0x772B |  | U32 |  | RO
235 | Informationaboutsubpackage 2ofsouthbounddevice 1 | 0x772D |  | U32 |  | RO
236 | Informationaboutsubpackage 3ofsouthbounddevice 1 | 0x772F |  | U32 |  | RO
237 | Numberofupgradepackagesforsouthbounddevice 2 | 0x7735 |  | U16 | 1 | RO
238 | Informationaboutsubpackage 1ofsouthbounddevice 2 | 0x7736 |  | U32 |  | RO
239 | Informationaboutsubpackage 2ofsouthbounddevice 2 | 0x7738 |  | U32 |  | RO
240 | Informationaboutsubpackage 3ofsouthbounddevice 2 | 0x773A |  | U32 |  | RO
241 | Informationaboutsubpackage 4ofsouthbounddevice 2 | 0x773C |  | U32 |  | RO
242 | Ofefringname ofsouthbounddevice 1 | 0x7761 |  | STRING |  | RO
243 | Offeringname ofsouthbounddevice 2 | 0x7770 |  | STRING |  | RO
244 | Ofefringname ofsouthbounddevice 3. | 0x777F |  | STRING |  | RO
245 | Hardwareversion | 0x7918 |  | STRING | 1 | RO
246 | MainDSPversion | 0x7940 |  | STRING |  | RO
247 | CPLDversionnumber | 0x795E |  | STRING |  | RO
248 | AFCIversionnumber | 0x796D |  | STRING |  | RO
249 | DC-MBUSversionnumber | 0x798B |  | STRING |  | RO
250 | Registrationcode | 0x79E0 |  | STRING | 1 | RO
251 | [Remotecommunication]Single-noderemotecommunication | 0x7D00 |  | U16 |  | RO
252 | PV1voltage | 0x7D10 |  | S16 | V 10 | RO | mppt1_voltage
253 | PV1current | 0x7D11 |  | S16 | A 100 | RO | mppt1_current
254 | PV2Voltage | 0x7D12 |  | S16 | V 10 | RO | mppt2_voltage
255 | PV2current | 0x7D13 |  | S16 | A 100 | RO | mppt2_current
256 | PV3Voltage | 0x7D14 |  | S16 | V 10 | RO | mppt3_voltage
257 | PV3current | 0x7D15 |  | S16 | A 100 | RO | mppt3_current
258 | PV4Voltage | 0x7D16 |  | S16 | V 10 | RO | mppt4_voltage
259 | PV4current | 0x7D17 |  | S16 | A 100 | RO | mppt4_current
260 | PV5voltage | 0x7D18 |  | S16 | V 10 | RO | mppt5_voltage
261 | PV5current | 0x7D19 |  | S16 | A 100 | RO | mppt5_current
262 | PV6voltage | 0x7D1A |  | S16 | V 10 | RO | mppt6_voltage
263 | PV6current | 0x7D1B |  | S16 | A 100 | RO | mppt6_current
264 | PV7Voltage | 0x7D1C |  | S16 | V 10 | RO | mppt7_voltage
265 | PV7current | 0x7D1D |  | S16 | A 100 | RO | mppt7_current
266 | PV8Voltage | 0x7D1E |  | S16 | V 10 | RO | mppt8_voltage
267 | PV8current | 0x7D1F |  | S16 | A 100 | RO | mppt8_current
268 | PV_POWER | 0x7D40 |  | S32 | kW 1000 | RO | pv_power
269 | PowergridlineAandBvoltage | 0x7D42 |  | U16 | V 10 | RO
270 | PowergridB/Clinevoltage | 0x7D43 |  | U16 | V 10 | RO
271 | PowergridCAlinevoltage | 0x7D44 |  | U16 | V 10 | RO
272 | Powergridphase Avoltage | 0x7D45 |  | U16 | V 10 | RO | r_voltage
273 | Powergridphase Bvoltage | 0x7D46 |  | U16 | V 10 | RO | s_voltage
274 | Powergridphase Cvoltage | 0x7D47 |  | U16 | V 10 | RO | t_voltage
275 | Powergridphase Acurrent | 0x7D48 |  | S32 | A 1000 | RO | r_current
276 | Powergridphase Bcurrent | 0x7D4A |  | S32 | A 1000 | RO | s_current
277 | Powergridphase Ccurrent | 0x7D4C |  | S32 | A 1000 | RO | t_current
278 | Peakactivepower ofthecurrentday | 0x7D4E |  | S32 | kW 1000 | RO
279 | AC_POWER | 0x7D50 |  | S32 | kW 1000 | RO | ac_power
280 | REACTIVE_POWER | 0x7D52 |  | S32 | 1000 | RO | reactive_power
281 | Powerfactor | 0x7D54 |  | S16 | 1000 | RO | power_factor
282 | FREQUENCY | 0x7D55 |  | U16 | Hz 100 | RO | frequency
283 | INVERTER_EFFICIENCY | 0x7D56 |  | U16 | 100 | RO
284 | Start-uptime | 0x7D5B |  | U16 | 1 | RO
285 | Shutdowntime | 0x7D5D |  | U16 | 1 | RO
286 | Activepower[fast] | 0x7D5F |  | S32 | kW 1000 | RO
287 | Accumulatedpowergeneration | 0x7D6A |  | U32 | kWh 100 | RO | cumulative_energy
288 | TOTAL_DC_INPUT_POWER | 0x7D6C |  | U32 | kWh 100 | RO | pv_power
289 | Statisticaltimeofthecurrentenergyyield. | 0x7D6E |  | U16 | 1 | RO
290 | CurrentHourElectricity | 0x7D70 |  | U32 | kWh 100 | RO
291 | Current-daypowergeneration | 0x7D72 |  | U32 | kWh 100 | RO
292 | Electricitygenerated inthecurrentmonth | 0x7D74 |  | U32 | kWh 100 | RO
293 | Electricitygenerated inthecurrentyear | 0x7D76 |  | U32 | kWh 100 | RO
294 | LastHourPowerStatisticsTime | 0x7D9C |  | U16 | 1 | RO
295 | Electricitygenerated intheprevioushour | 0x7D9E |  | U32 | kWh 100 | RO
296 | Electricitystatisticstimeofthepreviousday | 0x7DA0 |  | U16 | 1 | RO
297 | Electricitygenerated inthepreviousday | 0x7DA2 |  | U32 | kWh 100 | RO
298 | Statisticaltimeofthepreviousmonth. | 0x7DA4 |  | U16 | 1 | RO
299 | Electricitygenerated inthepreviousmonth | 0x7DA6 |  | U32 | kWh 100 | RO
300 | Electricitystatisticstimeofthepreviousyear | 0x7DA8 |  | U16 | 1 | RO
301 | Electricitygenerated inthepreviousyear | 0x7DAA |  | U32 | kWh 100 | RO
302 | MaximumPVvoltage | 0x7DB1 |  | S16 | V 10 | RO
303 | MinimumPVvoltage | 0x7DB2 |  | S16 | V 10 | RO
304 | AveragePVnegative-to-groundvoltage | 0x7DB3 |  | S16 | V 10 | RO
305 | MaximumPVpositive-to-groundvoltage | 0x7DB4 |  | S16 | V 10 | RO
306 | MinimumPVnegative-to-groundvoltage | 0x7DB5 |  | S16 | V 10 | RO
307 | Inverter-to-PEwithstandvoltage | 0x7DB6 |  | U16 | V 1 | RO
308 | ISOfeatureinformation | 0x7DB7 |  | U16 | 1 | RO
309 | PVnegative-to-groundvoltage | 0x7DBF |  | S16 | V 10 | RO
310 | Directionofthebuilt-inPIDcompensation | 0x7DC0 |  | U16 |  | RO
311 | TotalDCenergyyieldofMPPT1 | 0x7DD4 |  | U32 | kWh 100 | RO
312 | TotalDCenergyyieldofMPPT2 | 0x7DD6 |  | U32 | kWh 100 | RO
313 | CUMULATIVE_ENERGY | 0x7DDA |  | U32 | kWh 100 | RO | cumulative_energy
314 | Tiltangle 1sampling | 0x84D2 |  | S16 | 100 | RO
315 | Azimuth1sampling | 0x84D3 |  | S16 | 100 | RO
316 | Tiltangle 2sampling | 0x84D4 |  | S16 | 100 | RO
317 | Azimuth2sampling | 0x84D5 |  | S16 | 100 | RO
318 | Tiltangle 3sampling | 0x84D6 |  | S16 | 100 | RO
319 | Azimuth3sampling | 0x84D7 |  | S16 | 100 | RO
320 | Tiltangle 4sampling | 0x84D8 |  | S16 | 100 | RO
321 | Azimuth4sampling | 0x84D9 |  | S16 | 100 | RO
322 | Tiltangle 5sampling | 0x84DA |  | S16 | 100 | RO
323 | Azimuth5sampling | 0x84DB |  | S16 | 100 | RO
324 | Tiltangle 6sampling | 0x84DC |  | S16 | 100 | RO
325 | Azimuth6sampling | 0x84DD |  | S16 | 100 | RO
326 | Tiltangle 7sampling | 0x84DE |  | S16 | 100 | RO
327 | Azimuth7sampling | 0x84DF |  | S16 | 100 | RO
328 | Tiltangle 8sampling | 0x84E0 |  | S16 | 100 | RO
329 | Azimuth8sampling | 0x84E1 |  | S16 | 100 | RO
330 | Tiltangle 9sampling | 0x84E2 |  | S16 | 100 | RO
331 | Azimuth9sampling | 0x84E3 |  | S16 | 100 | RO
332 | Tiltangle 10sampling | 0x84E4 |  | S16 | 100 | RO
333 | Azimuth10sampling | 0x84E5 |  | S16 | 100 | RO
334 | Tiltangle 11sampling | 0x84E6 |  | S16 | 100 | RO
335 | Azimuth11sampling | 0x84E7 |  | S16 | 100 | RO
336 | Tiltangle 12sampling | 0x84E8 |  | S16 | 100 | RO
337 | Azimuth12sampling | 0x84E9 |  | S16 | 100 | RO
338 | Tiltangle 13sampling | 0x84EA |  | S16 | 100 | RO
339 | Bearing13sampling | 0x84EB |  | S16 | 100 | RO
340 | Tiltangle 14sampling | 0x84EC |  | S16 | 100 | RO
341 | Azimuth14sampling | 0x84ED |  | S16 | 100 | RO
342 | Tiltangle 15sampling | 0x84EE |  | S16 | 100 | RO
343 | Bearingangle 15sampling | 0x84EF |  | S16 | 100 | RO
344 | Tiltangle 16sampling | 0x84F0 |  | S16 | 100 | RO
345 | Bearing16sampling | 0x84F1 |  | S16 | 100 | RO
346 | Trackingsystemcontroller | 0x84F2 |  | U16 |  | RO
347 | SupportSystemType | 0x84F3 |  | U16 |  | RO
348 | OPERATINGMODE | 0x84F4 |  | U16 |  | RO
349 | Totalnumberofstents | 0x84F5 |  | U16 | 1 | RO
350 | WORKINGMODEMASK | 0x84F8 |  | U32 | 1 | RO
351 | INTERNAL_TEMPERATURE1 | 0x88CD |  | S16 | 10 | RO | inner_temp
352 | INTERNAL_TEMPERATURE2 | 0x88CE |  | S16 | 10 | RO | inner_temp
353 | INTERNAL_TEMPERATURE3 | 0x88CF |  | S16 | 10 | RO | inner_temp
354 | INTERNAL_TEMPERATURE4 | 0x88D0 |  | S16 | 10 | RO | inner_temp
355 | INTERNAL_TEMPERATURE5 | 0x88D1 |  | S16 | 10 | RO | inner_temp
356 | INTERNAL_TEMPERATURE6 | 0x88D2 |  | S16 | 10 | RO | inner_temp
357 | Phase ADCcomponentDCI | 0x88DE |  | S16 | A 1000 | RO
358 | Phase BDCcomponentDCI | 0x88DF |  | S16 | A 1000 | RO
359 | Phase CDCcomponentDCI | 0x88E0 |  | S16 | A 1000 | RO
360 | LeakagecurrentRCD | 0x88E1 |  | S16 | 1 | RO
361 | I-Vscanningcapability | 0x8917 |  | U16 |  | RO
362 | [ManagementSystem]NMSIPaddress | 0x891E |  | U32 | 1 | RO
363 | [STA]WirelessRoutingAccessSignalStrength | 0x8920 |  | U16 |  | RO
364 | [NTP]NTPLastSynchronizationTime | 0x8929 |  | U32 | 1 | RO
365 | DEFERREDACTIVATIONSTATE | 0x892B |  | U16 |  | RO
366 | [4G]Monthlyusedtraffic | 0x892C |  | U32 | 100 | RO
367 | [4G]MonthlyRemainingTraffic | 0x892E |  | U32 | 100 | RO
368 | [4G]Averagedailytrafficusage | 0x8930 |  | U32 | 100 | RO
369 | [STA]Routerconnectiontime | 0x8934 |  | U16 | 1 | RO
370 | [Smart I-V-V-Diagnosis]AuthorizationFunction | 0x8940 |  | U32 | V 1 | RO
371 | [Smart I-V-V-Diagnosis]Licenseexpirationdate | 0x8943 |  | U16 | V 1 | RO
372 | Licenseloadingtime | 0x8945 |  | U16 | 1 | RO
373 | LicenseDeregistrationTime | 0x8947 |  | U16 | 1 | RO
374 | Invalidationcode. | 0x8953 |  | STRING | 1 | RO
375 | AuthorizationFeatureSignature | 0x8993 |  | U16 |  | RO
376 | [StringMonitoring]LicenseExpirationTime | 0x8996 |  | U16 | 1 | RO
377 | [4G]IPaddress | 0x89B2 |  | U32 | 1 | RO
378 | [4G]SubnetMask | 0x89B4 |  | U32 | 1 | RO
379 | [4G]IMEI | 0x89B6 |  | STRING | 1 | RO
380 | [4G]signalstrength | 0x89C0 |  | U16 | 1 | RO
381 | [4G]PINnumberinputtimes | 0x89C1 |  | U16 | 1 | RO
382 | Gridvoltage(phase Avoltage) | 0x90ED |  | S32 | V 10 | RO
383 | Phase Bvoltage | 0x90EF |  | S32 | V 10 | RO
384 | Phase Cvoltage | 0x90F1 |  | S32 | V 10 | RO
385 | Gridcurrent(phase Acurrent) | 0x90F3 |  | S32 | A 100 | RO
386 | Phase Bcurrent | 0x90F5 |  | S32 | A 100 | RO
387 | Phase Ccurrent | 0x90F7 |  | S32 | A 100 | RO
388 | Activepower | 0x90F9 |  | S32 | W 1 | RO
389 | reactivepower | 0x90FB |  | S32 | 1 | RO
390 | Powerfactor | 0x90FD |  | S16 | 1000 | RO
391 | FREQUENCY | 0x90FE |  | S16 | Hz 100 | RO | frequency
392 | Positiveactivepower | 0x90FF |  | S32 | kWh 100 | RO
393 | Reverseactivepower | 0x9101 |  | S32 | kWh 100 | RO
394 | Accumulatedreactivepower | 0x9103 |  | S32 | 100 | RO
395 | MeterType | 0x9105 |  | U16 |  | RO
396 | A-Blinevoltage | 0x9106 |  | S32 | V 10 | RO
397 | BClinevoltage | 0x9108 |  | S32 | V 10 | RO
398 | CAlinevoltage | 0x910A |  | S32 | V 10 | RO
399 | Phase Aactivepower | 0x910C |  | S32 | W 1 | RO
400 | Phase Bactivepower | 0x910E |  | S32 | W 1 | RO
401 | Phase Cactivepower | 0x9110 |  | S32 | W 1 | RO
402 | Totalnumberofoptimizers | 0x9150 |  | U16 | 1 | RO
403 | Numberofonlineoptimizers | 0x9151 |  | U16 | 1 | RO
404 | Featuredatasequencenumber | 0x9152 |  | U16 | 1 | RO
405 | PhysicalLocationLocatingProgress | 0x9153 |  | U16 |  | RO
406 | Logexportprogress | 0x9154 |  | U16 |  | RO
407 | Real-timedataqueryprogress | 0x9155 |  | U16 |  | RO
408 | NumberofSearchedOptimizers | 0x9157 |  | U16 | 1 | RO
409 | LayoutFileStorageProgress | 0x9159 |  | U16 | 1 | RO
410 | NumberofNetworkedNetworks | 0x9183 |  | U16 |  | RO
411 | Numberofneighboringnetworks | 0x9184 |  | U16 |  | RO
412 | Type | 0x9222 |  | U16 |  | RO
413 | Maximumnumberofconnecteddevices | 0x9235 |  | U16 | 1 | RO
414 | Carriers | 0x9240 |  | STRING | 1 | RO
415 | Totalratedcapacityofgrid-tiedinverters | 0x925E |  | U32 | kW 1000 | RO
416 | Conversionfactor | 0x9260 |  | U32 | 1000 | RO
417 | CurrentPercentage | 0x9262 |  | U16 | 10 | RO
418 | [Scheduleserver]Latestconnectiontime | 0x9265 |  | U32 |  | RO
419 | Numberofconnecteddevices | 0x9276 |  | U16 |  | RO
420 | Silenceflag | 0x9278 |  | U16 |  | RO
421 | Q_UCHARACTERISTICCURVEMODE | 0x9C65 |  | U16 |  | RW
422 | Q-USchedulingTriggerPowerPercentage | 0x9C66 |  | S16 | 1 | RW
423 | Powerfactor | 0x9CBA |  | S16 | 1000 | RW
424 | Reactivepowercompensation(Q/S)[lowprecision] | 0x9CBB |  | S16 | 1000 | RW
425 | Reactivepoweradjustmenttime | 0x9CBC |  | U16 | 1 | RW
426 | Activepowerpercentagederating(lowprecision) | 0x9CBD |  | S16 | 10 | RW
427 | Nightreactivepowercompensation(Q/S) | 0x9CC0 |  | S16 | 1000 | RW
428 | Fixedvalue ofreactivepower atnight | 0x9CC1 |  | S32 | 1000 | RW
429 | PF-Ucharacteristiccurve | 0x9CEF |  | U16 |  | RW
430 | [Characteristiccurve]Reactivepoweradjustmenttime | 0x9D04 |  | U16 | 1 | RW
431 | Q-USchedulingExitPowerPercentage | 0x9D06 |  | S16 | 1 | RW
432 | Activepowerpercentagecontrol[lowprecision] | 0x9D07 |  | S16 | 10 | RW
433 | Quickpower-onandpower-off | 0x9D0A |  | U16 |  | WO
434 | Q-Ucharacteristiccurveminimum PFlimit | 0x9DB7 |  | U16 | 1000 | RW
435 | Powergridstandardcode | 0xA410 |  | U16 | 1 | RW
436 | OUTPUTMODE | 0xA411 |  | U16 |  | RW
437 | Voltagelevel | 0xA412 |  | U16 | V 1 | RW
438 | FrequencyClass | 0xA413 |  | U16 | Hz 1 | RW
439 | Remotepowerscheduling | 0xA41E |  | U16 |  | RW
440 | reactivepowergradient | 0xA41F |  | U32 | 1000 | RW
441 | Activepowerchangegradient | 0xA421 |  | U32 | 1000 | RW
442 | Maximumactivepower | 0xA427 |  | U32 | kW 1000 | RW
443 | Activepowerreference | 0xA42B |  | U32 | kW 1000 | RW
444 | Plantactivepowergradient | 0xA42D |  | U16 | 1 | RW
445 | FREQUENCYMODULATIONCONTROLRESPONSEDEADBAND | 0xA43B |  | U16 | Hz 1000 | RW
446 | OF_FGRIDSWITCHOVERMODE | 0xA43C |  | U16 |  | RW
447 | OFF_GRIDMODE | 0xA43D |  | U16 |  | RW
448 | PQMODE | 0xA43E |  | U16 |  | RW
449 | STRINGCONNECTIONMODE | 0xA441 |  | U16 |  | RW
450 | FREQUENCYMODULATIONCONTROLPOWERCHANGEGRADIENT | 0xA443 |  | U16 | 1 | RW
451 | Frequencymodulationcontrolpowerchangelimitingamplitude | 0xA444 |  | U16 | 10 | RW
452 | PredictedMPPTpower | 0xA448 |  | U32 | kW 1000 | RO
453 | Powerlimit0%shutdown | 0xA44E | 03 | U16 | % | RW
454 | Automaticpower-offwhencommunication isdisconnected | 0xA44F | 03 | U16 |  | RW
455 | Automaticpower-onaftercommunicationrecovery | 0xA450 | 03 | U16 |  | RW
456 | POWER_QUALITY_OPTIMIZATION_MODE | 0xA451 | 03 | U16 |  | RW
457 | Nightreactivepower | 0xA453 | 03 | U16 |  | RW
458 | ABNORMALGROUNDINGSHUTDOWN | 0xA454 | 03 | U16 |  | RW
459 | Nightreactivepowerparameterstakeeffect | 0xA456 | 03 | U16 |  | RW
460 | FAILUREPROTECTIONACTIVEPOWERMODE | 0xA45C | 03 | U16 |  | RW
461 | ActivePowerLimitforFailureProtection[kW][LowPrecision] | 0xA45D | 03 | U32 | kW 10 | RW
462 | FAILUREPROTECTIONREACTIVEPOWERMODE | 0xA45F | 03 | U16 |  | RW
463 | FREQUENCYRATEPROTECTION | 0xA460 | 03 | U16 |  | RW
464 | FREQUENCYCHANGERATEPROTECTIONPOINT | 0xA461 | 03 | U16 | Hz 10 | RW
465 | FREQUENCYCHANGERATEPROTECTIONTIME | 0xA462 | 03 | U16 | 10 | RW
466 | Reactivepowerlimitforfailureprotection[Q/S][lowprecision] | 0xA463 | 03 | S16 | 1000 | RW
467 | Power-onvoltageupperlimitforgridconnection | 0xA464 | 03 | U16 | V 10 | RW
468 | Power-onvoltagelowerlimitforgridconnection | 0xA465 | 03 | U16 | V 10 | RW
469 | Power-onfrequencyupperlimitforgridconnection | 0xA466 | 03 | U16 | Hz 100 | RW
470 | Power-onfrequencylowerlimitforgridconnection | 0xA467 | 03 | U16 | Hz 100 | RW
471 | Powergridreconnectionvoltageupperlimit | 0xA468 | 03 | U16 | V 10 | RW
472 | PowerGridReconnectionVoltageLowerThreshold | 0xA469 | 03 | U16 | V 10 | RW
473 | Powergridreconnectionfrequencyupperlimit | 0xA46A | 03 | U16 | Hz 100 | RW
474 | Powergridreconnectionfrequencylowerlimit | 0xA46B | 03 | U16 | Hz 100 | RW
475 | AutomaticPowerGridReconnectionTime | 0xA46C | 03 | U16 | 1 | RW
476 | Voltageunbalanceprotectionthreshold | 0xA472 | 03 | U16 | 10 | RW
477 | Cos?-P/Pntriggervoltage | 0xA475 | 03 | U16 | 1 | RW
478 | Cos?-P/Pnexitvoltage | 0xA476 | 03 | U16 | 1 | RW
479 | Timefordeterminingshort-termpowergridinterruption | 0xA479 | 03 | U32 | 1 | RW
480 | Gridvoltagejumptriggerthreshold | 0xA47F | 03 | U16 | 10 | RW
481 | Short-termpowergridinterruptionandquickstartup | 0xA484 | 03 | U16 |  | RW
482 | PowergridvoltageprotectionshieldduringVRT | 0xA489 | 03 | U16 |  | RW
483 | VRTactivecurrentlimitingpercentage | 0xA48C | 03 | U16 | 1 | RW
484 | VRTactivepowerrecoverygradient | 0xA48D | 03 | U16 | 1 | RW
485 | RCDcurrentlimit | 0xA498 | 03 | U16 | 10 | RW
486 | Voltagerisesuppression | 0xA49A | 03 | U16 |  | RW
487 | Voltagerisesuppressionreactivepoweradjustmentpoint | 0xA49B | 03 | U16 | 10 | RW
488 | Voltagerisesuppressionactivederatingthreshold | 0xA49C | 03 | U16 | 10 | RW
489 | FREQUENCYMODULATIONCONTROL | 0xA49D | 03 | U16 |  | RW
490 | FREQUENCYMODULATIONCONTROLDIFFERENTIALMODULATIONRATE | 0xA49E | 03 | U16 | 1 | RW
491 | Overfrequencyderating | 0xA49F | 03 | U16 |  | RW
492 | Overfrequencyderatingcutofffrequency | 0xA4A0 | 03 | U16 | Hz 100 | RW
493 | Overfrequencyderatingcut-offpower | 0xA4A1 | 03 | U16 | 1 | RW
494 | Triggeringfrequency ofoverfrequencyderating | 0xA4A2 | 03 | U16 | Hz 100 | RW
495 | Overfrequencyderatingexitfrequency | 0xA4A3 | 03 | U16 | Hz 100 | RW
496 | Overfrequencyderatingpowerrecoverygradient | 0xA4A4 | 03 | U16 | 1 | RW
497 | UnderfrequencyPowerIncrease | 0xA4A7 | 03 | U16 |  | RW
498 | UnderfrequencyPowerIncreaseRecoveryGradient | 0xA4A8 | 03 | U16 | 1 | RW
499 | Cutofffrequency ofunderfrequencypowerincrease | 0xA4C0 | 03 | U16 | Hz 100 | RW
500 | Cut-offpowerforunderfrequencypowerincrease | 0xA4C1 | 03 | U16 | 1 | RW
501 | UnderfrequencyPowerIncreaseTriggeringFrequency | 0xA4C2 | 03 | U16 | Hz 100 | RW
502 | UnderfrequencyPowerIncreaseExitFrequency | 0xA4C3 | 03 | U16 | Hz 100 | RW
503 | BUILT_IN_PIDMODE | 0xA4C4 | 03 | U16 |  | RW
504 | PIDoutputvoltage | 0xA4C5 | 03 | S16 | V 10 | RW
505 | Activepowerchangegradient | 0xA4D0 | 03 | U32 | 1000 | RW
506 | Undervoltageprotectionthresholdfor10minutes | 0xA52F | 03 | U16 | V 10 | RW
507 | Ten-minuteundervoltageprotectiontime | 0xA530 | 03 | U32 | 1 | RW
508 | Ten-minuteovervoltageprotectionthreshold | 0xA532 | 03 | U16 | V 10 | RW
509 | Ten-minuteovervoltageprotectiontime | 0xA533 | 03 | U32 | 1 | RW
510 | Level-1overvoltageprotectionthreshold | 0xA535 | 03 | U16 | V 10 | RW
511 | Level-1overvoltageprotectiontime | 0xA536 | 03 | U32 | 1 | RW
512 | Level-2overvoltageprotectionthreshold | 0xA538 | 03 | U16 | V 10 | RW
513 | Level 2OvervoltageProtectionTime | 0xA539 | 03 | U32 | 1 | RW
514 | Level-3overvoltageprotectionthreshold | 0xA53B | 03 | U16 | V 10 | RW
515 | Level-3overvoltageprotectiontime | 0xA53C | 03 | U32 | 1 | RW
516 | Level-4overvoltageprotectionthreshold | 0xA53E | 03 | U16 | V 10 | RW
517 | Level-4overvoltageprotectiontime | 0xA53F | 03 | U32 | 1 | RW
518 | Level-5overvoltageprotectionthreshold | 0xA541 | 03 | U16 | V 10 | RW
519 | Level-5overvoltageprotectiontime | 0xA542 | 03 | U32 | 1 | RW
520 | Level-6overvoltageprotectionthreshold | 0xA544 | 03 | U16 | V 10 | RW
521 | Level-6overvoltageprotectiontime | 0xA545 | 03 | U32 | 1 | RW
522 | Level-1undervoltageprotectionthreshold | 0xA547 | 03 | U16 | V 10 | RW
523 | Level-1UndervoltageProtectionTime | 0xA548 | 03 | U32 | 1 | RW
524 | Level-2undervoltageprotectionthreshold | 0xA54A | 03 | U16 | V 10 | RW
525 | Level 2UndervoltageProtectionTime | 0xA54B | 03 | U32 | 1 | RW
526 | Level-3undervoltageprotectionthreshold | 0xA54D | 03 | U16 | V 10 | RW
527 | Level-3UndervoltageProtectionTime | 0xA54E | 03 | U32 | 1 | RW
528 | Level-4undervoltageprotectionthreshold | 0xA550 | 03 | U16 | V 10 | RW
529 | Level-4UndervoltageProtectionTime | 0xA551 | 03 | U32 | 1 | RW
530 | Level-5undervoltageprotectionthreshold | 0xA553 | 03 | U16 | V 10 | RW
531 | Level-5UndervoltageProtectionTime | 0xA554 | 03 | U32 | 1 | RW
532 | Level-6undervoltageprotectionthreshold | 0xA556 | 03 | U16 | V 10 | RW
533 | Level-6UndervoltageProtectionTime | 0xA557 | 03 | U32 | 1 | RW
534 | Level-1overfrequencyprotectionthreshold | 0xA559 | 03 | U16 | Hz 100 | RW
535 | Level-1OverfrequencyProtectionTime | 0xA55A | 03 | U32 | 1 | RW
536 | Level-2overfrequencyprotectionthreshold | 0xA55C | 03 | U16 | Hz 100 | RW
537 | Level-2overfrequencyprotectiontime | 0xA55D | 03 | U32 | 1 | RW
538 | Level-3overfrequencyprotectionthreshold | 0xA55F | 03 | U16 | Hz 100 | RW
539 | Level-3overfrequencyprotectiontime | 0xA560 | 03 | U32 | 1 | RW
540 | Level-4overfrequencyprotectionthreshold | 0xA562 | 03 | U16 | Hz 100 | RW
541 | Level-4overfrequencyprotectiontime | 0xA563 | 03 | U32 | 1 | RW
542 | Level-5overfrequencyprotectionthreshold | 0xA565 | 03 | U16 | Hz 100 | RW
543 | Level-5overfrequencyprotectiontime | 0xA566 | 03 | U32 | 1 | RW
544 | Level-6overfrequencyprotectionthreshold | 0xA568 | 03 | U16 | Hz 100 | RW
545 | Six-leveloverfrequencyprotectiontime | 0xA569 | 03 | U32 | 1 | RW
546 | Level-1underfrequencyprotectionthreshold | 0xA56B | 03 | U16 | Hz 100 | RW
547 | Level-1UnderfrequencyProtectionTime | 0xA56C | 03 | U32 | 1 | RW
548 | Level-2underfrequencyprotectionthreshold | 0xA56E | 03 | U16 | Hz 100 | RW
549 | Level-2underfrequencyprotectiontime | 0xA56F | 03 | U32 | 1 | RW
550 | Level-3underfrequencyprotectionthreshold | 0xA571 | 03 | U16 | Hz 100 | RW
551 | Level-3underfrequencyprotectiontime | 0xA572 | 03 | U32 | 1 | RW
552 | Level-4underfrequencyprotectionthreshold | 0xA574 | 03 | U16 | Hz 100 | RW
553 | Level-4UnderfrequencyProtectionTime | 0xA575 | 03 | U32 | 1 | RW
554 | Level-5underfrequencyprotectionthreshold | 0xA577 | 03 | U16 | Hz 100 | RW
555 | Level-5UnderfrequencyProtectionTime | 0xA578 | 03 | U32 | 1 | RW
556 | Level-6underfrequencyprotectionthreshold | 0xA57A | 03 | U16 | Hz 100 | RW
557 | Level-6UnderfrequencyProtectionTime | 0xA57B | 03 | U32 | 1 | RW
558 | Outputimpedanceenhancementfrequencypoint | 0xA5A4 | 03 | U16 | Hz 10 | RW
559 | UnderfrequencyPowerIncreaseEffectiveDelayTime | 0xA5BD | 03 | U16 | 1 | RW
560 | Powersettings | 0xA82C | 03 | U16 | 1 | RW
561 | [ManagementSystem]TCPFrameLength | 0xA837 | 03 | U16 | 1 | RW
562 | MANAGEMENT_SYSTEM_PORTMODE | 0xA85C | 03 | U16 |  | RW
563 | STAWIRELESS_ROUTING_ENCRYPTION_MODE | 0xA89C | 03 | U16 |  | RW
564 | [App]Initialpower-onflag | 0xA95F | 03 | U16 |  | RW
565 | PARALLELCOMMUNICATIONMODE | 0xA961 | 03 | U16 |  | RW
566 | REG_4GNETWORKMODE | 0xA9A6 | 03 | U16 |  | RW
567 | REG_4GAPNMODE | 0xA9A7 | 03 | U16 |  | RW
568 | Start-upcurrent | 0xAA71 | 03 | U16 | A 100 | RW
569 | Restorefactorysettings. | 0xAFC8 | 03 | U16 |  | WO
570 | Accumulatedenergyyieldcorrection | 0xAFD0 | 03 | U32 | kWh 100 | WO | cumulative_energy
571 | Powerlimitforgrid-tiedsites | 0xB7E7 | 03 | S32 | W 1 | RW
572 | SettingtheAccumulatedEnergyYield | 0xB829 | 03 | U16 |  | WO
573 | Networkfrequencyband | 0xB830 | 03 | U16 |  | RW
574 | SECURITYMODE | 0xB834 | 03 | U16 |  | RW
575 | Fastpower-downenable | 0xB835 | 03 | U16 |  | RW
576 | Forwardpower | 0xB8C4 | 03 | U16 |  | RW
577 | CTratedcurrent | 0xB8C6 | 03 | U16 | A 1 | RW
578 | ACTIVEPOWERCONTROLMODE | 0xB937 | 03 | U16 |  | RW
579 | Maximumpowerfedtothegrid(kW) | 0xB938 | 03 | S32 | kW 1000 | RW
580 | MaximumFeedGridPower(%) | 0xB93A | 03 | S16 | 10 | RW
581 | RESTRICTIONMODE | 0xB93B | 03 | U16 |  | RW
582 | Powerdecreaseadjustmentperiod | 0xB93C | 03 | U16 | 10 | RW
583 | PowerIncreaseThreshold | 0xB93E | 03 | U32 | kW 1000 | RW
584 | Activepowerlimitforfailprotection[%][lowprecision] | 0xB940 | 03 | S16 | 10 | RW
585 | REACTIVEPOWERCONTROLMODE | 0xB941 | 03 | U16 |  | RW
586 | targetpowerfactor | 0xB944 | 03 | S16 | 1000 | RW
587 | Reactivepoweradjustmentperiod | 0xB945 | 03 | U16 | 10 | RW
588 | Failureprotectionreactivepowerlimit[PF] | 0xB948 | 03 | S16 | 1000 | RW
589 | Powerplant DCcapacity | 0xB94B | 03 | U32 | kW 1000 | RW
590 | Feedingpowerover-thresholdprotectionshutdown | 0xBB4E | 03 | U16 |  | RW

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## INFO_MAPPING
INFO_MAPPING — Model / Serial Number 수동 매핑
※ D열에서 매핑할 레지스터를 선택하세요. E~G열은 추천 후보, H열은 전체 INFO 후보 목록.
No | Field | 설명 | 매칭된 레지스터 (주소) | 추천 후보 1 | 추천 후보 2 | 추천 후보 3 | 전체 레지스터 목록 | FC
1 | model | Model 정보 (제조사/타입/제품명) | MODEL (0x7530) |  |  |  | ABNORMALGROUNDINGSHUTDOWN | 3 | ABNORMALGROUNDINGSHUTDOWN | 3 | 0xA454 | pdf
2 | sn | Serial Number / Firmware Version | SERIAL_NUMBER (0x753F) |  |  |  | ABNORMAL_GROUNDING | 3 | ABNORMAL_GROUNDING | 3 | 0x080D | pdf
[7 empty] | ABNORMAL_PV_MODULECONFIGURATION |  | ABNORMAL_PV_MODULECONFIGURATION | 3 | 0x0820
[7 empty] | ABNORMAL_RESIDUAL_CURRENT |  | ABNORMAL_RESIDUAL_CURRENT | 3 | 0x0803
[7 empty] | ABNORMAL_STRING_POWER |  | ABNORMAL_STRING_POWER | 3 | 0x07DD
[7 empty] | ABNT_NBR_16149 |  | ABNT_NBR_16149 | 3 | 0x005C
[7 empty] | ABNT_NBR_16149_MV480 |  | ABNT_NBR_16149_MV480 | 3 | 0x005D
[7 empty] | ABNT_NBR_16149_MV800 |  | ABNT_NBR_16149_MV800 | 3 | 0x007D
[7 empty] | ABUDHABI_MV800 |  | ABUDHABI_MV800 | 3 | 0x009D
[7 empty] | ACCUMULATEDENERGYYIELDCORRECTION |  | ACCUMULATEDENERGYYIELDCORRECTION | 3 | 0xAFD0
[7 empty] | ACCUMULATEDPOWERGENERATION |  | ACCUMULATEDPOWERGENERATION | 3 | 0x7D6A
[7 empty] | ACCUMULATEDREACTIVEPOWER |  | ACCUMULATEDREACTIVEPOWER | 3 | 0x9103
[7 empty] | ACTIVEPOWER |  | ACTIVEPOWER | 3 | 0x90F9
[7 empty] | ACTIVEPOWERADJUSTMENTSTATUS |  | ACTIVEPOWERADJUSTMENTSTATUS | 3 | 0x89E4
[7 empty] | ACTIVEPOWERCHANGEGRADIENT |  | ACTIVEPOWERCHANGEGRADIENT | 3 | 0xA421
[7 empty] | ACTIVEPOWERCONTROLMODE |  | ACTIVEPOWERCONTROLMODE | 3 | 0xB937
[7 empty] | ACTIVEPOWERFAST |  | ACTIVEPOWERFAST | 3 | 0x7D5F
[7 empty] | ACTIVEPOWERLIMITFORFAILPROTECTIONLOWPRECISION |  | ACTIVEPOWERLIMITFORFAILPROTECTIONLOWPRECISION | 3 | 0xB940
[7 empty] | ACTIVEPOWERPERCENTAGECONTROLLOWPRECISION |  | ACTIVEPOWERPERCENTAGECONTROLLOWPRECISION | 3 | 0x9D07
[7 empty] | ACTIVEPOWERPERCENTAGEDERATINGLOWPRECISION |  | ACTIVEPOWERPERCENTAGEDERATINGLOWPRECISION | 3 | 0x9CBD
[7 empty] | ACTIVEPOWERREFERENCE |  | ACTIVEPOWERREFERENCE | 3 | 0xA42B
[7 empty] | ACTIVE_ISLANDING |  | ACTIVE_ISLANDING | 3 | 0x0816
[7 empty] | ACTIVE_POWER_LIMITFOR_FAILURE_PROTECTIONK_WLOW_PRECISION |  | ACTIVE_POWER_LIMITFOR_FAILURE_PROTECTIONK_WLOW_PRECISION | 3 | 0xA45D
[7 empty] | AC_POWER |  | AC_POWER | 3 | 0x7D50
[7 empty] | AFCIVERSIONNUMBER |  | AFCIVERSIONNUMBER | 3 | 0x796D
[7 empty] | AFCI_SELF_CHECK_FAIL_1 |  | AFCI_SELF_CHECK_FAIL_1 | 3 | 0x07E5
[7 empty] | ALARM1 |  | ALARM1 | 3 | 0x7D08
[7 empty] | ALARM2 |  | ALARM2 | 3 | 0x7D09
[7 empty] | ALARM3 |  | ALARM3 | 3 | 0x7D0A
[7 empty] | ALARM4 |  | ALARM4 | 3 | 0x7D0B
[7 empty] | ALARM5 |  | ALARM5 | 3 | 0x7D0C
[7 empty] | ALARM6 |  | ALARM6 | 3 | 0x7D0D
[7 empty] | ALARMCLEARANCE |  | ALARMCLEARANCE | 3 | 0xAFCD
[7 empty] | ALARMCLEARANCE_SN |  | ALARMCLEARANCE_SN | 3 | 0x7D9B
[7 empty] | ALARMMASKING |  | ALARMMASKING | 3 | 0xAFCE
[7 empty] | ALARMPORTSELF_CHECKSTART |  | ALARMPORTSELF_CHECKSTART | 3 | 0xAFED
[7 empty] | ALARMSETTING |  | ALARMSETTING | 3 | 0xAFCB
[7 empty] | ANRE_MV480 |  | ANRE_MV480 | 3 | 0x0035
[7 empty] | APPARENTPOWERREFERENCE |  | APPARENTPOWERREFERENCE | 3 | 0xA429
[7 empty] | APP_INITIALPOWER_ONFLAG |  | APP_INITIALPOWER_ONFLAG | 3 | 0xA95F
[7 empty] | AUDIBLEANDVISUALALARM |  | AUDIBLEANDVISUALALARM | 3 | 0xA432
[7 empty] | AUDIBLEANDVISUALALARMCONFIRMATION |  | AUDIBLEANDVISUALALARMCONFIRMATION | 3 | 0xAFF0
[7 empty] | AUTHORIZATION_FEATURE_SIGNATURE |  | AUTHORIZATION_FEATURE_SIGNATURE | 3 | 0x8993
[7 empty] | AUTOMATICPOWER_OFFWHENCOMMUNICATION_ISDISCONNECTED |  | AUTOMATICPOWER_OFFWHENCOMMUNICATION_ISDISCONNECTED | 3 | 0xA44F
[7 empty] | AUTOMATICPOWER_ONAFTERCOMMUNICATIONRECOVERY |  | AUTOMATICPOWER_ONAFTERCOMMUNICATIONRECOVERY | 3 | 0xA450
[7 empty] | AUTOMATIC_POWER_GRID_RECONNECTION_TIME |  | AUTOMATIC_POWER_GRID_RECONNECTION_TIME | 3 | 0xA46C
[7 empty] | AVERAGE_PVNEGATIVE_TO_GROUNDVOLTAGE |  | AVERAGE_PVNEGATIVE_TO_GROUNDVOLTAGE | 3 | 0x7DB3
[7 empty] | AZIMUTH10SAMPLING |  | AZIMUTH10SAMPLING | 3 | 0x84E5
[7 empty] | AZIMUTH11SAMPLING |  | AZIMUTH11SAMPLING | 3 | 0x84E7
[7 empty] | AZIMUTH12SAMPLING |  | AZIMUTH12SAMPLING | 3 | 0x84E9
[7 empty] | AZIMUTH14SAMPLING |  | AZIMUTH14SAMPLING | 3 | 0x84ED
[7 empty] | AZIMUTH1SAMPLING |  | AZIMUTH1SAMPLING | 3 | 0x84D3
[7 empty] | AZIMUTH2SAMPLING |  | AZIMUTH2SAMPLING | 3 | 0x84D5
[7 empty] | AZIMUTH3SAMPLING |  | AZIMUTH3SAMPLING | 3 | 0x84D7
[7 empty] | AZIMUTH4SAMPLING |  | AZIMUTH4SAMPLING | 3 | 0x84D9
[7 empty] | AZIMUTH5SAMPLING |  | AZIMUTH5SAMPLING | 3 | 0x84DB
[7 empty] | AZIMUTH6SAMPLING |  | AZIMUTH6SAMPLING | 3 | 0x84DD
[7 empty] | AZIMUTH7SAMPLING |  | AZIMUTH7SAMPLING | 3 | 0x84DF
[7 empty] | AZIMUTH8SAMPLING |  | AZIMUTH8SAMPLING | 3 | 0x84E1
[7 empty] | AZIMUTH9SAMPLING |  | AZIMUTH9SAMPLING | 3 | 0x84E3
[7 empty] | A_BLINEVOLTAGE |  | A_BLINEVOLTAGE | 3 | 0x9106
[7 empty] | BAHRAIN |  | BAHRAIN | 3 | 0x00EA
[7 empty] | BAHRAIN_MV480 |  | BAHRAIN_MV480 | 3 | 0x00EB
[7 empty] | BAHRAIN_MV800 |  | BAHRAIN_MV800 | 3 | 0x00EC
[7 empty] | BANGLADESH |  | BANGLADESH | 3 | 0x00E5
[7 empty] | BANGLADESH_MV480 |  | BANGLADESH_MV480 | 3 | 0x00E6
[7 empty] | BANGLADESH_MV800 |  | BANGLADESH_MV800 | 3 | 0x00E7
[7 empty] | BATTERY_ABNORMAL |  | BATTERY_ABNORMAL | 3 | 0x0814
[7 empty] | BATTERY_REVERSE_CONNECTION7 |  | BATTERY_REVERSE_CONNECTION7 | 3 | 0x0815
[7 empty] | BCLINEVOLTAGE |  | BCLINEVOLTAGE | 3 | 0x9108
[7 empty] | BDEW_MV |  | BDEW_MV | 3 | 0x0008
[7 empty] | BDEW_MV480 |  | BDEW_MV480 | 3 | 0x001C
[7 empty] | BDEW_MV800 |  | BDEW_MV800 | 3 | 0x007C
[7 empty] | BEARING13SAMPLING |  | BEARING13SAMPLING | 3 | 0x84EB
[7 empty] | BEARING16SAMPLING |  | BEARING16SAMPLING | 3 | 0x84F1
[7 empty] | BEARINGANGLE_15SAMPLING |  | BEARINGANGLE_15SAMPLING | 3 | 0x84EF
[7 empty] | BRASIL_ANEEL_MV800 |  | BRASIL_ANEEL_MV800 | 3 | 0x0095
[7 empty] | BUILT_IN_PIDMODE |  | BUILT_IN_PIDMODE | 3 | 0xA4C4
[7 empty] | BUILT_IN_PIDRUNNINGSTATUS |  | BUILT_IN_PIDRUNNINGSTATUS | 3 | 0x7DBE
[7 empty] | BUILT_IN_PID_OPERATIONABNORMAL6 |  | BUILT_IN_PID_OPERATIONABNORMAL6 | 3 | 0x0825
[7 empty] | BUSNEGATIVEVOLTAGETOGROUND |  | BUSNEGATIVEVOLTAGETOGROUND | 3 | 0x88E4
[7 empty] | C10_11_MV800 |  | C10_11_MV800 | 3 | 0x00FE
[7 empty] | C11_C10_MV480 |  | C11_C10_MV480 | 3 | 0x0029
[7 empty] | CALINEVOLTAGE |  | CALINEVOLTAGE | 3 | 0x910A
[7 empty] | CAMEROON_MV800 |  | CAMEROON_MV800 | 3 | 0x009B
[7 empty] | CARRIERS |  | CARRIERS | 3 | 0x9240
[7 empty] | CEA_MV800 |  | CEA_MV800 | 3 | 0x010A
[7 empty] | CEI0_16 |  | CEI0_16 | 3 | 0x0017
[7 empty] | CEI0_16_MV480 |  | CEI0_16_MV480 | 3 | 0x0046
[7 empty] | CEI0_16_MV800 |  | CEI0_16_MV800 | 3 | 0x0097
[7 empty] | CEI0_21 |  | CEI0_21 | 3 | 0x000D
[7 empty] | CEI0_21_MV480 |  | CEI0_21_MV480 | 3 | 0x004A
[7 empty] | CEI0_21_MV800 |  | CEI0_21_MV800 | 3 | 0x008F
[7 empty] | CHARACTERISTICCURVE_REACTIVEPOWERADJUSTMENTTIME |  | CHARACTERISTICCURVE_REACTIVEPOWERADJUSTMENTTIME | 3 | 0x9D04
[7 empty] | CLEARINGACTIVEALARMS |  | CLEARINGACTIVEALARMS | 3 | 0xAFC9
[7 empty] | CLEAR_THERUNNINGTIMEINFORMATION |  | CLEAR_THERUNNINGTIMEINFORMATION | 3 | 0xAFD3
[7 empty] | CONNECTIONSTATUS_OFSTRING_6 |  | CONNECTIONSTATUS_OFSTRING_6 | 3 | 0x7E31
[7 empty] | CONVERSIONFACTOR |  | CONVERSIONFACTOR | 3 | 0x9260
[7 empty] | COS_P_PNEXITVOLTAGE |  | COS_P_PNEXITVOLTAGE | 3 | 0xA476
[7 empty] | COS_P_PNTRIGGERVOLTAGE |  | COS_P_PNTRIGGERVOLTAGE | 3 | 0xA475
[7 empty] | CPLDVERSIONNUMBER |  | CPLDVERSIONNUMBER | 3 | 0x795E
[7 empty] | CTRATEDCURRENT |  | CTRATEDCURRENT | 3 | 0xB8C6
[7 empty] | CUMULATIVE_ENERGY |  | CUMULATIVE_ENERGY | 3 | 0x7DDA
[7 empty] | CURRENTSTATUS_OFTHEPHYSICALLOCATION |  | CURRENTSTATUS_OFTHEPHYSICALLOCATION | 3 | 0x9156
[7 empty] | CURRENT_DAYPOWERGENERATION |  | CURRENT_DAYPOWERGENERATION | 3 | 0x7D72
[7 empty] | CURRENT_HOUR_ELECTRICITY |  | CURRENT_HOUR_ELECTRICITY | 3 | 0x7D70
[7 empty] | CURRENT_PERCENTAGE |  | CURRENT_PERCENTAGE | 3 | 0x9262
[7 empty] | CUSTOM_50_HZ |  | CUSTOM_50_HZ | 3 | 0x0015
[7 empty] | CUSTOM_60_HZ |  | CUSTOM_60_HZ | 3 | 0x0016
[7 empty] | CUSTOM_MV480_50_HZ |  | CUSTOM_MV480_50_HZ | 3 | 0x001D
[7 empty] | CUSTOM_MV600_50_HZ |  | CUSTOM_MV600_50_HZ | 3 | 0x0078
[7 empty] | CUSTOM_MV800_50HZ |  | CUSTOM_MV800_50HZ | 3 | 0x00C0
[7 empty] | CUTOFFFREQUENCY_OFUNDERFREQUENCYPOWERINCREASE |  | CUTOFFFREQUENCY_OFUNDERFREQUENCYPOWERINCREASE | 3 | 0xA4C0
[7 empty] | CUT_OFFPOWERFORUNDERFREQUENCYPOWERINCREASE |  | CUT_OFFPOWERFORUNDERFREQUENCYPOWERINCREASE | 3 | 0xA4C1
[7 empty] | DC_MBUSNETWORKINGSTATUS |  | DC_MBUSNETWORKINGSTATUS | 3 | 0x9182
[7 empty] | DC_MBUSVERSIONNUMBER |  | DC_MBUSVERSIONNUMBER | 3 | 0x798B
[7 empty] | DC_PROTECTION_UNIT_ABNORMAL8 |  | DC_PROTECTION_UNIT_ABNORMAL8 | 3 | 0x0828
[7 empty] | DEDICATED |  | DEDICATED | 3 | 0x00C6
[7 empty] | DEFAULTACTIVEPOWERCHANGEGRADIENT |  | DEFAULTACTIVEPOWERCHANGEGRADIENT | 3 | 0xBA3D
[7 empty] | DEFERREDACTIVATIONSTATE |  | DEFERREDACTIVATIONSTATE | 3 | 0x892B
[7 empty] | DESCRIPTION_ABOUTTHE_120TH_DEVICE |  | DESCRIPTION_ABOUTTHE_120TH_DEVICE | 3 | 0x00FF
[7 empty] | DESCRIPTION_ABOUTTHE_FIRST_DEVICE |  | DESCRIPTION_ABOUTTHE_FIRST_DEVICE | 3 | 0x0088
[7 empty] | DEVICE_FAULT |  | DEVICE_FAULT | 3 | 0x0810
[7 empty] | DEVICE_SNFEATURECODE |  | DEVICE_SNFEATURECODE | 3 | 0x7D0F
[7 empty] | DIRECTIONOFTHEBUILT_IN_PIDCOMPENSATION |  | DIRECTIONOFTHEBUILT_IN_PIDCOMPENSATION | 3 | 0x7DC0
[7 empty] | DISCONNECTEDSTATUS |  | DISCONNECTEDSTATUS | 3 | 0x915C
[7 empty] | DUBAI_MV800 |  | DUBAI_MV800 | 3 | 0x008A
[7 empty] | ELECTRICITYGENERATED_INTHECURRENTMONTH |  | ELECTRICITYGENERATED_INTHECURRENTMONTH | 3 | 0x7D74
[7 empty] | ELECTRICITYGENERATED_INTHECURRENTYEAR |  | ELECTRICITYGENERATED_INTHECURRENTYEAR | 3 | 0x7D76
[7 empty] | ELECTRICITYGENERATED_INTHEPREVIOUSDAY |  | ELECTRICITYGENERATED_INTHEPREVIOUSDAY | 3 | 0x7DA2
[7 empty] | ELECTRICITYGENERATED_INTHEPREVIOUSHOUR |  | ELECTRICITYGENERATED_INTHEPREVIOUSHOUR | 3 | 0x7D9E
[7 empty] | ELECTRICITYGENERATED_INTHEPREVIOUSMONTH |  | ELECTRICITYGENERATED_INTHEPREVIOUSMONTH | 3 | 0x7DA6
[7 empty] | ELECTRICITYGENERATED_INTHEPREVIOUSYEAR |  | ELECTRICITYGENERATED_INTHEPREVIOUSYEAR | 3 | 0x7DAA
[7 empty] | ELECTRICITYSTATISTICSTIMEOFTHEPREVIOUSDAY |  | ELECTRICITYSTATISTICSTIMEOFTHEPREVIOUSDAY | 3 | 0x7DA0
[7 empty] | ELECTRICITYSTATISTICSTIMEOFTHEPREVIOUSYEAR |  | ELECTRICITYSTATISTICSTIMEOFTHEPREVIOUSYEAR | 3 | 0x7DA8
[7 empty] | ELECTRIC_RULE_NO_21_LV208 |  | ELECTRIC_RULE_NO_21_LV208 | 3 | 0x00D2
[7 empty] | ELECTRIC_RULE_NO_21_LV240 |  | ELECTRIC_RULE_NO_21_LV240 | 3 | 0x00D3
[7 empty] | ELECTRIC_RULE_NO_21_MV480 |  | ELECTRIC_RULE_NO_21_MV480 | 3 | 0x0036
[7 empty] | ELECTRIC_RULE_NO_21_MV800 |  | ELECTRIC_RULE_NO_21_MV800 | 3 | 0x00BA
[7 empty] | EN50438_IE |  | EN50438_IE | 3 | 0x003E
[7 empty] | EN50438_IE_MV480 |  | EN50438_IE_MV480 | 3 | 0x003D
[7 empty] | EN50438_IE_MV800 |  | EN50438_IE_MV800 | 3 | 0x008C
[7 empty] | ESNVALIDATIONCOMMAND |  | ESNVALIDATIONCOMMAND | 3 | 0xAFD7
[7 empty] | EXTERNAL_FAN_ABNORMAL |  | EXTERNAL_FAN_ABNORMAL | 3 | 0x0826
[7 empty] | EXTERNAL_POWERALARM10 |  | EXTERNAL_POWERALARM10 | 3 | 0x7E08
[7 empty] | EXTERNAL_POWERALARM11 |  | EXTERNAL_POWERALARM11 | 3 | 0x7E09
[7 empty] | EXTERNAL_POWERALARM12 |  | EXTERNAL_POWERALARM12 | 3 | 0x7E0A
[7 empty] | EXTERNAL_POWERALARM13 |  | EXTERNAL_POWERALARM13 | 3 | 0x7E0B
[7 empty] | EXTERNAL_POWERALARM14 |  | EXTERNAL_POWERALARM14 | 3 | 0x7E0C
[7 empty] | EXTERNAL_POWERALARM15 |  | EXTERNAL_POWERALARM15 | 3 | 0x7E0D
[7 empty] | EXTERNAL_POWERALARM16 |  | EXTERNAL_POWERALARM16 | 3 | 0x7E0E
[7 empty] | EXTERNAL_POWERALARM17 |  | EXTERNAL_POWERALARM17 | 3 | 0x7E11
[7 empty] | EXTERNAL_POWERALARM_1 |  | EXTERNAL_POWERALARM_1 | 3 | 0x7DFF
[7 empty] | EXTERNAL_POWERALARM_2 |  | EXTERNAL_POWERALARM_2 | 3 | 0x7E00
[7 empty] | EXTERNAL_POWERALARM_3 |  | EXTERNAL_POWERALARM_3 | 3 | 0x7E01
[7 empty] | EXTERNAL_POWERALARM_4 |  | EXTERNAL_POWERALARM_4 | 3 | 0x7E02
[7 empty] | EXTERNAL_POWERALARM_5 |  | EXTERNAL_POWERALARM_5 | 3 | 0x7E03
[7 empty] | EXTERNAL_POWERALARM_6 |  | EXTERNAL_POWERALARM_6 | 3 | 0x7E04
[7 empty] | EXTERNAL_POWERALARM_7 |  | EXTERNAL_POWERALARM_7 | 3 | 0x7E05
[7 empty] | EXTERNAL_POWERALARM_8 |  | EXTERNAL_POWERALARM_8 | 3 | 0x7E06
[7 empty] | EXTERNAL_POWERALARM_9 |  | EXTERNAL_POWERALARM_9 | 3 | 0x7E07
[7 empty] | FAILUREPROTECTIONACTIVEPOWERMODE |  | FAILUREPROTECTIONACTIVEPOWERMODE | 3 | 0xA45C
[7 empty] | FAILUREPROTECTIONREACTIVEPOWERLIMIT_PF |  | FAILUREPROTECTIONREACTIVEPOWERLIMIT_PF | 3 | 0xB948
[7 empty] | FAILUREPROTECTIONREACTIVEPOWERMODE |  | FAILUREPROTECTIONREACTIVEPOWERMODE | 3 | 0xA45F
[7 empty] | FASTPOWER_DOWNENABLE |  | FASTPOWER_DOWNENABLE | 3 | 0xB835
[7 empty] | FAST_SHUTDOWN_SELF_TEST_STATUS |  | FAST_SHUTDOWN_SELF_TEST_STATUS | 3 | 0x9185
[7 empty] | FAULTY_MONITORING_UNIT |  | FAULTY_MONITORING_UNIT | 3 | 0xF000
[7 empty] | FAULTY_POWER_COLLECTOR2 |  | FAULTY_POWER_COLLECTOR2 | 3 | 0x0813
[7 empty] | FAULT_CODE |  | FAULT_CODE | 3 | 0x7D5A
[7 empty] | FEATUREDATASEQUENCENUMBER |  | FEATUREDATASEQUENCENUMBER | 3 | 0x9152
[7 empty] | FEATURE_DATA_SEQUENCENUMBER |  | FEATURE_DATA_SEQUENCENUMBER | 3 | 0x0002
[7 empty] | FECONNECTIONSTATUS |  | FECONNECTIONSTATUS | 3 | 0x8936
[7 empty] | FEEDINGPOWEROVER_THRESHOLDPROTECTIONSHUTDOWN |  | FEEDINGPOWEROVER_THRESHOLDPROTECTIONSHUTDOWN | 3 | 0xBB4E
[7 empty] | FILE_VERSION |  | FILE_VERSION | 3 | 0x0004
[7 empty] | FIRMWARE_VERSION |  | FIRMWARE_VERSION | 3 | 0x7553
[7 empty] | FIXEDVALUE_OFREACTIVEPOWER_ATNIGHT |  | FIXEDVALUE_OFREACTIVEPOWER_ATNIGHT | 3 | 0x9CC1
[7 empty] | FORWARDPOWER |  | FORWARDPOWER | 3 | 0xB8C4
[7 empty] | FREQUENCY |  | FREQUENCY | 3 | 0x7D55
[7 empty] | FREQUENCYCHANGERATEPROTECTIONPOINT |  | FREQUENCYCHANGERATEPROTECTIONPOINT | 3 | 0xA461
[7 empty] | FREQUENCYCHANGERATEPROTECTIONTIME |  | FREQUENCYCHANGERATEPROTECTIONTIME | 3 | 0xA462
[7 empty] | FREQUENCYMODULATIONCONTROL |  | FREQUENCYMODULATIONCONTROL | 3 | 0xA49D
[7 empty] | FREQUENCYMODULATIONCONTROLDIFFERENTIALMODULATIONRATE |  | FREQUENCYMODULATIONCONTROLDIFFERENTIALMODULATIONRATE | 3 | 0xA49E
[7 empty] | FREQUENCYMODULATIONCONTROLPOWERCHANGEGRADIENT |  | FREQUENCYMODULATIONCONTROLPOWERCHANGEGRADIENT | 3 | 0xA443
[7 empty] | FREQUENCYMODULATIONCONTROLPOWERCHANGELIMITINGAMPLITUDE |  | FREQUENCYMODULATIONCONTROLPOWERCHANGELIMITINGAMPLITUDE | 3 | 0xA444
[7 empty] | FREQUENCYMODULATIONCONTROLRESPONSEDEADBAND |  | FREQUENCYMODULATIONCONTROLRESPONSEDEADBAND | 3 | 0xA43B
[7 empty] | FREQUENCYRATEPROTECTION |  | FREQUENCYRATEPROTECTION | 3 | 0xA460
[7 empty] | FREQUENCY_CLASS |  | FREQUENCY_CLASS | 3 | 0xA413
[7 empty] | FUNCTION_CODE |  | FUNCTION_CODE | 3 | 0x005A
[7 empty] | G59_ENGLAND |  | G59_ENGLAND | 3 | 0x0009
[7 empty] | G59_ENGLAND_MV480 |  | G59_ENGLAND_MV480 | 3 | 0x001F
[7 empty] | G59_ENGLAND_MV800 |  | G59_ENGLAND_MV800 | 3 | 0x006D
[7 empty] | G83_ENGLAND |  | G83_ENGLAND | 3 | 0x000B
[7 empty] | G83_SCOTLAND |  | G83_SCOTLAND | 3 | 0x000C
[7 empty] | G99_TYPEA_HV |  | G99_TYPEA_HV | 3 | 0x0109
[7 empty] | G99_TYPEA_LV |  | G99_TYPEA_LV | 3 | 0x0102
[7 empty] | G99_TYPEB_HV |  | G99_TYPEB_HV | 3 | 0x0104
[7 empty] | G99_TYPEB_HV_MV480 |  | G99_TYPEB_HV_MV480 | 3 | 0x0105
[7 empty] | G99_TYPEB_HV_MV800 |  | G99_TYPEB_HV_MV800 | 3 | 0x0106
[7 empty] | G99_TYPEB_LV |  | G99_TYPEB_LV | 3 | 0x0103
[7 empty] | G99_TYPEC_HV_MV800 |  | G99_TYPEC_HV_MV800 | 3 | 0x0107
[7 empty] | G99_TYPED_MV800 |  | G99_TYPED_MV800 | 3 | 0x0108
[7 empty] | GHANA_MV480 |  | GHANA_MV480 | 3 | 0x00AF
[7 empty] | GHANA_MV800 |  | GHANA_MV800 | 3 | 0x00CA
[7 empty] | GRIDCURRENTPHASE_ACURRENT |  | GRIDCURRENTPHASE_ACURRENT | 3 | 0x90F3
[7 empty] | GRIDFAULTZEROCURRENTMODE |  | GRIDFAULTZEROCURRENTMODE | 3 | 0xA47E
[7 empty] | GRIDVOLTAGEJUMPTRIGGERTHRESHOLD |  | GRIDVOLTAGEJUMPTRIGGERTHRESHOLD | 3 | 0xA47F
[7 empty] | GRIDVOLTAGEPHASE_AVOLTAGE |  | GRIDVOLTAGEPHASE_AVOLTAGE | 3 | 0x90ED
[7 empty] | GRID_LOSS |  | GRID_LOSS | 3 | 0x07F0
[7 empty] | GRID_OVERFREQUENCY |  | GRID_OVERFREQUENCY | 3 | 0x07F4
[7 empty] | GRID_OVERVOLTAGE |  | GRID_OVERVOLTAGE | 3 | 0x07F2
[7 empty] | GRID_UNDERFREQUENCY |  | GRID_UNDERFREQUENCY | 3 | 0x07F5
[7 empty] | GRID_UNDERVOLTAGE |  | GRID_UNDERVOLTAGE | 3 | 0x07F1
[7 empty] | GRID_VOLT_IMBALANCE |  | GRID_VOLT_IMBALANCE | 3 | 0x07F3
[7 empty] | HARDWAREVERSION |  | HARDWAREVERSION | 3 | 0x7918
[7 empty] | HAWAII_USA |  | HAWAII_USA | 3 | 0x0037
[7 empty] | HECO_LM_LV208 |  | HECO_LM_LV208 | 3 | 0x00FC
[7 empty] | HECO_LM_LV240 |  | HECO_LM_LV240 | 3 | 0x00FD
[7 empty] | HECO_OMH_LV208 |  | HECO_OMH_LV208 | 3 | 0x00D4
[7 empty] | HECO_OMH_LV240 |  | HECO_OMH_LV240 | 3 | 0x00D5
[7 empty] | HIGH_INPUT_STRING_VOLTAGE_TOGROUND |  | HIGH_INPUT_STRING_VOLTAGE_TOGROUND | 3 | 0x07DE
[7 empty] | IEC_61727_MV800_60HZ |  | IEC_61727_MV800_60HZ | 3 | 0x0090
[7 empty] | IEEE_1547A_LV208 |  | IEEE_1547A_LV208 | 3 | 0x00D0
[7 empty] | IEEE_1547A_LV240 |  | IEEE_1547A_LV240 | 3 | 0x00D1
[7 empty] | IEEE_1547A_MV480 |  | IEEE_1547A_MV480 | 3 | 0x003F
[7 empty] | IEEE_1547A_MV600 |  | IEEE_1547A_MV600 | 3 | 0x0056
[7 empty] | IEEE_1547A_MV800 |  | IEEE_1547A_MV800 | 3 | 0x00B9
[7 empty] | IEEE_1547_LV208 |  | IEEE_1547_LV208 | 3 | 0x00CE
[7 empty] | IEEE_1547_LV240 |  | IEEE_1547_LV240 | 3 | 0x00CF
[7 empty] | IEEE_1547_MV480 |  | IEEE_1547_MV480 | 3 | 0x0030
[7 empty] | IEEE_1547_MV600 |  | IEEE_1547_MV600 | 3 | 0x004F
[7 empty] | IEEE_1547_MV800 |  | IEEE_1547_MV800 | 3 | 0x00B7
[7 empty] | INFORMATIONABOUTSUBPACKAGE10 |  | INFORMATIONABOUTSUBPACKAGE10 | 3 | 0x75B2
[7 empty] | INFORMATIONABOUTSUBPACKAGE_1 |  | INFORMATIONABOUTSUBPACKAGE_1 | 3 | 0x75A0
[7 empty] | INFORMATIONABOUTSUBPACKAGE_1OFSOUTHBOUNDDEVICE_1 |  | INFORMATIONABOUTSUBPACKAGE_1OFSOUTHBOUNDDEVICE_1 | 3 | 0x772B
[7 empty] | INFORMATIONABOUTSUBPACKAGE_1OFSOUTHBOUNDDEVICE_2 |  | INFORMATIONABOUTSUBPACKAGE_1OFSOUTHBOUNDDEVICE_2 | 3 | 0x7736
[7 empty] | INFORMATIONABOUTSUBPACKAGE_2OFSOUTHBOUNDDEVICE_1 |  | INFORMATIONABOUTSUBPACKAGE_2OFSOUTHBOUNDDEVICE_1 | 3 | 0x772D
[7 empty] | INFORMATIONABOUTSUBPACKAGE_2OFSOUTHBOUNDDEVICE_2 |  | INFORMATIONABOUTSUBPACKAGE_2OFSOUTHBOUNDDEVICE_2 | 3 | 0x7738
[7 empty] | INFORMATIONABOUTSUBPACKAGE_3 |  | INFORMATIONABOUTSUBPACKAGE_3 | 3 | 0x75A4
[7 empty] | INFORMATIONABOUTSUBPACKAGE_3OFSOUTHBOUNDDEVICE_1 |  | INFORMATIONABOUTSUBPACKAGE_3OFSOUTHBOUNDDEVICE_1 | 3 | 0x772F
[7 empty] | INFORMATIONABOUTSUBPACKAGE_3OFSOUTHBOUNDDEVICE_2 |  | INFORMATIONABOUTSUBPACKAGE_3OFSOUTHBOUNDDEVICE_2 | 3 | 0x773A
[7 empty] | INFORMATIONABOUTSUBPACKAGE_4OFSOUTHBOUNDDEVICE_2 |  | INFORMATIONABOUTSUBPACKAGE_4OFSOUTHBOUNDDEVICE_2 | 3 | 0x773C
[7 empty] | INFORMATIONABOUTSUBPACKAGE_6 |  | INFORMATIONABOUTSUBPACKAGE_6 | 3 | 0x75AA
[7 empty] | INNER_TEMP |  | INNER_TEMP | 3 | 0x7D57
[7 empty] | INSULATION_IMPEDANCE |  | INSULATION_IMPEDANCE | 3 | 0x7D58
[7 empty] | INTERNALALARM |  | INTERNALALARM | 3 | 0x88C2
[7 empty] | INTERNALFAN1RUNNINGTIME |  | INTERNALFAN1RUNNINGTIME | 3 | 0x88BA
[7 empty] | INTERNALTEMPERATURE10 |  | INTERNALTEMPERATURE10 | 3 | 0x88D6
[7 empty] | INTERNALTEMPERATURE11 |  | INTERNALTEMPERATURE11 | 3 | 0x88D7
[7 empty] | INTERNALTEMPERATURE12 |  | INTERNALTEMPERATURE12 | 3 | 0x88D8
[7 empty] | INTERNALTEMPERATURE7 |  | INTERNALTEMPERATURE7 | 3 | 0x88D3
[7 empty] | INTERNALTEMPERATURE8 |  | INTERNALTEMPERATURE8 | 3 | 0x88D4
[7 empty] | INTERNALTEMPERATURE9 |  | INTERNALTEMPERATURE9 | 3 | 0x88D5
[7 empty] | INTERNAL_FAN_ABNORMAL |  | INTERNAL_FAN_ABNORMAL | 3 | 0x0827
[7 empty] | INTERNAL_TEMPERATURE1 |  | INTERNAL_TEMPERATURE1 | 3 | 0x88CD
[7 empty] | INTERNAL_TEMPERATURE2 |  | INTERNAL_TEMPERATURE2 | 3 | 0x88CE
[7 empty] | INTERNAL_TEMPERATURE3 |  | INTERNAL_TEMPERATURE3 | 3 | 0x88CF
[7 empty] | INTERNAL_TEMPERATURE4 |  | INTERNAL_TEMPERATURE4 | 3 | 0x88D0
[7 empty] | INTERNAL_TEMPERATURE5 |  | INTERNAL_TEMPERATURE5 | 3 | 0x88D1
[7 empty] | INTERNAL_TEMPERATURE6 |  | INTERNAL_TEMPERATURE6 | 3 | 0x88D2
[7 empty] | INVALIDATIONCODE |  | INVALIDATIONCODE | 3 | 0x8953
[7 empty] | INVERTERCOMPREHENSIVESTATUS |  | INVERTERCOMPREHENSIVESTATUS | 3 | 0x928E
[7 empty] | INVERTERINTEGRATEDSTATUSSUPPORTFLAG |  | INVERTERINTEGRATEDSTATUSSUPPORTFLAG | 3 | 0x928F
[7 empty] | INVERTER_EFFICIENCY |  | INVERTER_EFFICIENCY | 3 | 0x7D56
[7 empty] | INVERTER_MODE |  | INVERTER_MODE | 3 | 0x7D59
[7 empty] | INVERTER_TO_PEWITHSTANDVOLTAGE |  | INVERTER_TO_PEWITHSTANDVOLTAGE | 3 | 0x7DB6
[7 empty] | ISOFEATUREINFORMATION |  | ISOFEATUREINFORMATION | 3 | 0x7DB7
[7 empty] | I_VSCANNINGCAPABILITY |  | I_VSCANNINGCAPABILITY | 3 | 0x8917
[7 empty] | I_VSCANSTATUS |  | I_VSCANSTATUS | 3 | 0x8916
[7 empty] | JAMAICA_MV800 |  | JAMAICA_MV800 | 3 | 0x00A9
[7 empty] | KAZAKHSTAN_MV800 |  | KAZAKHSTAN_MV800 | 3 | 0x00F2
[7 empty] | KENYA_ETHIOPIA |  | KENYA_ETHIOPIA | 3 | 0x006B
[7 empty] | KENYA_ETHIOPIA_MV800 |  | KENYA_ETHIOPIA_MV800 | 3 | 0x0099
[7 empty] | L1_CURRENT |  | L1_CURRENT | 3 | 0x0073
[7 empty] | L1_VOLTAGE |  | L1_VOLTAGE | 3 | 0x0070
[7 empty] | L2_CURRENT |  | L2_CURRENT | 3 | 0x0074
[7 empty] | L2_VOLTAGE |  | L2_VOLTAGE | 3 | 0x0071
[7 empty] | L3_CURRENT |  | L3_CURRENT | 3 | 0x0075
[7 empty] | L3_VOLTAGE |  | L3_VOLTAGE | 3 | 0x0072
[7 empty] | LAST_HOUR_POWER_STATISTICS_TIME |  | LAST_HOUR_POWER_STATISTICS_TIME | 3 | 0x7D9C
[7 empty] | LATEST_HISTORICAL_ALARM_SERIAL_NUMBER |  | LATEST_HISTORICAL_ALARM_SERIAL_NUMBER | 3 | 0x7DAE
[7 empty] | LAYOUT_FILE_CHANGE_SN |  | LAYOUT_FILE_CHANGE_SN | 3 | 0x915A
[7 empty] | LAYOUT_FILE_STORAGE_PROGRESS |  | LAYOUT_FILE_STORAGE_PROGRESS | 3 | 0x9159
[7 empty] | LEAKAGECURRENT_RCD |  | LEAKAGECURRENT_RCD | 3 | 0x88E1
[7 empty] | LEBANON |  | LEBANON | 3 | 0x009E
[7 empty] | LEBANON_MV480 |  | LEBANON_MV480 | 3 | 0x009F
[7 empty] | LEBANON_MV800 |  | LEBANON_MV800 | 3 | 0x00A0
[7 empty] | LEVEL_1OVERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_1OVERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA559
[7 empty] | LEVEL_1OVERFREQUENCY_PROTECTION_TIME |  | LEVEL_1OVERFREQUENCY_PROTECTION_TIME | 3 | 0xA55A
[7 empty] | LEVEL_1OVERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_1OVERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA535
[7 empty] | LEVEL_1OVERVOLTAGEPROTECTIONTIME |  | LEVEL_1OVERVOLTAGEPROTECTIONTIME | 3 | 0xA536
[7 empty] | LEVEL_1UNDERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_1UNDERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA56B
[7 empty] | LEVEL_1UNDERFREQUENCY_PROTECTION_TIME |  | LEVEL_1UNDERFREQUENCY_PROTECTION_TIME | 3 | 0xA56C
[7 empty] | LEVEL_1UNDERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_1UNDERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA547
[7 empty] | LEVEL_1UNDERVOLTAGE_PROTECTION_TIME |  | LEVEL_1UNDERVOLTAGE_PROTECTION_TIME | 3 | 0xA548
[7 empty] | LEVEL_2OVERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_2OVERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA55C
[7 empty] | LEVEL_2OVERFREQUENCYPROTECTIONTIME |  | LEVEL_2OVERFREQUENCYPROTECTIONTIME | 3 | 0xA55D
[7 empty] | LEVEL_2OVERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_2OVERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA538
[7 empty] | LEVEL_2OVERVOLTAGE_PROTECTION_TIME |  | LEVEL_2OVERVOLTAGE_PROTECTION_TIME | 3 | 0xA539
[7 empty] | LEVEL_2UNDERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_2UNDERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA56E
[7 empty] | LEVEL_2UNDERFREQUENCYPROTECTIONTIME |  | LEVEL_2UNDERFREQUENCYPROTECTIONTIME | 3 | 0xA56F
[7 empty] | LEVEL_2UNDERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_2UNDERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA54A
[7 empty] | LEVEL_2UNDERVOLTAGE_PROTECTION_TIME |  | LEVEL_2UNDERVOLTAGE_PROTECTION_TIME | 3 | 0xA54B
[7 empty] | LEVEL_3OVERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_3OVERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA55F
[7 empty] | LEVEL_3OVERFREQUENCYPROTECTIONTIME |  | LEVEL_3OVERFREQUENCYPROTECTIONTIME | 3 | 0xA560
[7 empty] | LEVEL_3OVERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_3OVERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA53B
[7 empty] | LEVEL_3OVERVOLTAGEPROTECTIONTIME |  | LEVEL_3OVERVOLTAGEPROTECTIONTIME | 3 | 0xA53C
[7 empty] | LEVEL_3UNDERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_3UNDERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA571
[7 empty] | LEVEL_3UNDERFREQUENCYPROTECTIONTIME |  | LEVEL_3UNDERFREQUENCYPROTECTIONTIME | 3 | 0xA572
[7 empty] | LEVEL_3UNDERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_3UNDERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA54D
[7 empty] | LEVEL_3UNDERVOLTAGE_PROTECTION_TIME |  | LEVEL_3UNDERVOLTAGE_PROTECTION_TIME | 3 | 0xA54E
[7 empty] | LEVEL_4OVERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_4OVERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA562
[7 empty] | LEVEL_4OVERFREQUENCYPROTECTIONTIME |  | LEVEL_4OVERFREQUENCYPROTECTIONTIME | 3 | 0xA563
[7 empty] | LEVEL_4OVERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_4OVERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA53E
[7 empty] | LEVEL_4OVERVOLTAGEPROTECTIONTIME |  | LEVEL_4OVERVOLTAGEPROTECTIONTIME | 3 | 0xA53F
[7 empty] | LEVEL_4UNDERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_4UNDERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA574
[7 empty] | LEVEL_4UNDERFREQUENCY_PROTECTION_TIME |  | LEVEL_4UNDERFREQUENCY_PROTECTION_TIME | 3 | 0xA575
[7 empty] | LEVEL_4UNDERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_4UNDERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA550
[7 empty] | LEVEL_4UNDERVOLTAGE_PROTECTION_TIME |  | LEVEL_4UNDERVOLTAGE_PROTECTION_TIME | 3 | 0xA551
[7 empty] | LEVEL_5OVERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_5OVERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA565
[7 empty] | LEVEL_5OVERFREQUENCYPROTECTIONTIME |  | LEVEL_5OVERFREQUENCYPROTECTIONTIME | 3 | 0xA566
[7 empty] | LEVEL_5OVERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_5OVERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA541
[7 empty] | LEVEL_5OVERVOLTAGEPROTECTIONTIME |  | LEVEL_5OVERVOLTAGEPROTECTIONTIME | 3 | 0xA542
[7 empty] | LEVEL_5UNDERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_5UNDERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA577
[7 empty] | LEVEL_5UNDERFREQUENCY_PROTECTION_TIME |  | LEVEL_5UNDERFREQUENCY_PROTECTION_TIME | 3 | 0xA578
[7 empty] | LEVEL_5UNDERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_5UNDERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA553
[7 empty] | LEVEL_5UNDERVOLTAGE_PROTECTION_TIME |  | LEVEL_5UNDERVOLTAGE_PROTECTION_TIME | 3 | 0xA554
[7 empty] | LEVEL_6OVERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_6OVERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA568
[7 empty] | LEVEL_6OVERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_6OVERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA544
[7 empty] | LEVEL_6OVERVOLTAGEPROTECTIONTIME |  | LEVEL_6OVERVOLTAGEPROTECTIONTIME | 3 | 0xA545
[7 empty] | LEVEL_6UNDERFREQUENCYPROTECTIONTHRESHOLD |  | LEVEL_6UNDERFREQUENCYPROTECTIONTHRESHOLD | 3 | 0xA57A
[7 empty] | LEVEL_6UNDERFREQUENCY_PROTECTION_TIME |  | LEVEL_6UNDERFREQUENCY_PROTECTION_TIME | 3 | 0xA57B
[7 empty] | LEVEL_6UNDERVOLTAGEPROTECTIONTHRESHOLD |  | LEVEL_6UNDERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA556
[7 empty] | LEVEL_6UNDERVOLTAGE_PROTECTION_TIME |  | LEVEL_6UNDERVOLTAGE_PROTECTION_TIME | 3 | 0xA557
[7 empty] | LICENSELOADINGTIME |  | LICENSELOADINGTIME | 3 | 0x8945
[7 empty] | LICENSE_DEREGISTRATION_TIME |  | LICENSE_DEREGISTRATION_TIME | 3 | 0x8947
[7 empty] | LICENSE_EXPIRED |  | LICENSE_EXPIRED | 3 | 0x0812
[7 empty] | LICENSE_SN |  | LICENSE_SN | 3 | 0x8949
[7 empty] | LOGEXPORTPROGRESS |  | LOGEXPORTPROGRESS | 3 | 0x9154
[7 empty] | LOW_INSULATION_RESISTANCE |  | LOW_INSULATION_RESISTANCE | 3 | 0x080E
[7 empty] | MAIN_DSPVERSION |  | MAIN_DSPVERSION | 3 | 0x7940
[7 empty] | MANAGEMENT_SYSTEM_NMSIPADDRESS |  | MANAGEMENT_SYSTEM_NMSIPADDRESS | 3 | 0x891E
[7 empty] | MANAGEMENT_SYSTEM_PORTMODE |  | MANAGEMENT_SYSTEM_PORTMODE | 3 | 0xA85C
[7 empty] | MANAGEMENT_SYSTEM_TCPFRAME_LENGTH |  | MANAGEMENT_SYSTEM_TCPFRAME_LENGTH | 3 | 0xA837
[7 empty] | MAURITIUS |  | MAURITIUS | 3 | 0x00F3
[7 empty] | MAXIMUMACTIVEPOWER |  | MAXIMUMACTIVEPOWER | 3 | 0xA427
[7 empty] | MAXIMUMACTIVEPOWER_PMAX |  | MAXIMUMACTIVEPOWER_PMAX | 3 | 0x757B
[7 empty] | MAXIMUMACTIVEPOWER_PMAX_R_EAL |  | MAXIMUMACTIVEPOWER_PMAX_R_EAL | 3 | 0x7583
[7 empty] | MAXIMUMAPPARENTCAPABILITY_SMAX_R_EAL |  | MAXIMUMAPPARENTCAPABILITY_SMAX_R_EAL | 3 | 0x7585
[7 empty] | MAXIMUMAPPARENTPOWER |  | MAXIMUMAPPARENTPOWER | 3 | 0xA425
[7 empty] | MAXIMUMAPPARENT_SMAX |  | MAXIMUMAPPARENT_SMAX | 3 | 0x757D
[7 empty] | MAXIMUMNUMBEROFCONNECTEDDEVICES |  | MAXIMUMNUMBEROFCONNECTEDDEVICES | 3 | 0x9235
[7 empty] | MAXIMUMPOWERFEDTOTHEGRIDK_W |  | MAXIMUMPOWERFEDTOTHEGRIDK_W | 3 | 0xB938
[7 empty] | MAXIMUM_FEED_GRID_POWER |  | MAXIMUM_FEED_GRID_POWER | 3 | 0xB93A
[7 empty] | MAXIMUM_FEED_GRID_POWER_DEFAULT |  | MAXIMUM_FEED_GRID_POWER_DEFAULT | 3 | 0xBA3B
[7 empty] | MAXIMUM_PVPOSITIVE_TO_GROUNDVOLTAGE |  | MAXIMUM_PVPOSITIVE_TO_GROUNDVOLTAGE | 3 | 0x7DB4
[7 empty] | MAXIMUM_PVVOLTAGE |  | MAXIMUM_PVVOLTAGE | 3 | 0x7DB1
[7 empty] | METERMODEL |  | METERMODEL | 3 | 0xB8C7
[7 empty] | METER_MODEL_CHECK_RESULT |  | METER_MODEL_CHECK_RESULT | 3 | 0x9112
[7 empty] | METER_STATUS |  | METER_STATUS | 3 | 0x90EC
[7 empty] | METER_TYPE |  | METER_TYPE | 3 | 0x9105
[7 empty] | MINIMUM_PVNEGATIVE_TO_GROUNDVOLTAGE |  | MINIMUM_PVNEGATIVE_TO_GROUNDVOLTAGE | 3 | 0x7DB5
[7 empty] | MINIMUM_PVVOLTAGE |  | MINIMUM_PVVOLTAGE | 3 | 0x7DB2
[7 empty] | MODEL |  | MODEL | 3 | 0x7530
[7 empty] | MODEL_ID |  | MODEL_ID | 3 | 0x7576
[7 empty] | MODULE1RUNNINGSTATUS_OFTHEBATTERY |  | MODULE1RUNNINGSTATUS_OFTHEBATTERY | 3 | 0x9088
[7 empty] | MONITORALARM_3 |  | MONITORALARM_3 | 3 | 0x7DFE
[7 empty] | MONITORALARM_4 |  | MONITORALARM_4 | 3 | 0x7E0F
[7 empty] | MONITORALARM_5 |  | MONITORALARM_5 | 3 | 0x7E10
[7 empty] | MONITORINGALARM_1 |  | MONITORINGALARM_1 | 3 | 0x7DFC
[7 empty] | MONITORINGALARM_2 |  | MONITORINGALARM_2 | 3 | 0x7DFD
[7 empty] | MONITORINGSOFTWAREVERSION |  | MONITORINGSOFTWAREVERSION | 3 | 0x7931
[7 empty] | MONITORING_BOARD_SN |  | MONITORING_BOARD_SN | 3 | 0x7927
[7 empty] | MPPT3DCTOTAL_ENERGY_YIELD |  | MPPT3DCTOTAL_ENERGY_YIELD | 3 | 0x7DD8
[7 empty] | NAMIBIA |  | NAMIBIA | 3 | 0x005B
[7 empty] | NAMIBIA_MV480 |  | NAMIBIA_MV480 | 3 | 0x0091
[7 empty] | NAMIBIA_MV800 |  | NAMIBIA_MV800 | 3 | 0x009A
[7 empty] | NEGATIVEBUSVOLTAGE |  | NEGATIVEBUSVOLTAGE | 3 | 0x88E3
[7 empty] | NETHERLANDS |  | NETHERLANDS | 3 | 0x0011
[7 empty] | NETWORKFREQUENCYBAND |  | NETWORKFREQUENCYBAND | 3 | 0xB830
[7 empty] | NICARAGUA_MV800 |  | NICARAGUA_MV800 | 3 | 0x00B8
[7 empty] | NIGERIA |  | NIGERIA | 3 | 0x006E
[7 empty] | NIGERIA_MV480 |  | NIGERIA_MV480 | 3 | 0x006F
[7 empty] | NIGERIA_MV800 |  | NIGERIA_MV800 | 3 | 0x009C
[7 empty] | NIGHTREACTIVEPOWER |  | NIGHTREACTIVEPOWER | 3 | 0xA453
[7 empty] | NIGHTREACTIVEPOWERCOMPENSATION_Q_S |  | NIGHTREACTIVEPOWERCOMPENSATION_Q_S | 3 | 0x9CC0
[7 empty] | NIGHTREACTIVEPOWERPARAMETERSTAKEEFFECT |  | NIGHTREACTIVEPOWERPARAMETERSTAKEEFFECT | 3 | 0xA456
[7 empty] | NORTHERN_IRELAND_MV800 |  | NORTHERN_IRELAND_MV800 | 3 | 0x008E
[7 empty] | NORTH_MACEDONIA_MV800 |  | NORTH_MACEDONIA_MV800 | 3 | 0x0110
[7 empty] | NO_PERMISSION |  | NO_PERMISSION | 3 | 0x0080
[7 empty] | NRS_097_2_1_MV480 |  | NRS_097_2_1_MV480 | 3 | 0x002E
[7 empty] | NRS_097_2_1_MV800 |  | NRS_097_2_1_MV800 | 3 | 0x0085
[7 empty] | NTPLAST_NTPSYNCHRONIZATIONSTATUS |  | NTPLAST_NTPSYNCHRONIZATIONSTATUS | 3 | 0x8928
[7 empty] | NTPNTPLAST_SYNCHRONIZATION_TIME |  | NTPNTPLAST_SYNCHRONIZATION_TIME | 3 | 0x8929
[7 empty] | NTS_MV480 |  | NTS_MV480 | 3 | 0x0112
[7 empty] | NTS_MV800 |  | NTS_MV800 | 3 | 0x0113
[7 empty] | NUMBEROFCONNECTEDDEVICES |  | NUMBEROFCONNECTEDDEVICES | 3 | 0x9276
[7 empty] | NUMBEROFCRITICALALARMS |  | NUMBEROFCRITICALALARMS | 3 | 0x7D97
[7 empty] | NUMBEROFMAJORALARMS |  | NUMBEROFMAJORALARMS | 3 | 0x7D98
[7 empty] | NUMBEROFNEIGHBORINGNETWORKS |  | NUMBEROFNEIGHBORINGNETWORKS | 3 | 0x9184
[7 empty] | NUMBEROFONLINEOPTIMIZERS |  | NUMBEROFONLINEOPTIMIZERS | 3 | 0x9151
[7 empty] | NUMBEROFUNIQUESOUTHBOUNDSOFTWARE_IDS |  | NUMBEROFUNIQUESOUTHBOUNDSOFTWARE_IDS | 3 | 0x7724
[7 empty] | NUMBEROFUPGRADEPACKAGES |  | NUMBEROFUPGRADEPACKAGES | 3 | 0x759F
[7 empty] | NUMBEROFUPGRADEPACKAGESFORSOUTHBOUNDDEVICE_1 |  | NUMBEROFUPGRADEPACKAGESFORSOUTHBOUNDDEVICE_1 | 3 | 0x772A
[7 empty] | NUMBEROFUPGRADEPACKAGESFORSOUTHBOUNDDEVICE_2 |  | NUMBEROFUPGRADEPACKAGESFORSOUTHBOUNDDEVICE_2 | 3 | 0x7735
[7 empty] | NUMBEROF_MINOR_ALARMS |  | NUMBEROF_MINOR_ALARMS | 3 | 0x7D99
[7 empty] | NUMBEROF_MPPTS |  | NUMBEROF_MPPTS | 3 | 0x7578
[7 empty] | NUMBEROF_NETWORKED_NETWORKS |  | NUMBEROF_NETWORKED_NETWORKS | 3 | 0x9183
[7 empty] | NUMBEROF_PVSTRINGS |  | NUMBEROF_PVSTRINGS | 3 | 0x7577
[7 empty] | NUMBEROF_SEARCHED_OPTIMIZERS |  | NUMBEROF_SEARCHED_OPTIMIZERS | 3 | 0x9157
[7 empty] | NUMBEROF_WARNING_ALARMS |  | NUMBEROF_WARNING_ALARMS | 3 | 0x7D9A
[7 empty] | OFEFRINGNAME_OFSOUTHBOUNDDEVICE_1 |  | OFEFRINGNAME_OFSOUTHBOUNDDEVICE_1 | 3 | 0x7761
[7 empty] | OFEFRINGNAME_OFSOUTHBOUNDDEVICE_3 |  | OFEFRINGNAME_OFSOUTHBOUNDDEVICE_3 | 3 | 0x777F
[7 empty] | OFFERINGNAME_OFSOUTHBOUNDDEVICE_2 |  | OFFERINGNAME_OFSOUTHBOUNDDEVICE_2 | 3 | 0x7770
[7 empty] | OFF_GRIDMODE |  | OFF_GRIDMODE | 3 | 0xA43D
[7 empty] | OF_FGRIDSWITCHOVERMODE |  | OF_FGRIDSWITCHOVERMODE | 3 | 0xA43C
[7 empty] | ON_GRID_OFF_GRID_CONTROLLERABNORMAL4 |  | ON_GRID_OFF_GRID_CONTROLLERABNORMAL4 | 3 | 0x0822
[7 empty] | OPERATINGMODE |  | OPERATINGMODE | 3 | 0x84F4
[7 empty] | OPTIMIZER_FAULT5 |  | OPTIMIZER_FAULT5 | 3 | 0x0821
[7 empty] | OUTPUTIMPEDANCEENHANCEMENTFREQUENCYPOINT |  | OUTPUTIMPEDANCEENHANCEMENTFREQUENCYPOINT | 3 | 0xA5A4
[7 empty] | OUTPUTMODE |  | OUTPUTMODE | 3 | 0xA411
[7 empty] | OUTPUT_DC_COMPONENT_OVERHIGH |  | OUTPUT_DC_COMPONENT_OVERHIGH | 3 | 0x07F8
[7 empty] | OUTPUT_OVERCURRENT |  | OUTPUT_OVERCURRENT | 3 | 0x07F7
[7 empty] | OVERFREQUENCYDERATING |  | OVERFREQUENCYDERATING | 3 | 0xA49F
[7 empty] | OVERFREQUENCYDERATINGCUTOFFFREQUENCY |  | OVERFREQUENCYDERATINGCUTOFFFREQUENCY | 3 | 0xA4A0
[7 empty] | OVERFREQUENCYDERATINGCUT_OFFPOWER |  | OVERFREQUENCYDERATINGCUT_OFFPOWER | 3 | 0xA4A1
[7 empty] | OVERFREQUENCYDERATINGEXITFREQUENCY |  | OVERFREQUENCYDERATINGEXITFREQUENCY | 3 | 0xA4A3
[7 empty] | OVERFREQUENCYDERATINGPOWERRECOVERYGRADIENT |  | OVERFREQUENCYDERATINGPOWERRECOVERYGRADIENT | 3 | 0xA4A4
[7 empty] | OVERTEMPERATURE |  | OVERTEMPERATURE | 3 | 0x080F
[7 empty] | PAKISTAN |  | PAKISTAN | 3 | 0x00F9
[7 empty] | PAKISTAN_MV480 |  | PAKISTAN_MV480 | 3 | 0x00FA
[7 empty] | PAKISTAN_MV800 |  | PAKISTAN_MV800 | 3 | 0x0094
[7 empty] | PANAMA_MV800 |  | PANAMA_MV800 | 3 | 0x010F
[7 empty] | PARALLELCOMMUNICATIONMODE |  | PARALLELCOMMUNICATIONMODE | 3 | 0xA961
[7 empty] | PASSIVE_ISLANDING |  | PASSIVE_ISLANDING | 3 | 0x0817
[7 empty] | PEAKACTIVEPOWER_OFTHECURRENTDAY |  | PEAKACTIVEPOWER_OFTHECURRENTDAY | 3 | 0x7D4E
[7 empty] | PERIPHERAL_PORT_SHORTCIRCUIT3 |  | PERIPHERAL_PORT_SHORTCIRCUIT3 | 3 | 0x081B
[7 empty] | PF_UCHARACTERISTICCURVE |  | PF_UCHARACTERISTICCURVE | 3 | 0x9CEF
[7 empty] | PHASE_AACTIVEPOWER |  | PHASE_AACTIVEPOWER | 3 | 0x910C
[7 empty] | PHASE_ADCCOMPONENT_DCI |  | PHASE_ADCCOMPONENT_DCI | 3 | 0x88DE
[7 empty] | PHASE_BACTIVEPOWER |  | PHASE_BACTIVEPOWER | 3 | 0x910E
[7 empty] | PHASE_BCURRENT |  | PHASE_BCURRENT | 3 | 0x90F5
[7 empty] | PHASE_BDCCOMPONENT_DCI |  | PHASE_BDCCOMPONENT_DCI | 3 | 0x88DF
[7 empty] | PHASE_BVOLTAGE |  | PHASE_BVOLTAGE | 3 | 0x90EF
[7 empty] | PHASE_CACTIVEPOWER |  | PHASE_CACTIVEPOWER | 3 | 0x9110
[7 empty] | PHASE_CCURRENT |  | PHASE_CCURRENT | 3 | 0x90F7
[7 empty] | PHASE_CDCCOMPONENT_DCI |  | PHASE_CDCCOMPONENT_DCI | 3 | 0x88E0
[7 empty] | PHASE_CVOLTAGE |  | PHASE_CVOLTAGE | 3 | 0x90F1
[7 empty] | PHASE_WIRE_SHORT_CIRCUITEDTO_PE |  | PHASE_WIRE_SHORT_CIRCUITEDTO_PE | 3 | 0x07EF
[7 empty] | PHYSICAL_LOCATION_LOCATING_PROGRESS |  | PHYSICAL_LOCATION_LOCATING_PROGRESS | 3 | 0x9153
[7 empty] | PIDOUTPUTVOLTAGE |  | PIDOUTPUTVOLTAGE | 3 | 0xA4C5
[7 empty] | PLANTACTIVEPOWERGRADIENT |  | PLANTACTIVEPOWERGRADIENT | 3 | 0xA42D
[7 empty] | PO12_3 |  | PO12_3 | 3 | 0x0047
[7 empty] | PO12_3_MV480 |  | PO12_3_MV480 | 3 | 0x003C
[7 empty] | PO12_3_MV800 |  | PO12_3_MV800 | 3 | 0x00C2
[7 empty] | POSITIVEACTIVEPOWER |  | POSITIVEACTIVEPOWER | 3 | 0x90FF
[7 empty] | POSITIVEBUSVOLTAGE |  | POSITIVEBUSVOLTAGE | 3 | 0x88E2
[7 empty] | POWERDECREASEADJUSTMENTPERIOD |  | POWERDECREASEADJUSTMENTPERIOD | 3 | 0xB93C
[7 empty] | POWERFACTOR |  | POWERFACTOR | 3 | 0x7D54
[7 empty] | POWERGRIDFAULTRECOVERYAUTOMATICSTARTUP |  | POWERGRIDFAULTRECOVERYAUTOMATICSTARTUP | 3 | 0xA44D
[7 empty] | POWERGRIDFAULTRECOVERYTIME |  | POWERGRIDFAULTRECOVERYTIME | 3 | 0xA478
[7 empty] | POWERGRIDLINE_AAND_BVOLTAGE |  | POWERGRIDLINE_AAND_BVOLTAGE | 3 | 0x7D42
[7 empty] | POWERGRIDPHASE_ACURRENT |  | POWERGRIDPHASE_ACURRENT | 3 | 0x7D48
[7 empty] | POWERGRIDPHASE_AVOLTAGE |  | POWERGRIDPHASE_AVOLTAGE | 3 | 0x7D45
[7 empty] | POWERGRIDPHASE_BCURRENT |  | POWERGRIDPHASE_BCURRENT | 3 | 0x7D4A
[7 empty] | POWERGRIDPHASE_BVOLTAGE |  | POWERGRIDPHASE_BVOLTAGE | 3 | 0x7D46
[7 empty] | POWERGRIDPHASE_CCURRENT |  | POWERGRIDPHASE_CCURRENT | 3 | 0x7D4C
[7 empty] | POWERGRIDPHASE_CVOLTAGE |  | POWERGRIDPHASE_CVOLTAGE | 3 | 0x7D47
[7 empty] | POWERGRIDRECONNECTIONFREQUENCYLOWERLIMIT |  | POWERGRIDRECONNECTIONFREQUENCYLOWERLIMIT | 3 | 0xA46B
[7 empty] | POWERGRIDRECONNECTIONFREQUENCYUPPERLIMIT |  | POWERGRIDRECONNECTIONFREQUENCYUPPERLIMIT | 3 | 0xA46A
[7 empty] | POWERGRIDRECONNECTIONVOLTAGEUPPERLIMIT |  | POWERGRIDRECONNECTIONVOLTAGEUPPERLIMIT | 3 | 0xA468
[7 empty] | POWERGRIDSTANDARDCODE |  | POWERGRIDSTANDARDCODE | 3 | 0xA410
[7 empty] | POWERGRIDVOLTAGEPROTECTIONSHIELDDURING_VRT |  | POWERGRIDVOLTAGEPROTECTIONSHIELDDURING_VRT | 3 | 0xA489
[7 empty] | POWERGRID_B_CLINEVOLTAGE |  | POWERGRID_B_CLINEVOLTAGE | 3 | 0x7D43
[7 empty] | POWERGRID_CALINEVOLTAGE |  | POWERGRID_CALINEVOLTAGE | 3 | 0x7D44
[7 empty] | POWERLIMIT0SHUTDOWN |  | POWERLIMIT0SHUTDOWN | 3 | 0xA44E
[7 empty] | POWERLIMITFORGRID_TIEDSITES |  | POWERLIMITFORGRID_TIEDSITES | 3 | 0xB7E7
[7 empty] | POWERPLANT_DCCAPACITY |  | POWERPLANT_DCCAPACITY | 3 | 0xB94B
[7 empty] | POWERSETTINGS |  | POWERSETTINGS | 3 | 0xA82C
[7 empty] | POWER_FACTOR |  | POWER_FACTOR | 3 | 0x0000
[7 empty] | POWER_GRID_RECONNECTION_VOLTAGE_LOWER_THRESHOLD |  | POWER_GRID_RECONNECTION_VOLTAGE_LOWER_THRESHOLD | 3 | 0xA469
[7 empty] | POWER_GRID_STANDARD_CODE_PROTOCOL_VERSION |  | POWER_GRID_STANDARD_CODE_PROTOCOL_VERSION | 3 | 0x759D
[7 empty] | POWER_INCREASE_THRESHOLD |  | POWER_INCREASE_THRESHOLD | 3 | 0xB93E
[7 empty] | POWER_ONFREQUENCYLOWERLIMITFORGRIDCONNECTION |  | POWER_ONFREQUENCYLOWERLIMITFORGRIDCONNECTION | 3 | 0xA467
[7 empty] | POWER_ONFREQUENCYUPPERLIMITFORGRIDCONNECTION |  | POWER_ONFREQUENCYUPPERLIMITFORGRIDCONNECTION | 3 | 0xA466
[7 empty] | POWER_ONSOFTSTARTTIMEDUETOPOWERGRIDFAULTS |  | POWER_ONSOFTSTARTTIMEDUETOPOWERGRIDFAULTS | 3 | 0xA474
[7 empty] | POWER_ONVOLTAGELOWERLIMITFORGRIDCONNECTION |  | POWER_ONVOLTAGELOWERLIMITFORGRIDCONNECTION | 3 | 0xA465
[7 empty] | POWER_ONVOLTAGEUPPERLIMITFORGRIDCONNECTION |  | POWER_ONVOLTAGEUPPERLIMITFORGRIDCONNECTION | 3 | 0xA464
[7 empty] | POWER_QUALITY_OPTIMIZATION_MODE |  | POWER_QUALITY_OPTIMIZATION_MODE | 3 | 0xA451
[7 empty] | PQMODE |  | PQMODE | 3 | 0xA43E
[7 empty] | PRC_024_EASTERN_LV208 |  | PRC_024_EASTERN_LV208 | 3 | 0x00D6
[7 empty] | PRC_024_EASTERN_LV240 |  | PRC_024_EASTERN_LV240 | 3 | 0x00D7
[7 empty] | PRC_024_EASTERN_MV480 |  | PRC_024_EASTERN_MV480 | 3 | 0x0038
[7 empty] | PRC_024_EASTERN_MV600 |  | PRC_024_EASTERN_MV600 | 3 | 0x0052
[7 empty] | PRC_024_EASTERN_MV800 |  | PRC_024_EASTERN_MV800 | 3 | 0x00BC
[7 empty] | PRC_024_ERCOT_LV208 |  | PRC_024_ERCOT_LV208 | 3 | 0x00DA
[7 empty] | PRC_024_ERCOT_LV240 |  | PRC_024_ERCOT_LV240 | 3 | 0x00DB
[7 empty] | PRC_024_ERCOT_MV480 |  | PRC_024_ERCOT_MV480 | 3 | 0x003B
[7 empty] | PRC_024_ERCOT_MV600 |  | PRC_024_ERCOT_MV600 | 3 | 0x0055
[7 empty] | PRC_024_ERCOT_MV800 |  | PRC_024_ERCOT_MV800 | 3 | 0x00BF
[7 empty] | PRC_024_QUEBEC_LV208 |  | PRC_024_QUEBEC_LV208 | 3 | 0x00DC
[7 empty] | PRC_024_QUEBEC_LV240 |  | PRC_024_QUEBEC_LV240 | 3 | 0x00DD
[7 empty] | PRC_024_QUEBEC_MV480 |  | PRC_024_QUEBEC_MV480 | 3 | 0x003A
[7 empty] | PRC_024_QUEBEC_MV600 |  | PRC_024_QUEBEC_MV600 | 3 | 0x0054
[7 empty] | PRC_024_QUEBEC_MV800 |  | PRC_024_QUEBEC_MV800 | 3 | 0x00BE
[7 empty] | PRC_024_WESTERN_LV208 |  | PRC_024_WESTERN_LV208 | 3 | 0x00D8
[7 empty] | PRC_024_WESTERN_LV240 |  | PRC_024_WESTERN_LV240 | 3 | 0x00D9
[7 empty] | PRC_024_WESTERN_MV480 |  | PRC_024_WESTERN_MV480 | 3 | 0x0039
[7 empty] | PRC_024_WESTERN_MV600 |  | PRC_024_WESTERN_MV600 | 3 | 0x0053
[7 empty] | PRC_024_WESTERN_MV800 |  | PRC_024_WESTERN_MV800 | 3 | 0x00BD
[7 empty] | PREDICTED_MPPTPOWER |  | PREDICTED_MPPTPOWER | 3 | 0xA448
[7 empty] | PRODUCTSALESAREA |  | PRODUCTSALESAREA | 3 | 0x7599
[7 empty] | PRODUCTSOFTWARE_ID |  | PRODUCTSOFTWARE_ID | 3 | 0x759B
[7 empty] | PRODUCT_SOFTWARE_VERSION_NUMBER |  | PRODUCT_SOFTWARE_VERSION_NUMBER | 3 | 0x759C
[7 empty] | PROTOCOLVERSION_MODBUS |  | PROTOCOLVERSION_MODBUS | 3 | 0x7574
[7 empty] | PV1CURRENT |  | PV1CURRENT | 3 | 0x7D11
[7 empty] | PV1VOLTAGE |  | PV1VOLTAGE | 3 | 0x7D10
[7 empty] | PV2CURRENT |  | PV2CURRENT | 3 | 0x7D13
[7 empty] | PV2VOLTAGE |  | PV2VOLTAGE | 3 | 0x7D12
[7 empty] | PV3CURRENT |  | PV3CURRENT | 3 | 0x7D15
[7 empty] | PV3VOLTAGE |  | PV3VOLTAGE | 3 | 0x7D14
[7 empty] | PV4CURRENT |  | PV4CURRENT | 3 | 0x7D17
[7 empty] | PV4VOLTAGE |  | PV4VOLTAGE | 3 | 0x7D16
[7 empty] | PV5CURRENT |  | PV5CURRENT | 3 | 0x7D19
[7 empty] | PV5VOLTAGE |  | PV5VOLTAGE | 3 | 0x7D18
[7 empty] | PV6CURRENT |  | PV6CURRENT | 3 | 0x7D1B
[7 empty] | PV6VOLTAGE |  | PV6VOLTAGE | 3 | 0x7D1A
[7 empty] | PV7CURRENT |  | PV7CURRENT | 3 | 0x7D1D
[7 empty] | PV7VOLTAGE |  | PV7VOLTAGE | 3 | 0x7D1C
[7 empty] | PV8CURRENT |  | PV8CURRENT | 3 | 0x7D1F
[7 empty] | PV8VOLTAGE |  | PV8VOLTAGE | 3 | 0x7D1E
[7 empty] | PVNEGATIVE_TO_GROUNDVOLTAGE |  | PVNEGATIVE_TO_GROUNDVOLTAGE | 3 | 0x7DBF
[7 empty] | PV_POWER |  | PV_POWER | 3 | 0x7D40
[7 empty] | PV_STRING_LOSS |  | PV_STRING_LOSS | 3 | 0x07DF
[7 empty] | P_P_VALUE_AT_POINT_1N |  | P_P_VALUE_AT_POINT_1N | 3 | 0x000A
[7 empty] | QUICKPOWER_ONANDPOWER_OFF |  | QUICKPOWER_ONANDPOWER_OFF | 3 | 0x9D0A
[7 empty] | Q_UCHARACTERISTICCURVEMINIMUM_PFLIMIT |  | Q_UCHARACTERISTICCURVEMINIMUM_PFLIMIT | 3 | 0x9DB7
[7 empty] | Q_UCHARACTERISTICCURVEMODE |  | Q_UCHARACTERISTICCURVEMODE | 3 | 0x9C65
[7 empty] | Q_USCHEDULING_EXIT_POWER_PERCENTAGE |  | Q_USCHEDULING_EXIT_POWER_PERCENTAGE | 3 | 0x9D06
[7 empty] | Q_USCHEDULING_TRIGGER_POWER_PERCENTAGE |  | Q_USCHEDULING_TRIGGER_POWER_PERCENTAGE | 3 | 0x9C66
[7 empty] | RATEDPOWER |  | RATEDPOWER | 3 | 0x7579
[7 empty] | RCDCURRENTLIMIT |  | RCDCURRENTLIMIT | 3 | 0xA498
[7 empty] | RD1699_661 |  | RD1699_661 | 3 | 0x000F
[7 empty] | RD1699_661_MV480 |  | RD1699_661_MV480 | 3 | 0x0010
[7 empty] | RD1699_661_MV800 |  | RD1699_661_MV800 | 3 | 0x00C1
[7 empty] | REACTIVEPOWER |  | REACTIVEPOWER | 3 | 0x90FB
[7 empty] | REACTIVEPOWERADJUSTMENTPERIOD |  | REACTIVEPOWERADJUSTMENTPERIOD | 3 | 0xB945
[7 empty] | REACTIVEPOWERADJUSTMENTSTATUS |  | REACTIVEPOWERADJUSTMENTSTATUS | 3 | 0x89E8
[7 empty] | REACTIVEPOWERADJUSTMENTTIME |  | REACTIVEPOWERADJUSTMENTTIME | 3 | 0x9CBC
[7 empty] | REACTIVEPOWERCOMPENSATION_Q_SLOWPRECISION |  | REACTIVEPOWERCOMPENSATION_Q_SLOWPRECISION | 3 | 0x9CBB
[7 empty] | REACTIVEPOWERCONTROLMODE |  | REACTIVEPOWERCONTROLMODE | 3 | 0xB941
[7 empty] | REACTIVEPOWERGRADIENT |  | REACTIVEPOWERGRADIENT | 3 | 0xA41F
[7 empty] | REACTIVEPOWERLIMITFORFAILUREPROTECTION_Q_SLOWPRECISION |  | REACTIVEPOWERLIMITFORFAILUREPROTECTION_Q_SLOWPRECISION | 3 | 0xA463
[7 empty] | REACTIVE_POWER |  | REACTIVE_POWER | 3 | 0x7D52
[7 empty] | REAL_TIMEDATAQUERYPROGRESS |  | REAL_TIMEDATAQUERYPROGRESS | 3 | 0x9155
[7 empty] | REAL_TIMEMAXIMUMREACTIVEPOWER_QMAXABSORBEDFROMTHEPOWERGRID |  | REAL_TIMEMAXIMUMREACTIVEPOWER_QMAXABSORBEDFROMTHEPOWERGRID | 3 | 0x7581
[7 empty] | REAL_TIMEMAXIMUMREACTIVEPOWER_QMAXFEDTOTHEPOWERGRID |  | REAL_TIMEMAXIMUMREACTIVEPOWER_QMAXFEDTOTHEPOWERGRID | 3 | 0x757F
[7 empty] | REGISTRATIONCODE |  | REGISTRATIONCODE | 3 | 0x79E0
[7 empty] | REG_0X0E |  | REG_0X0E | 3 | 0x000E
[7 empty] | REG_0X2B |  | REG_0X2B | 3 | 0x002B
[7 empty] | REG_0X41 |  | REG_0X41 | 3 | 0x0041
[7 empty] | REG_0X83 |  | REG_0X83 | 3 | 0x0083
[7 empty] | REG_0X87 |  | REG_0X87 | 3 | 0x0087
[7 empty] | REG_4GAPNMODE |  | REG_4GAPNMODE | 3 | 0xA9A7
[7 empty] | REG_4GAVERAGEDAILYTRAFFICUSAGE |  | REG_4GAVERAGEDAILYTRAFFICUSAGE | 3 | 0x8930
[7 empty] | REG_4GDEFAULT_APN |  | REG_4GDEFAULT_APN | 3 | 0xA9AA
[7 empty] | REG_4GDEFAULT_APNUSERNAME |  | REG_4GDEFAULT_APNUSERNAME | 3 | 0xA9CA
[7 empty] | REG_4GDEFAULT_IDENTITYAUTHENTICATIONTYPE |  | REG_4GDEFAULT_IDENTITYAUTHENTICATIONTYPE | 3 | 0xA9A9
[7 empty] | REG_4GIMEI |  | REG_4GIMEI | 3 | 0x89B6
[7 empty] | REG_4GIPADDRESS |  | REG_4GIPADDRESS | 3 | 0x89B2
[7 empty] | REG_4GMODULESTATUS |  | REG_4GMODULESTATUS | 3 | 0x89B1
[7 empty] | REG_4GMONTHLYUSEDTRAFFIC |  | REG_4GMONTHLYUSEDTRAFFIC | 3 | 0x892C
[7 empty] | REG_4GMONTHLY_REMAINING_TRAFFIC |  | REG_4GMONTHLY_REMAINING_TRAFFIC | 3 | 0x892E
[7 empty] | REG_4GNETWORKMODE |  | REG_4GNETWORKMODE | 3 | 0xA9A6
[7 empty] | REG_4GPINCHECKSTATUS |  | REG_4GPINCHECKSTATUS | 3 | 0x89C2
[7 empty] | REG_4GPINNUMBERINPUTTIMES |  | REG_4GPINNUMBERINPUTTIMES | 3 | 0x89C1
[7 empty] | REG_4GSIGNALSTRENGTH |  | REG_4GSIGNALSTRENGTH | 3 | 0x89C0
[7 empty] | REG_4GSUBNET_MASK |  | REG_4GSUBNET_MASK | 3 | 0x89B4
[7 empty] | REG_4GTRAFFICSTATUS |  | REG_4GTRAFFICSTATUS | 3 | 0x8932
[7 empty] | RELATIVE_POSITIONING_STATUS |  | RELATIVE_POSITIONING_STATUS | 3 | 0x9158
[7 empty] | REMOTECOMMUNICATION_SINGLE_NODEREMOTECOMMUNICATION |  | REMOTECOMMUNICATION_SINGLE_NODEREMOTECOMMUNICATION | 3 | 0x7D00
[7 empty] | REMOTEPOWERSCHEDULING |  | REMOTEPOWERSCHEDULING | 3 | 0xA41E
[7 empty] | REMOTESIGNAL_RUNNINGSTATUSMONITORING |  | REMOTESIGNAL_RUNNINGSTATUSMONITORING | 3 | 0x7D02
[7 empty] | REMOTESIGNAL_RUNNINGSTATUSPOWERPROCESSING |  | REMOTESIGNAL_RUNNINGSTATUSPOWERPROCESSING | 3 | 0x7D03
[7 empty] | REPLACETHETARGETMODEL |  | REPLACETHETARGETMODEL | 3 | 0xA41C
[7 empty] | RESTOREFACTORYSETTINGS |  | RESTOREFACTORYSETTINGS | 3 | 0xAFC8
[7 empty] | RESTRICTIONMODE |  | RESTRICTIONMODE | 3 | 0xB93B
[7 empty] | REVERSEACTIVEPOWER |  | REVERSEACTIVEPOWER | 3 | 0x9101
[7 empty] | RUNNINGSTATUS |  | RUNNINGSTATUS | 3 | 0x9186
[7 empty] | RUNNINGTIMEOFCAPACITORBANK |  | RUNNINGTIMEOFCAPACITORBANK | 3 | 0x88B8
[7 empty] | SA_RPPS_MV480 |  | SA_RPPS_MV480 | 3 | 0x005F
[7 empty] | SA_RPPS_MV800 |  | SA_RPPS_MV800 | 3 | 0x0086
[7 empty] | SCHEDULESERVER_COMMUNICATIONSTATUS |  | SCHEDULESERVER_COMMUNICATIONSTATUS | 3 | 0x9263
[7 empty] | SCHEDULESERVER_LATESTCONNECTIONSTATUS |  | SCHEDULESERVER_LATESTCONNECTIONSTATUS | 3 | 0x9264
[7 empty] | SCHEDULESERVER_LATESTCONNECTIONTIME |  | SCHEDULESERVER_LATESTCONNECTIONTIME | 3 | 0x9265
[7 empty] | SCIENCEAND_TECHNOLOGY_JINGKE_PROTOCOL_VERSION |  | SCIENCEAND_TECHNOLOGY_JINGKE_PROTOCOL_VERSION | 3 | 0xAC47
[7 empty] | SECURITYMODE |  | SECURITYMODE | 3 | 0xB834
[7 empty] | SERIALNUMBEROFTHELATESTACTIVEALARM |  | SERIALNUMBEROFTHELATESTACTIVEALARM | 3 | 0x7DAC
[7 empty] | SERIAL_NUMBER |  | SERIAL_NUMBER | 3 | 0x753F
[7 empty] | SETTINGTHE_ACCUMULATED_ENERGY_YIELD |  | SETTINGTHE_ACCUMULATED_ENERGY_YIELD | 3 | 0xB829
[7 empty] | SHORT_TERMPOWERGRIDINTERRUPTIONANDQUICKSTARTUP |  | SHORT_TERMPOWERGRIDINTERRUPTIONANDQUICKSTARTUP | 3 | 0xA484
[7 empty] | SHUTDOWNTIME |  | SHUTDOWNTIME | 3 | 0x7D5D
[7 empty] | SILENCEFLAG |  | SILENCEFLAG | 3 | 0x9278
[7 empty] | SIX_LEVELOVERFREQUENCYPROTECTIONTIME |  | SIX_LEVELOVERFREQUENCYPROTECTIONTIME | 3 | 0xA569
[7 empty] | SMART_I_V_V_DIAGNOSIS_AUTHORIZATION_FUNCTION |  | SMART_I_V_V_DIAGNOSIS_AUTHORIZATION_FUNCTION | 3 | 0x8940
[7 empty] | SMART_I_V_V_DIAGNOSIS_LICENSEEXPIRATIONDATE |  | SMART_I_V_V_DIAGNOSIS_LICENSEEXPIRATIONDATE | 3 | 0x8943
[7 empty] | SMART_I_V_V_DIAGNOSIS_LICENSE_STATUS |  | SMART_I_V_V_DIAGNOSIS_LICENSE_STATUS | 3 | 0x8942
[7 empty] | SOFTWAREVERSION |  | SOFTWAREVERSION | 3 | 0x7562
[7 empty] | SOUTH_KOREA |  | SOUTH_KOREA | 3 | 0x002F
[7 empty] | STAROUTERCONNECTIONSTATUS |  | STAROUTERCONNECTIONSTATUS | 3 | 0x8935
[7 empty] | STAROUTERCONNECTIONTIME |  | STAROUTERCONNECTIONTIME | 3 | 0x8934
[7 empty] | START_UPCURRENT |  | START_UPCURRENT | 3 | 0xAA71
[7 empty] | START_UPTIME |  | START_UPTIME | 3 | 0x7D5B
[7 empty] | STATISTICALTIMEOFTHECURRENTENERGYYIELD |  | STATISTICALTIMEOFTHECURRENTENERGYYIELD | 3 | 0x7D6E
[7 empty] | STATISTICALTIMEOFTHEPREVIOUSMONTH |  | STATISTICALTIMEOFTHEPREVIOUSMONTH | 3 | 0x7DA4
[7 empty] | STAWIRELESS_ROUTING_ACCESS_SIGNAL_STRENGTH |  | STAWIRELESS_ROUTING_ACCESS_SIGNAL_STRENGTH | 3 | 0x8920
[7 empty] | STAWIRELESS_ROUTING_ENCRYPTION_MODE |  | STAWIRELESS_ROUTING_ENCRYPTION_MODE | 3 | 0xA89C
[7 empty] | STAWLANLISTSCANNINGSTATUS |  | STAWLANLISTSCANNINGSTATUS | 3 | 0x8921
[7 empty] | STENT_SYSTEM_STATUS |  | STENT_SYSTEM_STATUS | 3 | 0x84D0
[7 empty] | STRINGCONNECTIONMODE |  | STRINGCONNECTIONMODE | 3 | 0xA441
[7 empty] | STRINGMONITORING_LICENSESTATUS |  | STRINGMONITORING_LICENSESTATUS | 3 | 0x8995
[7 empty] | STRING_1ACCESSSTATUS |  | STRING_1ACCESSSTATUS | 3 | 0x7E2C
[7 empty] | STRING_2ACCESSSTATUS |  | STRING_2ACCESSSTATUS | 3 | 0x7E2D
[7 empty] | STRING_3ACCESSSTATUS |  | STRING_3ACCESSSTATUS | 3 | 0x7E2E
[7 empty] | STRING_4ACCESSSTATUS |  | STRING_4ACCESSSTATUS | 3 | 0x7E2F
[7 empty] | STRING_5ACCESSSTATUS |  | STRING_5ACCESSSTATUS | 3 | 0x7E30
[7 empty] | STRING_7ACCESSSTATUS |  | STRING_7ACCESSSTATUS | 3 | 0x7E32
[7 empty] | STRING_8ACCESSSTATUS |  | STRING_8ACCESSSTATUS | 3 | 0x7E33
[7 empty] | STRING_CURRENT_BACKFEED |  | STRING_CURRENT_BACKFEED | 3 | 0x07DC
[7 empty] | STRING_MONITORING_LICENSE_EXPIRATION_TIME |  | STRING_MONITORING_LICENSE_EXPIRATION_TIME | 3 | 0x8996
[7 empty] | STRING_REVERSE_CONNECTION |  | STRING_REVERSE_CONNECTION | 3 | 0x07DB
[7 empty] | SUBDEVICEPRESENCEFLAG |  | SUBDEVICEPRESENCEFLAG | 3 | 0x7601
[7 empty] | SUBDEVICE_SUPPORT_ID |  | SUBDEVICE_SUPPORT_ID | 3 | 0x75FF
[7 empty] | SUBPACKAGE_2INFORMATION |  | SUBPACKAGE_2INFORMATION | 3 | 0x75A2
[7 empty] | SUBPACKAGE_4INFORMATION |  | SUBPACKAGE_4INFORMATION | 3 | 0x75A6
[7 empty] | SUBPACKAGE_5INFORMATION |  | SUBPACKAGE_5INFORMATION | 3 | 0x75A8
[7 empty] | SUBPACKAGE_7INFORMATION |  | SUBPACKAGE_7INFORMATION | 3 | 0x75AC
[7 empty] | SUBPACKAGE_8INFORMATION |  | SUBPACKAGE_8INFORMATION | 3 | 0x75AE
[7 empty] | SUBPACKAGE_9INFORMATION |  | SUBPACKAGE_9INFORMATION | 3 | 0x75B0
[7 empty] | SUPPORT10CUSTOM_FAULT_STATUS |  | SUPPORT10CUSTOM_FAULT_STATUS | 3 | 0x852E
[7 empty] | SUPPORT10GENERAL_FAULT_STATUS |  | SUPPORT10GENERAL_FAULT_STATUS | 3 | 0x852D
[7 empty] | SUPPORT11CUSTOM_FAULT_STATUS |  | SUPPORT11CUSTOM_FAULT_STATUS | 3 | 0x8530
[7 empty] | SUPPORT11GENERAL_FAULT_STATUS |  | SUPPORT11GENERAL_FAULT_STATUS | 3 | 0x852F
[7 empty] | SUPPORT12CUSTOM_FAULT_STATUS |  | SUPPORT12CUSTOM_FAULT_STATUS | 3 | 0x8532
[7 empty] | SUPPORT12GENERAL_FAULT_STATUS |  | SUPPORT12GENERAL_FAULT_STATUS | 3 | 0x8531
[7 empty] | SUPPORT13CUSTOM_FAULT_STATUS |  | SUPPORT13CUSTOM_FAULT_STATUS | 3 | 0x8534
[7 empty] | SUPPORT13GENERAL_FAULT_STATUS |  | SUPPORT13GENERAL_FAULT_STATUS | 3 | 0x8533
[7 empty] | SUPPORT14CUSTOM_FAULT_STATUS |  | SUPPORT14CUSTOM_FAULT_STATUS | 3 | 0x8536
[7 empty] | SUPPORT14GENERAL_FAULT_STATUS |  | SUPPORT14GENERAL_FAULT_STATUS | 3 | 0x8535
[7 empty] | SUPPORT15CUSTOM_FAULT_STATUS |  | SUPPORT15CUSTOM_FAULT_STATUS | 3 | 0x8538
[7 empty] | SUPPORT15GENERAL_FAULT_STATUS |  | SUPPORT15GENERAL_FAULT_STATUS | 3 | 0x8537
[7 empty] | SUPPORT16CUSTOM_FAULT_STATUS |  | SUPPORT16CUSTOM_FAULT_STATUS | 3 | 0x853A
[7 empty] | SUPPORT16GENERAL_FAULT_STATUS |  | SUPPORT16GENERAL_FAULT_STATUS | 3 | 0x8539
[7 empty] | SUPPORTACCESSSTATUS |  | SUPPORTACCESSSTATUS | 3 | 0x84F6
[7 empty] | SUPPORT_1GENERAL_FAULT_STATUS |  | SUPPORT_1GENERAL_FAULT_STATUS | 3 | 0x851B
[7 empty] | SUPPORT_1USER_DEFINEDFAULTSTATUS |  | SUPPORT_1USER_DEFINEDFAULTSTATUS | 3 | 0x851C
[7 empty] | SUPPORT_2CUSTOM_FAULT_STATUS |  | SUPPORT_2CUSTOM_FAULT_STATUS | 3 | 0x851E
[7 empty] | SUPPORT_2GENERAL_FAULT_STATUS |  | SUPPORT_2GENERAL_FAULT_STATUS | 3 | 0x851D
[7 empty] | SUPPORT_3GENERAL_FAULT_STATUS |  | SUPPORT_3GENERAL_FAULT_STATUS | 3 | 0x851F
[7 empty] | SUPPORT_3USER_DEFINEDFAULTSTATUS |  | SUPPORT_3USER_DEFINEDFAULTSTATUS | 3 | 0x8520
[7 empty] | SUPPORT_4CUSTOM_FAULT_STATUS |  | SUPPORT_4CUSTOM_FAULT_STATUS | 3 | 0x8522
[7 empty] | SUPPORT_4GENERAL_FAULT_STATUS |  | SUPPORT_4GENERAL_FAULT_STATUS | 3 | 0x8521
[7 empty] | SUPPORT_5CUSTOM_FAULT_STATUS |  | SUPPORT_5CUSTOM_FAULT_STATUS | 3 | 0x8524
[7 empty] | SUPPORT_5GENERAL_FAULT_STATUS |  | SUPPORT_5GENERAL_FAULT_STATUS | 3 | 0x8523
[7 empty] | SUPPORT_6CUSTOM_FAULT_STATUS |  | SUPPORT_6CUSTOM_FAULT_STATUS | 3 | 0x8526
[7 empty] | SUPPORT_6GENERAL_FAULT_STATUS |  | SUPPORT_6GENERAL_FAULT_STATUS | 3 | 0x8525
[7 empty] | SUPPORT_7CUSTOM_FAULT_STATUS |  | SUPPORT_7CUSTOM_FAULT_STATUS | 3 | 0x8528
[7 empty] | SUPPORT_7GENERAL_FAULT_STATUS |  | SUPPORT_7GENERAL_FAULT_STATUS | 3 | 0x8527
[7 empty] | SUPPORT_8CUSTOM_FAULT_STATUS |  | SUPPORT_8CUSTOM_FAULT_STATUS | 3 | 0x852A
[7 empty] | SUPPORT_8GENERAL_FAULT_STATUS |  | SUPPORT_8GENERAL_FAULT_STATUS | 3 | 0x8529
[7 empty] | SUPPORT_9CUSTOM_FAULT_STATUS |  | SUPPORT_9CUSTOM_FAULT_STATUS | 3 | 0x852C
[7 empty] | SUPPORT_9GENERAL_FAULT_STATUS |  | SUPPORT_9GENERAL_FAULT_STATUS | 3 | 0x852B
[7 empty] | SUPPORT_FAULT_CLEARANCE |  | SUPPORT_FAULT_CLEARANCE | 3 | 0xAC32
[7 empty] | SUPPORT_SYSTEM_TYPE |  | SUPPORT_SYSTEM_TYPE | 3 | 0x84F3
[7 empty] | TAIPOWER |  | TAIPOWER | 3 | 0x00CB
[7 empty] | TAIPOWER_MV480 |  | TAIPOWER_MV480 | 3 | 0x00CC
[7 empty] | TAIPOWER_MV800 |  | TAIPOWER_MV800 | 3 | 0x00CD
[7 empty] | TAI_MEA_MV480 |  | TAI_MEA_MV480 | 3 | 0x0023
[7 empty] | TAI_MEA_MV800 |  | TAI_MEA_MV800 | 3 | 0x00F8
[7 empty] | TAI_PEA_MV480 |  | TAI_PEA_MV480 | 3 | 0x0022
[7 empty] | TAI_PEA_MV800 |  | TAI_PEA_MV800 | 3 | 0x0082
[7 empty] | TARGETPOWERFACTOR |  | TARGETPOWERFACTOR | 3 | 0xB944
[7 empty] | TEN_MINUTEOVERVOLTAGEPROTECTIONTHRESHOLD |  | TEN_MINUTEOVERVOLTAGEPROTECTIONTHRESHOLD | 3 | 0xA532
[7 empty] | TEN_MINUTEOVERVOLTAGEPROTECTIONTIME |  | TEN_MINUTEOVERVOLTAGEPROTECTIONTIME | 3 | 0xA533
[7 empty] | TEN_MINUTEUNDERVOLTAGEPROTECTIONTIME |  | TEN_MINUTEUNDERVOLTAGEPROTECTIONTIME | 3 | 0xA530
[7 empty] | THIRD_PARTYLABELING_SN |  | THIRD_PARTYLABELING_SN | 3 | 0x75EF
[7 empty] | THIRD_PARTYLABEL_MANUFACTURERMODEL |  | THIRD_PARTYLABEL_MANUFACTURERMODEL | 3 | 0x75F9
[7 empty] | TILTANGLE_10SAMPLING |  | TILTANGLE_10SAMPLING | 3 | 0x84E4
[7 empty] | TILTANGLE_11SAMPLING |  | TILTANGLE_11SAMPLING | 3 | 0x84E6
[7 empty] | TILTANGLE_12SAMPLING |  | TILTANGLE_12SAMPLING | 3 | 0x84E8
[7 empty] | TILTANGLE_13SAMPLING |  | TILTANGLE_13SAMPLING | 3 | 0x84EA
[7 empty] | TILTANGLE_14SAMPLING |  | TILTANGLE_14SAMPLING | 3 | 0x84EC
[7 empty] | TILTANGLE_15SAMPLING |  | TILTANGLE_15SAMPLING | 3 | 0x84EE
[7 empty] | TILTANGLE_16SAMPLING |  | TILTANGLE_16SAMPLING | 3 | 0x84F0
[7 empty] | TILTANGLE_1SAMPLING |  | TILTANGLE_1SAMPLING | 3 | 0x84D2
[7 empty] | TILTANGLE_2SAMPLING |  | TILTANGLE_2SAMPLING | 3 | 0x84D4
[7 empty] | TILTANGLE_3SAMPLING |  | TILTANGLE_3SAMPLING | 3 | 0x84D6
[7 empty] | TILTANGLE_4SAMPLING |  | TILTANGLE_4SAMPLING | 3 | 0x84D8
[7 empty] | TILTANGLE_5SAMPLING |  | TILTANGLE_5SAMPLING | 3 | 0x84DA
[7 empty] | TILTANGLE_6SAMPLING |  | TILTANGLE_6SAMPLING | 3 | 0x84DC
[7 empty] | TILTANGLE_7SAMPLING |  | TILTANGLE_7SAMPLING | 3 | 0x84DE
[7 empty] | TILTANGLE_8SAMPLING |  | TILTANGLE_8SAMPLING | 3 | 0x84E0
[7 empty] | TILTANGLE_9SAMPLING |  | TILTANGLE_9SAMPLING | 3 | 0x84E2
[7 empty] | TIMEFORDETERMININGSHORT_TERMPOWERGRIDINTERRUPTION |  | TIMEFORDETERMININGSHORT_TERMPOWERGRIDINTERRUPTION | 3 | 0xA479
[7 empty] | TOTALBUSVOLTAGE |  | TOTALBUSVOLTAGE | 3 | 0x7DB0
[7 empty] | TOTALNUMBEROFOPTIMIZERS |  | TOTALNUMBEROFOPTIMIZERS | 3 | 0x9150
[7 empty] | TOTALNUMBEROFSTENTS |  | TOTALNUMBEROFSTENTS | 3 | 0x84F5
[7 empty] | TOTALRATEDCAPACITYOFGRID_TIEDINVERTERS |  | TOTALRATEDCAPACITYOFGRID_TIEDINVERTERS | 3 | 0x925E
[7 empty] | TOTAL_DCENERGYYIELDOF_MPPT1 |  | TOTAL_DCENERGYYIELDOF_MPPT1 | 3 | 0x7DD4
[7 empty] | TOTAL_DCENERGYYIELDOF_MPPT2 |  | TOTAL_DCENERGYYIELDOF_MPPT2 | 3 | 0x7DD6
[7 empty] | TOTAL_DC_INPUT_POWER |  | TOTAL_DC_INPUT_POWER | 3 | 0x7D6C
[7 empty] | TRACKINGSYSTEMCONTROLLER |  | TRACKINGSYSTEMCONTROLLER | 3 | 0x84F2
[7 empty] | TRANSIENT_AC_OVERVOLTAGE |  | TRANSIENT_AC_OVERVOLTAGE | 3 | 0x0818
[7 empty] | TRIGGERINGFREQUENCY_OFOVERFREQUENCYDERATING |  | TRIGGERINGFREQUENCY_OFOVERFREQUENCYDERATING | 3 | 0xA4A2
[7 empty] | TUNISIA |  | TUNISIA | 3 | 0x00A6
[7 empty] | TUNISIA_MV480 |  | TUNISIA_MV480 | 3 | 0x00A7
[7 empty] | TUNISIA_MV800 |  | TUNISIA_MV800 | 3 | 0x00A8
[7 empty] | TYPE |  | TYPE | 3 | 0x9222
[7 empty] | UNDERFREQUENCY_POWER_INCREASE |  | UNDERFREQUENCY_POWER_INCREASE | 3 | 0xA4A7
[7 empty] | UNDERFREQUENCY_POWER_INCREASE_EFFECTIVE_DELAY_TIME |  | UNDERFREQUENCY_POWER_INCREASE_EFFECTIVE_DELAY_TIME | 3 | 0xA5BD
[7 empty] | UNDERFREQUENCY_POWER_INCREASE_EXIT_FREQUENCY |  | UNDERFREQUENCY_POWER_INCREASE_EXIT_FREQUENCY | 3 | 0xA4C3
[7 empty] | UNDERFREQUENCY_POWER_INCREASE_RECOVERY_GRADIENT |  | UNDERFREQUENCY_POWER_INCREASE_RECOVERY_GRADIENT | 3 | 0xA4A8
[7 empty] | UNDERFREQUENCY_POWER_INCREASE_TRIGGERING_FREQUENCY |  | UNDERFREQUENCY_POWER_INCREASE_TRIGGERING_FREQUENCY | 3 | 0xA4C2
[7 empty] | UNDERVOLTAGEPROTECTIONTHRESHOLDFOR10MINUTES |  | UNDERVOLTAGEPROTECTIONTHRESHOLDFOR10MINUTES | 3 | 0xA52F
[7 empty] | UNIQUE_ID_1OFTHESOUTHBOUNDSOFTWARE |  | UNIQUE_ID_1OFTHESOUTHBOUNDSOFTWARE | 3 | 0x7725
[7 empty] | UNIQUE_ID_2OFTHESOUTHBOUNDSOFTWARE |  | UNIQUE_ID_2OFTHESOUTHBOUNDSOFTWARE | 3 | 0x7726
[7 empty] | UNIQUE_ID_OFTHESOFTWARE |  | UNIQUE_ID_OFTHESOFTWARE | 3 | 0x759E
[7 empty] | UNSTABLE_GRID_FREQUENCY |  | UNSTABLE_GRID_FREQUENCY | 3 | 0x07F6
[7 empty] | UPGRADESTATUS_ID |  | UPGRADESTATUS_ID | 3 | 0x8CC1
[7 empty] | UPGRADE_FAILED_OR_VERSION_MISMATCH |  | UPGRADE_FAILED_OR_VERSION_MISMATCH | 3 | 0x0811
[7 empty] | UPGRADE_STATUS |  | UPGRADE_STATUS | 3 | 0x9279
[7 empty] | UTE_C_15_712_1B |  | UTE_C_15_712_1B | 3 | 0x0003
[7 empty] | UTE_C_15_712_1_MV480 |  | UTE_C_15_712_1_MV480 | 3 | 0x0021
[7 empty] | UTE_C_15_712_1_MV800 |  | UTE_C_15_712_1_MV800 | 3 | 0x007E
[7 empty] | VDE_0126_1_1_BU |  | VDE_0126_1_1_BU | 3 | 0x0005
[7 empty] | VDE_0126_1_1_GRA |  | VDE_0126_1_1_GRA | 3 | 0x0006
[7 empty] | VDE_0126_1_1_GRB |  | VDE_0126_1_1_GRB | 3 | 0x0007
[7 empty] | VDE_AR_N4110 |  | VDE_AR_N4110 | 3 | 0x010C
[7 empty] | VDE_AR_N4110_MV480 |  | VDE_AR_N4110_MV480 | 3 | 0x010D
[7 empty] | VDE_AR_N4110_MV800 |  | VDE_AR_N4110_MV800 | 3 | 0x010E
[7 empty] | VDE_AR_N4120_HV |  | VDE_AR_N4120_HV | 3 | 0x00B4
[7 empty] | VDE_AR_N4120_HV480 |  | VDE_AR_N4120_HV480 | 3 | 0x00B5
[7 empty] | VDE_AR_N4120_HV800 |  | VDE_AR_N4120_HV800 | 3 | 0x00B6
[7 empty] | VOLTAGELEVEL |  | VOLTAGELEVEL | 3 | 0xA412
[7 empty] | VOLTAGERISESUPPRESSION |  | VOLTAGERISESUPPRESSION | 3 | 0xA49A
[7 empty] | VOLTAGERISESUPPRESSIONACTIVEDERATINGTHRESHOLD |  | VOLTAGERISESUPPRESSIONACTIVEDERATINGTHRESHOLD | 3 | 0xA49C
[7 empty] | VOLTAGERISESUPPRESSIONREACTIVEPOWERADJUSTMENTPOINT |  | VOLTAGERISESUPPRESSIONREACTIVEPOWERADJUSTMENTPOINT | 3 | 0xA49B
[7 empty] | VOLTAGEUNBALANCEPROTECTIONTHRESHOLD |  | VOLTAGEUNBALANCEPROTECTIONTHRESHOLD | 3 | 0xA472
[7 empty] | VRTACTIVECURRENTLIMITINGPERCENTAGE |  | VRTACTIVECURRENTLIMITINGPERCENTAGE | 3 | 0xA48C
[7 empty] | VRTACTIVEPOWERRECOVERYGRADIENT |  | VRTACTIVEPOWERRECOVERYGRADIENT | 3 | 0xA48D
[7 empty] | WORKINGMODEMASK |  | WORKINGMODEMASK | 3 | 0x84F8
[7 empty] | ZAMBIA |  | ZAMBIA | 3 | 0x0062
[7 empty] | ZAMBIA_MV480 |  | ZAMBIA_MV480 | 3 | 0x0063
[7 empty] | ZAMBIA_MV800 |  | ZAMBIA_MV800 | 3 | 0x0098