## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Sungrow
프로토콜 버전 | V1.1.53
설비 타입 | inverter
MPPT | 16
String | 32
String 모니터링 | Yes
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | Sungrow-PV_ti_20230117_communication-protocol_v1.1.53_en.pdf
추출 일시 | 2026-04-09 12:07
H01 매칭 | 82/82
DER 매칭 | 33/33
추출 레지스터 | 249
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | LOW_SYSTEM_INSULATION_RESISTANCE | 0x0027 | 03 | U16 |  | RO |  | Low System Insulation Resistance
2 | SERIAL_NUMBER | 0x137E | 03 | U16 |  | RO |  | SN ¦ Data type :UTF-8
3 | Device typecode | 0x1388 | 03 | U16 |  | RO |  | See Appendix 5
4 | NOMINAL_ACTIVEPOWER | 0x1389 | 03 | U16 | kW 0.1 | RO |  | Nominalactive power
5 | OUTPUT_TYPE | 0x138A | 03 | U16 |  | RO |  | Output type
6 | Daily poweryields | 0x138B | 03 | U16 | kWh 0.1 | RO
7 | Total poweryields | 0x138C | 03 | U32 | kWh | RO | cumulative_energy
8 | TOTAL_RUNNING_TIME | 0x138E | 03 | U32 |  | RO |  | Total runningtime
9 | Powerlimitationswitch | 0x138F | 03 | U16 |  | RO
10 | Internaltemperature | 0x1390 | 03 | S16 | ℃ 0.1 | RO
11 | TOTAL_APPARENTPOWER | 0x1391 | 03 | U32 | VA | RO |  | Totalapparentpower ¦ Valid for inverters:SG5KTL-MTSG6KTL-MTSG8KTL-MSG10KTL-MSG10KTL-MTSG12KTL-MSG15KTL-MSG17KTL-MSG20KTL-MRT SeriesSG33K3JSG36KTL-MSG40KTL-MSG50KTLSG50KTL-MSG60KTLSG60KTL-MSG60KU-MSG80KTLSG80KTL-MSG111HVSG125HVSG125HV-20SG33CXSG40CXSG50CXSG110CX
12 | NOMINAL_REACTIVEPOWER | 0x13B9 | 03 | U16 |  | RO |  | Nominalreactivepower
13 | ARRAY_INSULATIONRESISTANCE | 0x13CF | 03 | U16 |  | RO |  | Arrayinsulationresistance
14 | DAILY_RUNNING_TIME | 0x13F9 | 03 | U16 |  | RO |  | Daily runningtime
15 | PRESENT_COUNTRY | 0x13FA | 03 | U16 |  | RO |  | Presentcountry
16 | BUS_VOLTAGE | 0x141B | 03 | U16 | V 0.1 | RO |  | Bus voltage
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Total run state bit BIT17 | 0x000B | 03 | U16 |  | RO
2 | Total run bit (device is grid-connected running) | 0x0011 | 03 | U16 |  | RO
3 | Total fault bit (device is infault stop state) | 0x0012 | 03 | U16 |  | RO
4 | The inverter is in the initial power-on standby state. | 0x1200 | 03 | U16 |  | RO
5 | INVERTER_MODE | 0x13AE | 03 | U16 |  | RO | inverter_status | Data of address 5039 - 5045 areadditional
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Total fault state bit BIT18 | 0x0009 | 03 | U16 |  | RO
2 | ALARM_RUN | 0x000A | 03 | U16 |  | RO |  | Total run state bit BIT17
3 | COMMUNICATE_FAULT | 0x000D | 03 | U16 |  | RO |  | Total fault state bit BIT18
4 | Inverter Parallel Communication Alarm | 0x004B | 03 | U16 |  | RO
5 | Reverse Connection Alarm of the Meter/CT | 0x0054 | 03 | U16 |  | RO
6 | ELECTRIC_ARC_FAULT | 0x0058 | 03 | U16 |  | RO |  | Electric Arc Fault
7 | GROUNDING_CABLE_FAULT | 0x006A | 03 | U16 |  | RO |  | Grounding Cable Fault
8 | Default: 0-1100If country isGermany，range is 0-1000 | 0x013E | 03 | U16 |  | RO
9 | METER_COMMUNICATION_ABNORMALALARM | 0x0202 | 03 | U16 |  | RO |  | Meter Communication Abnormal Alarm
10 | PV Grounding Fault | 0x0640 | 03 | U16 |  | RO
11 | System Hardware Fault | 0x0650 | 03 | U16 |  | RO
12 | FAULT_ALARM_TIME_YEAR | 0x13AF | 03 | U16 |  | RO |  | Fault/Alarm time and ¦ Fault/Alarm code (5039 - 5045)are valid only when the devicework state is fault (0x5500) oralarm (0x9100).Except SG5.5RS-JP ,SG0.7/1.0/1/5/2.0/2.5/3.0RS-S,SG3.0/3.6/4.0/5.0/6.0RS,SG5.0RS-ADA, SG8.0/9.0/10RS
13 | FAULT_ALARM_TIME_MONTH | 0x13B0 | 03 | U16 |  | RO |  | Fault/Alarmtime: Month
14 | FAULT_ALARM_TIME_DAY | 0x13B1 | 03 | U16 |  | RO |  | Fault/Alarmtime: Day
15 | FAULT_ALARM_TIME_HOUR | 0x13B2 | 03 | U16 |  | RO |  | Fault/Alarmtime: Hour
16 | FAULT_ALARM_TIME_MINUTE | 0x13B3 | 03 | U16 |  | RO |  | Fault/Alarmtime: Minute
17 | FAULT_ALARM_TIME_SECOND | 0x13B4 | 03 | U16 |  | RO |  | Fault/Alarmtime: Second
18 | FAULT_ALARM_CODE_1 | 0x13B5 | 03 | U16 |  | RO |  | Fault/Alarmcode 1
19 | PID_ALARM_CODE | 0x141F | 03 | U16 |  | RO |  | 432:PID resistanceabnormal433:PID function
20 | Default: 0-55(Germany, Australia:0-50) | 0x2430 | 03 | U16 |  | RO |  | 1
21 | Default: 0-66(Germany, Australia:0-60) | 0x2431 | 03 | U16 |  | RO |  | 1
22 | Default: 0-88(Germany, Australia:0-80) | 0x2432 | 03 | U16 |  | RO |  | 2;1
23 | Default: 0-110(Germany, Belgium,Australia:0-100) | 0x2433 | 03 | U16 |  | RO |  | 2;1
24 | Default: 0-132(Germany, Australia:0-120) | 0x2434 | 03 | U16 |  | RO |  | 2;1
25 | Default: 0-165(Germany, Australia:0-150) | 0x2435 | 03 | U16 |  | RO |  | 2
26 | Default: 0-187(Germany, Australia:0-170) | 0x2436 | 03 | U16 |  | RO |  | 2
27 | Default: 0-220(Germany, Australia:0-200) | 0x2437 | 03 | U16 |  | RO |  | 2
28 | Default: 0-242(Germany, Australia:0-220) | 0x2438 | 03 | U16 |  | RO |  | 2
29 | Default: 0-275(Germany, Australia:0-250 | 0x2439 | 03 | U16 |  | RO |  | 2
30 | Default: 0-253(Germany, Australia:0-230) | 0x243B | 03 | U16 |  | RO |  | 2
31 | Default: 0-77(Germany:0-70; Australia: 0-69.99) | 0x243C | 03 | U16 |  | RO |  | 2;1
32 | Default: 0-1100(Germany,Belgium,Australia:0-1000) | 0x243D | 03 | U16 |  | RO |  | 1
33 | Default: 0-55(Germany, Australia:0-50) | 0x2440 | 03 | U16 |  | RO |  | 1
34 | Default: 0-66(Germany, Australia:0-60) | 0x2441 | 03 | U16 |  | RO |  | 1
35 | Default: 0-88(Germany, Australia:0-80) | 0x2442 | 03 | U16 |  | RO |  | 2;1
36 | Default: 0-110(Germany, Belgium,Australia:0-100) | 0x2443 | 03 | U16 |  | RO |  | 2;1
37 | Default: 0-132(Germany, Australia: | 0x2444 | 03 | U16 |  | RO |  | 2;1
38 | Default: 0-165(Germany, Australia:0-150) | 0x2445 | 03 | U16 |  | RO
39 | Default: 0-187(Germany, Australia:0-170) | 0x2446 | 03 | U16 |  | RO
40 | Default: 0-220(Germany, Australia:0-200) | 0x2447 | 03 | U16 |  | RO
41 | Default: 0-275(Germany, Australia:0-250 | 0x2449 | 03 | U16 |  | RO
42 | Default: 0-253(Germany, Australia:0-230) | 0x244B | 03 | U16 |  | RO
43 | Default: 0-77(Germany:0-70; Australia: 0-69.99) | 0x244C | 03 | U16 |  | RO |  | 2;1
44 | Default: 0-1100(Germany,Belgium,Australia:0-1000) | 0x244D | 03 | U16 |  | RO |  | 1
45 | Communicate fault | 0x2500 | 03 | U16 |  | RO
46 | FAULT | 0x5500 | 03 | U16 |  | RO |  | If a fault occurs, inverter will automatically stopoperation, and disconnect the AC relay. The faultinformation will be displayed in the app. Once thefault is removed in recovery time, inverter willautomatically resume running.
47 | Warning information is detected. | 0x9100 | 03 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 82/82
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | PDF_PHASE | O | 0x139B | L1_VOLTAGE | U16 | V | 0.1 | 상전압 사용
2 | s_voltage | PDF_PHASE | O | 0x139C | L2_VOLTAGE | U16 | V | 0.1 | 상전압 사용
3 | t_voltage | PDF_PHASE | O | 0x139D | L3_VOLTAGE | U16 | V | 0.1 | 상전압 사용
4 | r_current | PDF_PHASE | O | 0x139E | L1_CURRENT | U16 | A | 0.1 | 상전압 사용
5 | s_current | PDF_ALIAS_R | O | 0x139E | L1_CURRENT | U16 | A | 0.1 | three phase — r_current alias
6 | t_current | PDF_PHASE | O | 0x13A0 | L3_CURRENT | U16 | A | 0.1 | 상전압 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x1399 | PV_POWER | U32
13 | cumulative_energy | PDF | O | 0x138D | CUMULATIVE_ENERGY_HIGH | U16
14 | cumulative_energy_low | PDF_ALIAS | O | 0x138D | CUMULATIVE_ENERGY_HIGH | U16 |  |  | cumulative_energy alias (단일 레지스터에 통합값)
15 | status | PDF | O | 0x13AE | INVERTER_MODE | U16 |  |  | 8=Grid Overfreque, 9=Grid Underfrequ, 10=Grid Power Outa, 12=Excess Leakage , 13=Grid Abnormal, 17=Grid Voltage Im... (+9)
16 | alarm1 | PDF | O | 0x13B5 | FAULT_ALARM_CODE_1 | U16
17 | alarm2 | PDF | O | 0x141F | PID_ALARM_CODE | U16
18 | alarm3 | PDF | O | 0x13B5 | FAULT_ALARM_CODE_1 | U16
19 | mppt1_voltage | PDF | O | 0x1393 | MPPT_1_VOLTAGE (추정) | U16 | V | 0.1 | current(0x1394) -1 주소 추정
20 | mppt1_current | PDF | O | 0x1394 | MPPT1_CURRENT | U16 | A | 0.1
21 | mppt2_voltage | PDF | O | 0x1395 | MPPT2_VOLTAGE | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x1396 | MPPT2_CURRENT | U16 | A | 0.1
23 | mppt3_voltage | PDF | O | 0x1397 | MPPT 3voltage | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x1398 | MPPT 3current | U16 | A | 0.1
25 | mppt4_voltage | PDF | O | 0x13FB | MPPT_4_VOLTAGE (추정) | U16 | V | 0.1 | current(0x13FC) -1 주소 추정
26 | mppt4_current | PDF | O | 0x13FC | MPPT 4current | U16 | A | 0.1
27 | mppt5_voltage | PDF | O | 0x13FD | MPPT 5voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x13FE | MPPT 5current | U16 | A | 0.1
29 | mppt6_voltage | PDF | O | 0x13FF | MPPT 6voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x1400 | MPPT 6current | U16 | A | 0.1
31 | mppt7_voltage | PDF | O | 0x1401 | MPPT 7voltage | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x1402 | MPPT 7current | U16 | A | 0.1
33 | mppt8_voltage | PDF | O | 0x1403 | MPPT 8voltage | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x1404 | MPPT 8current | U16 | A | 0.1
35 | mppt9_voltage | PDF | O | 0x140A | MPPT_9_VOLTAGE (추정) | U16 | V | 0.1 | current(0x140B) -1 주소 추정
36 | mppt9_current | PDF | O | 0x140B | MPPT 9current | U16 | A | 0.1
37 | mppt10_voltage | PDF | O | 0x140C | MPPT 10voltage | U16 | V | 0.1
38 | mppt10_current | PDF | O | 0x140D | MPPT 10current | U16 | A | 0.1
39 | mppt11_voltage | PDF | O | 0x140E | MPPT 11voltage | U16 | V | 0.1
40 | mppt11_current | PDF | O | 0x140F | MPPT 11current | U16 | A | 0.1
41 | mppt12_voltage | PDF | O | 0x1410 | MPPT 12voltage | U16 | V | 0.1
42 | mppt12_current | PDF | O | 0x1411 | MPPT 12current | U16 | A | 0.1
43 | mppt13_voltage | PDF | O | 0x1442 | MPPT 13voltage | U16 | V | 0.1
44 | mppt13_current | PDF | O | 0x1443 | MPPT 13current | U16 | A | 0.1
45 | mppt14_voltage | PDF | O | 0x1444 | MPPT 14voltage | U16 | V | 0.1
46 | mppt14_current | PDF | O | 0x1445 | MPPT 14current | U16 | A | 0.1
47 | mppt15_voltage | PDF | O | 0x1446 | MPPT 15voltage | U16 | V | 0.1
48 | mppt15_current | HANDLER | O | - | - | U16 | A |  | handler 계산: sum(string_N_current) N=1~31
49 | mppt16_voltage | PDF | O | 0x1448 | MPPT 16voltage | U16 | V | 0.1
50 | mppt16_current | PDF | O | 0x1449 | MPPT 16current | U16 | A | 0.1
51 | string1_current | HANDLER | O | 0x1394 | MPPT1_CURRENT | U16 | A | 0.1
52 | string2_current | PDF | O | 0x1B66 | String 2current | STRINGING | A | 0.01
53 | string3_current | PDF | O | 0x1B67 | String 3current | STRINGING | A | 0.01
54 | string4_current | PDF | O | 0x1B68 | String 4current | STRINGING | A | 0.01
55 | string5_current | PDF | O | 0x1B69 | String 5current | STRINGING | A | 0.01
56 | string6_current | PDF | O | 0x1B6A | String 6current | STRINGING | A | 0.01
57 | string7_current | PDF | O | 0x1B6B | String 7current | STRINGING | A | 0.01
58 | string8_current | PDF | O | 0x1B6C | String 8current | STRINGING | A | 0.01
59 | string9_current | PDF | O | 0x1B6D | String 9current | STRINGING | A | 0.01
60 | string10_current | PDF | O | 0x1B6E | String 10current | STRINGING | A | 0.01
61 | string11_current | PDF | O | 0x1B6F | String 11current | STRINGING | A | 0.01
62 | string12_current | PDF | O | 0x1B70 | String 12current | STRINGING | A | 0.01
63 | string13_current | PDF | O | 0x1B71 | String 13current | STRINGING | A | 0.01
64 | string14_current | PDF | O | 0x1B72 | String 14current | STRINGING | A | 0.01
65 | string15_current | PDF | O | 0x1B73 | String 15current | STRINGING | A | 0.01
66 | string16_current | PDF | O | 0x1B74 | String 16current | STRINGING | A | 0.01
67 | string17_current | PDF | O | 0x1B75 | String 17current | STRINGING | A | 0.01
68 | string18_current | PDF | O | 0x1B76 | String 18current | STRINGING | A | 0.01
69 | string19_current | PDF | O | 0x1B77 | String 19current | STRINGING | A | 0.01
70 | string20_current | PDF | O | 0x1B78 | String 20current | STRINGING | A | 0.01
71 | string21_current | PDF | O | 0x1B79 | String 21current | STRINGING | A | 0.01
72 | string22_current | PDF | O | 0x1B7A | String 22current | STRINGING | A | 0.01
73 | string23_current | PDF | O | 0x1B7B | String 23current | STRINGING | A | 0.01
74 | string24_current | PDF | O | 0x1B7C | String 24current | STRINGING | A | 0.01
75 | string25_current | PDF | O | 0x1B7D | String 25current | STRINGING | A | 0.01
76 | string26_current | PDF | O | 0x1B7E | String 26current | STRINGING | A | 0.01
77 | string27_current | PDF | O | 0x1B7F | String 27current | STRINGING | A | 0.01
78 | string28_current | PDF | O | 0x1B80 | String 28current | STRINGING | A | 0.01
79 | string29_current | PDF | O | 0x1B81 | String 29current | STRINGING | A | 0.01
80 | string30_current | PDF | O | 0x1B82 | String 30current | STRINGING | A | 0.01
81 | string31_current | PDF | O | 0x1B83 | String 31current | STRINGING | A | 0.01
82 | string32_current | PDF | O | 0x1B84 | String 32current | STRINGING | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 16ch / String 32ch
MPPT 채널 수 | 16
String 채널 수 | 32
String 모니터링 | Yes
MPPT 채널 H01 매칭 (32개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x1393 | MPPT_1_VOLTAGE (추정) | U16 | V | 0.1 | current(0x1394) -1 주소 추정
2 | mppt1_current | PDF | O | 0x1394 | MPPT1_CURRENT | U16 | A | 0.1
3 | mppt2_voltage | PDF | O | 0x1395 | MPPT2_VOLTAGE | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x1396 | MPPT2_CURRENT | U16 | A | 0.1
5 | mppt3_voltage | PDF | O | 0x1397 | MPPT 3voltage | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x1398 | MPPT 3current | U16 | A | 0.1
7 | mppt4_voltage | PDF | O | 0x13FB | MPPT_4_VOLTAGE (추정) | U16 | V | 0.1 | current(0x13FC) -1 주소 추정
8 | mppt4_current | PDF | O | 0x13FC | MPPT 4current | U16 | A | 0.1
9 | mppt5_voltage | PDF | O | 0x13FD | MPPT 5voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x13FE | MPPT 5current | U16 | A | 0.1
11 | mppt6_voltage | PDF | O | 0x13FF | MPPT 6voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x1400 | MPPT 6current | U16 | A | 0.1
13 | mppt7_voltage | PDF | O | 0x1401 | MPPT 7voltage | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x1402 | MPPT 7current | U16 | A | 0.1
15 | mppt8_voltage | PDF | O | 0x1403 | MPPT 8voltage | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x1404 | MPPT 8current | U16 | A | 0.1
17 | mppt9_voltage | PDF | O | 0x140A | MPPT_9_VOLTAGE (추정) | U16 | V | 0.1 | current(0x140B) -1 주소 추정
18 | mppt9_current | PDF | O | 0x140B | MPPT 9current | U16 | A | 0.1
19 | mppt10_voltage | PDF | O | 0x140C | MPPT 10voltage | U16 | V | 0.1
20 | mppt10_current | PDF | O | 0x140D | MPPT 10current | U16 | A | 0.1
21 | mppt11_voltage | PDF | O | 0x140E | MPPT 11voltage | U16 | V | 0.1
22 | mppt11_current | PDF | O | 0x140F | MPPT 11current | U16 | A | 0.1
23 | mppt12_voltage | PDF | O | 0x1410 | MPPT 12voltage | U16 | V | 0.1
24 | mppt12_current | PDF | O | 0x1411 | MPPT 12current | U16 | A | 0.1
25 | mppt13_voltage | PDF | O | 0x1442 | MPPT 13voltage | U16 | V | 0.1
26 | mppt13_current | PDF | O | 0x1443 | MPPT 13current | U16 | A | 0.1
27 | mppt14_voltage | PDF | O | 0x1444 | MPPT 14voltage | U16 | V | 0.1
28 | mppt14_current | PDF | O | 0x1445 | MPPT 14current | U16 | A | 0.1
29 | mppt15_voltage | PDF | O | 0x1446 | MPPT 15voltage | U16 | V | 0.1
30 | mppt15_current | HANDLER | O | - | - | U16 | A |  | handler 계산: sum(string_N_current) N=1~31
31 | mppt16_voltage | PDF | O | 0x1448 | MPPT 16voltage | U16 | V | 0.1
32 | mppt16_current | PDF | O | 0x1449 | MPPT 16current | U16 | A | 0.1
String 채널 H01 매칭 (32개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | 0x1394 | MPPT1_CURRENT | U16 | A | 0.1
2 | string2_current | PDF | O | 0x1B66 | String 2current | STRINGING | A | 0.01
3 | string3_current | PDF | O | 0x1B67 | String 3current | STRINGING | A | 0.01
4 | string4_current | PDF | O | 0x1B68 | String 4current | STRINGING | A | 0.01
5 | string5_current | PDF | O | 0x1B69 | String 5current | STRINGING | A | 0.01
6 | string6_current | PDF | O | 0x1B6A | String 6current | STRINGING | A | 0.01
7 | string7_current | PDF | O | 0x1B6B | String 7current | STRINGING | A | 0.01
8 | string8_current | PDF | O | 0x1B6C | String 8current | STRINGING | A | 0.01
9 | string9_current | PDF | O | 0x1B6D | String 9current | STRINGING | A | 0.01
10 | string10_current | PDF | O | 0x1B6E | String 10current | STRINGING | A | 0.01
11 | string11_current | PDF | O | 0x1B6F | String 11current | STRINGING | A | 0.01
12 | string12_current | PDF | O | 0x1B70 | String 12current | STRINGING | A | 0.01
13 | string13_current | PDF | O | 0x1B71 | String 13current | STRINGING | A | 0.01
14 | string14_current | PDF | O | 0x1B72 | String 14current | STRINGING | A | 0.01
15 | string15_current | PDF | O | 0x1B73 | String 15current | STRINGING | A | 0.01
16 | string16_current | PDF | O | 0x1B74 | String 16current | STRINGING | A | 0.01
17 | string17_current | PDF | O | 0x1B75 | String 17current | STRINGING | A | 0.01
18 | string18_current | PDF | O | 0x1B76 | String 18current | STRINGING | A | 0.01
19 | string19_current | PDF | O | 0x1B77 | String 19current | STRINGING | A | 0.01
20 | string20_current | PDF | O | 0x1B78 | String 20current | STRINGING | A | 0.01
21 | string21_current | PDF | O | 0x1B79 | String 21current | STRINGING | A | 0.01
22 | string22_current | PDF | O | 0x1B7A | String 22current | STRINGING | A | 0.01
23 | string23_current | PDF | O | 0x1B7B | String 23current | STRINGING | A | 0.01
24 | string24_current | PDF | O | 0x1B7C | String 24current | STRINGING | A | 0.01
25 | string25_current | PDF | O | 0x1B7D | String 25current | STRINGING | A | 0.01
26 | string26_current | PDF | O | 0x1B7E | String 26current | STRINGING | A | 0.01
27 | string27_current | PDF | O | 0x1B7F | String 27current | STRINGING | A | 0.01
28 | string28_current | PDF | O | 0x1B80 | String 28current | STRINGING | A | 0.01
29 | string29_current | PDF | O | 0x1B81 | String 29current | STRINGING | A | 0.01
30 | string30_current | PDF | O | 0x1B82 | String 30current | STRINGING | A | 0.01
31 | string31_current | PDF | O | 0x1B83 | String 31current | STRINGING | A | 0.01
32 | string32_current | PDF | O | 0x1B84 | String 32current | STRINGING | A | 0.01
MONITORING 전체 (158개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | PV_STRING_COUNT | 0x0008 | 03 | U16 |  | RO
2 | EXCESSIVE_LEAKAGE_CURRENT | 0x000C | 03 | U16 |  | RO
3 | Excessively High Ambient Temperature | 0x0025 | 03 | U16 |  | RO
4 | Except SG5.5RS-JP | 0x002A | 03 | U32 |  | RO
5 | Excessively Low Ambient Temperature | 0x002B | 03 | U16 |  | RO | s_current
6 | -150-150 | 0x002C | 03 | U16 |  | RO
7 | -180-180 | 0x002D | 03 | U16 |  | RO
8 | -180-180 | 0x002E | 03 | U16 |  | RO
9 | -180-180 | 0x002F | 03 | U16 |  | RO
10 | -170-170 | 0x0072 | 03 | U16 |  | RO
11 | -300-300 | 0x010F | 03 | U16 |  | RO
12 | -300-300 | 0x0136 | 03 | U16 |  | RO
13 | -247-247 | 0x0137 | 03 | U16 |  | RO
14 | -400-400 | 0x0138 | 03 | U16 |  | RO
15 | -625-625 | 0x013B | 03 | U16 |  | RO
16 | -166-166 | 0x013D | 03 | U16 |  | RO
17 | Grid Confrontation | 0x0143 | 03 | U16 |  | RO
18 | -555-555 | 0x014C | 03 | U16 |  | RO
19 | PIDovervoltage/overcurrentprotection | 0x01B2 | 03 | U16 |  | RO
20 | String Current Reflux | 0x060C | 03 | STRINGING |  | RO
21 | Uninitialized | 0x1111 | 03 | U16 |  | RO
22 | Protocol num | 0x1356 | 03 | U32 |  | RO
23 | Protocol ver | 0x1358 | 03 | U32 |  | RO
24 | Armsoftwarever | 0x135A | 03 | U16 |  | RO
25 | DSPsoftwarever | 0x1369 | 03 | U16 |  | RO
26 | CUMULATIVE_ENERGY_HIGH | 0x138D | 03 | U16 |  | RO | cumulative_energy
27 | Export powerlimitation | 0x1392 | 03 | U16 |  | RO
28 | See Appendix 5 | 0x1393 | 03 | U16 | V 0.1 | RO
29 | MPPT1_CURRENT | 0x1394 | 03 | U16 | A 0.1 | RO | mppt1_current
30 | MPPT2_VOLTAGE | 0x1395 | 03 | U16 | V 0.1 | RO | mppt2_voltage
31 | MPPT2_CURRENT | 0x1396 | 03 | U16 | A 0.1 | RO | mppt2_current
32 | MPPT 3voltage | 0x1397 | 03 | U16 | V 0.1 | RO | mppt3_voltage
33 | MPPT 3current | 0x1398 | 03 | U16 | A 0.1 | RO | mppt3_current
34 | PV_POWER | 0x1399 | 03 | U32 |  | RO | pv_power
35 | L1_VOLTAGE | 0x139B | 03 | U16 | V 0.1 | RO | r_voltage
36 | L2_VOLTAGE | 0x139C | 03 | U16 | V 0.1 | RO | s_voltage
37 | L3_VOLTAGE | 0x139D | 03 | U16 | V 0.1 | RO | t_voltage
38 | L1_CURRENT | 0x139E | 03 | U16 | A 0.1 | RO | r_current
39 | Except SG5.5RS-JP | 0x139F | 03 | U16 | A 0.1 | RO
40 | L3_CURRENT | 0x13A0 | 03 | U16 | A 0.1 | RO | t_current
41 | AC_POWER | 0x13A7 | 03 | U32 |  | RO | ac_power
42 | REACTIVE_POWER | 0x13A9 | 03 | S32 |  | RO | reactive_power
43 | POWER_FACTOR | 0x13AB | 03 | S16 |  | RO | power_factor
44 | FREQUENCY | 0x13AC | 03 | U16 | Hz 0.1 | RO | frequency
45 | -500-500Curve B is valid | 0x13BA | 03 | S16 |  | RO
46 | Curve A:0~500Curve B:100-1000 | 0x13BB | 03 | U16 | A 0.1 | RO
47 | Curve A:500~1000Curve B:200-1000 | 0x13BC | 03 | U16 | A 0.1 | RO
48 | Curve A:900~1000Curve B:-500-500 | 0x13BD | 03 | S16 | A | RO
49 | Curve A:900~1000Curve B:-500-500 | 0x13BE | 03 | S16 | A | RO
50 | powerA<=powerB<powerC | 0x13C9 | 03 | U16 | % 0.1 | RO
51 | 200~1000 | 0x13CA | 03 | U16 | % 0.1 | RO
52 | 200~1000 | 0x13CB | 03 | U16 | % 0.1 | RO
53 | 900~1000 | 0x13CC | 03 | U16 |  | RO
54 | 1000~1100 | 0x13CD | 03 | U16 | % 0.1 | RO
55 | 900~1000 | 0x13CE | 03 | U16 | % 0.1 | RO
56 | RegulationSetpoint | 0x13D6 | 03 | U16 |  | RO
57 | ReactivePowerRegulationSetpoint | 0x13D7 | 03 | S32 |  | RO
58 | -500-500，Curve A is valid | 0x13D8 | 03 | S16 | A 0.1 | RO
59 | See Appendix 2Except SG5.5RS-JP | 0x13D9 | 03 | U32 |  | RO
60 | Meter Aphase power | 0x13DD | 03 | S32 |  | RO
61 | (Ind) 0~ 500 | 0x13DE | 03 | U16 | % 0.1 | RO
62 | Meter Bphase power | 0x13DF | 03 | S32 |  | RO
63 | Meter Cphase power | 0x13E1 | 03 | S32 |  | RO
64 | Load power | 0x13E3 | 03 | S32 |  | RO
65 | Daily exportenergy | 0x13E5 | 03 | U32 | kWh 0.1 | RO
66 | Total exportenergy | 0x13E7 | 03 | U32 | kWh 0.1 | RO
67 | Daily importenergy | 0x13E9 | 03 | U32 | kWh 0.1 | RO
68 | Total importenergy | 0x13EB | 03 | U32 | kWh 0.1 | RO
69 | Daily directenergyconsumption | 0x13ED | 03 | U32 | kWh 0.1 | RO
70 | Total directenergyconsumption | 0x13EF | 03 | U32 | kWh 0.1 | RO
71 | 0-1,0 Curve A,1 Curve B | 0x13F1 | 03 | U16 | A | RO
72 | See Appendix 5Except SG5.5RS-JP | 0x13FB | 03 | U16 | V 0.1 | RO
73 | MPPT 4current | 0x13FC | 03 | U16 | A 0.1 | RO | mppt4_current
74 | MPPT 5voltage | 0x13FD | 03 | U16 | V 0.1 | RO | mppt5_voltage
75 | MPPT 5current | 0x13FE | 03 | U16 | A 0.1 | RO | mppt5_current
76 | MPPT 6voltage | 0x13FF | 03 | U16 | V 0.1 | RO | mppt6_voltage
77 | MPPT 6current | 0x1400 | 03 | U16 | A 0.1 | RO | mppt6_current
78 | MPPT 7voltage | 0x1401 | 03 | U16 | V 0.1 | RO | mppt7_voltage
79 | MPPT 7current | 0x1402 | 03 | U16 | A 0.1 | RO | mppt7_current
80 | MPPT 8voltage | 0x1403 | 03 | U16 | V 0.1 | RO | mppt8_voltage
81 | MPPT 8current | 0x1404 | 03 | U16 | A 0.1 | RO | mppt8_current
82 | QP ExitPowerRatio_ | 0x1405 | 03 | U16 | % 0.1 | RO
83 | 0xAA Yes0x55 No | 0x1406 | 03 | U16 |  | RO
84 | MONTHLY_POWERYIELDS | 0x1408 | 03 | U32 | kWh 0.1 | RO
85 | See Appendix 5Except SG5.5RS-JP | 0x140A | 03 | U16 | V 0.1 | RO
86 | MPPT 9current | 0x140B | 03 | U16 | A 0.1 | RO | mppt9_current
87 | MPPT 10voltage | 0x140C | 03 | U16 | V 0.1 | RO | mppt10_voltage
88 | MPPT 10current | 0x140D | 03 | U16 | A 0.1 | RO | mppt10_current
89 | MPPT 11voltage | 0x140E | 03 | U16 | V 0.1 | RO | mppt11_voltage
90 | MPPT 11current | 0x140F | 03 | U16 | A 0.1 | RO | mppt11_current
91 | MPPT 12voltage | 0x1410 | 03 | U16 | V 0.1 | RO | mppt12_voltage
92 | MPPT 12current | 0x1411 | 03 | U16 | A 0.1 | RO | mppt12_current
93 | If support Overload-660-0If not-600-0 | 0x1412 | 03 | S16 | % 0.1 | RO
94 | 800~1000 | 0x1413 | 03 | U16 | % 0.1 | RO
95 | Xinjiang power grid requirements | 0x1414 | 03 | U16 |  | RO
96 | If support Overload-660-660If not-600-600 | 0x1416 | 03 | S16 | % 0.1 | RO
97 | Heart Beat | 0x1417 | 03 | U16 |  | RO
98 | QU EnterPower_ | 0x1419 | 03 | U16 | % 0.1 | RO
99 | Negativevoltage to theground | 0x141A | 03 | S16 | V 0.1 | RO
100 | PID_WORK_STATE | 0x141E | 03 | U16 |  | RO
101 | MPPT 13voltage | 0x1442 | 03 | U16 | V 0.1 | RO | mppt13_voltage
102 | MPPT 13current | 0x1443 | 03 | U16 | A 0.1 | RO | mppt13_current
103 | MPPT 14voltage | 0x1444 | 03 | U16 | V 0.1 | RO | mppt14_voltage
104 | MPPT 14current | 0x1445 | 03 | U16 | A 0.1 | RO | mppt14_current
105 | MPPT 15voltage | 0x1446 | 03 | U16 | V 0.1 | RO | mppt15_voltage
106 | MPPT 16current | 0x1447 | 03 | U16 | A 0.1 | RO | mppt16_current
107 | MPPT 16voltage | 0x1448 | 03 | U16 | V 0.1 | RO | mppt16_voltage
108 | MPPT 16current | 0x1449 | 03 | U16 | A 0.1 | RO | mppt16_current
109 | The inverter is initializing and synchronizing with thegrid | 0x1600 | 03 | U16 |  | RO
110 | String 2current | 0x1B66 | 03 | STRINGING | A 0.01 | RO | string2_current
111 | String 3current | 0x1B67 | 03 | STRINGING | A 0.01 | RO | string3_current
112 | String 4current | 0x1B68 | 03 | STRINGING | A 0.01 | RO | string4_current
113 | String 5current | 0x1B69 | 03 | STRINGING | A 0.01 | RO | string5_current
114 | String 6current | 0x1B6A | 03 | STRINGING | A 0.01 | RO | string6_current
115 | String 7current | 0x1B6B | 03 | STRINGING | A 0.01 | RO | string7_current
116 | String 8current | 0x1B6C | 03 | STRINGING | A 0.01 | RO | string8_current
117 | String 9current | 0x1B6D | 03 | STRINGING | A 0.01 | RO | string9_current
118 | String 10current | 0x1B6E | 03 | STRINGING | A 0.01 | RO | string10_current
119 | String 11current | 0x1B6F | 03 | STRINGING | A 0.01 | RO | string11_current
120 | String 12current | 0x1B70 | 03 | STRINGING | A 0.01 | RO | string12_current
121 | String 13current | 0x1B71 | 03 | STRINGING | A 0.01 | RO | string13_current
122 | String 14current | 0x1B72 | 03 | STRINGING | A 0.01 | RO | string14_current
123 | String 15current | 0x1B73 | 03 | STRINGING | A 0.01 | RO | string15_current
124 | String 16current | 0x1B74 | 03 | STRINGING | A 0.01 | RO | string16_current
125 | String 17current | 0x1B75 | 03 | STRINGING | A 0.01 | RO | string17_current
126 | String 18current | 0x1B76 | 03 | STRINGING | A 0.01 | RO | string18_current
127 | String 19current | 0x1B77 | 03 | STRINGING | A 0.01 | RO | string19_current
128 | String 20current | 0x1B78 | 03 | STRINGING | A 0.01 | RO | string20_current
129 | String 21current | 0x1B79 | 03 | STRINGING | A 0.01 | RO | string21_current
130 | String 22current | 0x1B7A | 03 | STRINGING | A 0.01 | RO | string22_current
131 | String 23current | 0x1B7B | 03 | STRINGING | A 0.01 | RO | string23_current
132 | String 24current | 0x1B7C | 03 | STRINGING | A 0.01 | RO | string24_current
133 | String 25current | 0x1B7D | 03 | STRINGING | A 0.01 | RO | string25_current
134 | String 26current | 0x1B7E | 03 | STRINGING | A 0.01 | RO | string26_current
135 | String 27current | 0x1B7F | 03 | STRINGING | A 0.01 | RO | string27_current
136 | String 28current | 0x1B80 | 03 | STRINGING | A 0.01 | RO | string28_current
137 | String 29current | 0x1B81 | 03 | STRINGING | A 0.01 | RO | string29_current
138 | String 30current | 0x1B82 | 03 | STRINGING | A 0.01 | RO | string30_current
139 | String 31current | 0x1B83 | 03 | STRINGING | A 0.01 | RO | string31_current
140 | String 32current | 0x1B84 | 03 | STRINGING | A 0.01 | RO | string32_current
141 | -218~218 | 0x2C00 | 03 | U16 |  | RO
142 | -264~264 | 0x2C01 | 03 | U16 |  | RO
143 | -330~330 | 0x2C02 | 03 | U16 |  | RO
144 | -660~660 | 0x2C06 | 03 | U16 |  | RO
145 | -1500~1500 | 0x2C0C | 03 | U16 |  | RO
146 | -179~179 | 0x2C10 | 03 | U16 |  | RO
147 | -660~660 | 0x2C12 | 03 | U16 |  | RO
148 | -750 - 750 | 0x2C1C | 03 | U16 |  | RO
149 | -450~450 | 0x2C22 | 03 | U16 |  | RO
150 | -1500 - 1500 | 0x2C25 | 03 | U16 |  | RO
151 | -2112 - 2112 | 0x2C26 | 03 | U16 |  | RO
152 | -2112 - 2112 | 0x2C27 | 03 | U16 |  | RO
153 | -1710 - 1710 | 0x2C43 | 03 | U16 |  | RO
154 | -1998 - 1998 | 0x2C46 | 03 | U16 |  | RO
155 | -2112 - 2112 | 0x2C4F | 03 | U16 |  | RO
156 | Valid for inverters:SG320HXSG350HXSG285HXSG333HXSG350HX-US | 0x7F39 | 03 | U16 |  | RO
157 | Valid for inverters:SG320HX | 0x7F3A | 03 | U16 |  | RO
158 | Inverter is stopped. | 0x8000 | 03 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## INFO_MAPPING
INFO_MAPPING — Model / Serial Number 수동 매핑
※ D열에서 매핑할 레지스터를 선택하세요. E~G열은 추천 후보, H열은 전체 INFO 후보 목록.
No | Field | 설명 | 매칭된 레지스터 (주소) | 추천 후보 1 | 추천 후보 2 | 추천 후보 3 | 전체 레지스터 목록 | FC
1 | model | Model 정보 (제조사/타입/제품명) | DEVICE_TYPECODE (0x1388) |  |  |  | AC_POWER | 3 | AC_POWER | 3 | 0x13A7 | pdf
2 | sn | Serial Number / Firmware Version | SERIAL_NUMBER (0x137E) |  |  |  | ALARM_RUN | 3 | ALARM_RUN | 3 | 0x000A | pdf
[7 empty] | ARMSOFTWAREVER |  | ARMSOFTWAREVER | 3 | 0x135A
[7 empty] | ARRAY_INSULATIONRESISTANCE |  | ARRAY_INSULATIONRESISTANCE | 3 | 0x13CF
[7 empty] | BUS_VOLTAGE |  | BUS_VOLTAGE | 3 | 0x141B
[7 empty] | COMMUNICATE_FAULT |  | COMMUNICATE_FAULT | 3 | 0x2500
[7 empty] | CUMULATIVE_ENERGY_HIGH |  | CUMULATIVE_ENERGY_HIGH | 3 | 0x138D
[7 empty] | CURVE_A_0500CURVE_B_100_1000 |  | CURVE_A_0500CURVE_B_100_1000 | 3 | 0x13BB
[7 empty] | CURVE_A_5001000CURVE_B_200_1000 |  | CURVE_A_5001000CURVE_B_200_1000 | 3 | 0x13BC
[7 empty] | CURVE_A_9001000CURVE_B_500_500 |  | CURVE_A_9001000CURVE_B_500_500 | 3 | 0x13BD
[7 empty] | DAILY_DIRECTENERGYCONSUMPTION |  | DAILY_DIRECTENERGYCONSUMPTION | 3 | 0x13ED
[7 empty] | DAILY_EXPORTENERGY |  | DAILY_EXPORTENERGY | 3 | 0x13E5
[7 empty] | DAILY_IMPORTENERGY |  | DAILY_IMPORTENERGY | 3 | 0x13E9
[7 empty] | DAILY_POWERYIELDS |  | DAILY_POWERYIELDS | 3 | 0x138B
[7 empty] | DAILY_RUNNING_TIME |  | DAILY_RUNNING_TIME | 3 | 0x13F9
[7 empty] | DEFAULT_0_1100GERMANYBELGIUMAUSTRALIA_0_1000 |  | DEFAULT_0_1100GERMANYBELGIUMAUSTRALIA_0_1000 | 3 | 0x243D
[7 empty] | DEFAULT_0_1100IF_COUNTRY_IS_GERMANYRANGE_IS_0_1000 |  | DEFAULT_0_1100IF_COUNTRY_IS_GERMANYRANGE_IS_0_1000 | 3 | 0x013E
[7 empty] | DEFAULT_0_110GERMANY_BELGIUMAUSTRALIA_0_100 |  | DEFAULT_0_110GERMANY_BELGIUMAUSTRALIA_0_100 | 3 | 0x2433
[7 empty] | DEFAULT_0_132GERMANY_AUSTRALIA |  | DEFAULT_0_132GERMANY_AUSTRALIA | 3 | 0x2444
[7 empty] | DEFAULT_0_132GERMANY_AUSTRALIA_0_120 |  | DEFAULT_0_132GERMANY_AUSTRALIA_0_120 | 3 | 0x2434
[7 empty] | DEFAULT_0_165GERMANY_AUSTRALIA_0_150 |  | DEFAULT_0_165GERMANY_AUSTRALIA_0_150 | 3 | 0x2435
[7 empty] | DEFAULT_0_187GERMANY_AUSTRALIA_0_170 |  | DEFAULT_0_187GERMANY_AUSTRALIA_0_170 | 3 | 0x2436
[7 empty] | DEFAULT_0_220GERMANY_AUSTRALIA_0_200 |  | DEFAULT_0_220GERMANY_AUSTRALIA_0_200 | 3 | 0x2437
[7 empty] | DEFAULT_0_242GERMANY_AUSTRALIA_0_220 |  | DEFAULT_0_242GERMANY_AUSTRALIA_0_220 | 3 | 0x2438
[7 empty] | DEFAULT_0_253GERMANY_AUSTRALIA_0_230 |  | DEFAULT_0_253GERMANY_AUSTRALIA_0_230 | 3 | 0x243B
[7 empty] | DEFAULT_0_275GERMANY_AUSTRALIA_0_250 |  | DEFAULT_0_275GERMANY_AUSTRALIA_0_250 | 3 | 0x2439
[7 empty] | DEFAULT_0_55GERMANY_AUSTRALIA_0_50 |  | DEFAULT_0_55GERMANY_AUSTRALIA_0_50 | 3 | 0x2430
[7 empty] | DEFAULT_0_66GERMANY_AUSTRALIA_0_60 |  | DEFAULT_0_66GERMANY_AUSTRALIA_0_60 | 3 | 0x2431
[7 empty] | DEFAULT_0_77GERMANY_0_70_AUSTRALIA_0_69_99 |  | DEFAULT_0_77GERMANY_0_70_AUSTRALIA_0_69_99 | 3 | 0x243C
[7 empty] | DEFAULT_0_88GERMANY_AUSTRALIA_0_80 |  | DEFAULT_0_88GERMANY_AUSTRALIA_0_80 | 3 | 0x2432
[7 empty] | DEVICE_TYPECODE |  | DEVICE_TYPECODE | 3 | 0x1388
[7 empty] | DSPSOFTWAREVER |  | DSPSOFTWAREVER | 3 | 0x1369
[7 empty] | ELECTRIC_ARC_FAULT |  | ELECTRIC_ARC_FAULT | 3 | 0x0058
[7 empty] | EXCEPT_SG5_5RS_JP |  | EXCEPT_SG5_5RS_JP | 3 | 0x139F
[7 empty] | EXCESSIVELY_HIGH_AMBIENT_TEMPERATURE |  | EXCESSIVELY_HIGH_AMBIENT_TEMPERATURE | 3 | 0x0025
[7 empty] | EXCESSIVELY_LOW_AMBIENT_TEMPERATURE |  | EXCESSIVELY_LOW_AMBIENT_TEMPERATURE | 3 | 0x002B
[7 empty] | EXCESSIVE_LEAKAGE_CURRENT |  | EXCESSIVE_LEAKAGE_CURRENT | 3 | 0x000C
[7 empty] | EXPORT_POWERLIMITATION |  | EXPORT_POWERLIMITATION | 3 | 0x1392
[7 empty] | FAULT |  | FAULT | 3 | 0x5500
[7 empty] | FAULT_ALARM_CODE_1 |  | FAULT_ALARM_CODE_1 | 3 | 0x13B5
[7 empty] | FAULT_ALARM_TIME_DAY |  | FAULT_ALARM_TIME_DAY | 3 | 0x13B1
[7 empty] | FAULT_ALARM_TIME_HOUR |  | FAULT_ALARM_TIME_HOUR | 3 | 0x13B2
[7 empty] | FAULT_ALARM_TIME_MINUTE |  | FAULT_ALARM_TIME_MINUTE | 3 | 0x13B3
[7 empty] | FAULT_ALARM_TIME_MONTH |  | FAULT_ALARM_TIME_MONTH | 3 | 0x13B0
[7 empty] | FAULT_ALARM_TIME_SECOND |  | FAULT_ALARM_TIME_SECOND | 3 | 0x13B4
[7 empty] | FAULT_ALARM_TIME_YEAR |  | FAULT_ALARM_TIME_YEAR | 3 | 0x13AF
[7 empty] | FREQUENCY |  | FREQUENCY | 3 | 0x13AC
[7 empty] | GRID_CONFRONTATION |  | GRID_CONFRONTATION | 3 | 0x0143
[7 empty] | GROUNDING_CABLE_FAULT |  | GROUNDING_CABLE_FAULT | 3 | 0x006A
[7 empty] | HEART_BEAT |  | HEART_BEAT | 3 | 0x1417
[7 empty] | IF_SUPPORT_OVERLOAD_660_0IF_NOT_600_0 |  | IF_SUPPORT_OVERLOAD_660_0IF_NOT_600_0 | 3 | 0x1412
[7 empty] | IF_SUPPORT_OVERLOAD_660_660IF_NOT_600_600 |  | IF_SUPPORT_OVERLOAD_660_660IF_NOT_600_600 | 3 | 0x1416
[7 empty] | IND_0_500 |  | IND_0_500 | 3 | 0x13DE
[7 empty] | INTERNALTEMPERATURE |  | INTERNALTEMPERATURE | 3 | 0x1390
[7 empty] | INVERTER_IS_STOPPED |  | INVERTER_IS_STOPPED | 3 | 0x8000
[7 empty] | INVERTER_MODE |  | INVERTER_MODE | 3 | 0x13AE
[7 empty] | INVERTER_PARALLEL_COMMUNICATION_ALARM |  | INVERTER_PARALLEL_COMMUNICATION_ALARM | 3 | 0x004B
[7 empty] | L1_CURRENT |  | L1_CURRENT | 3 | 0x139E
[7 empty] | L1_VOLTAGE |  | L1_VOLTAGE | 3 | 0x139B
[7 empty] | L2_VOLTAGE |  | L2_VOLTAGE | 3 | 0x139C
[7 empty] | L3_CURRENT |  | L3_CURRENT | 3 | 0x13A0
[7 empty] | L3_VOLTAGE |  | L3_VOLTAGE | 3 | 0x139D
[7 empty] | LOAD_POWER |  | LOAD_POWER | 3 | 0x13E3
[7 empty] | LOW_SYSTEM_INSULATION_RESISTANCE |  | LOW_SYSTEM_INSULATION_RESISTANCE | 3 | 0x0027
[7 empty] | METER_APHASE_POWER |  | METER_APHASE_POWER | 3 | 0x13DD
[7 empty] | METER_BPHASE_POWER |  | METER_BPHASE_POWER | 3 | 0x13DF
[7 empty] | METER_COMMUNICATION_ABNORMALALARM |  | METER_COMMUNICATION_ABNORMALALARM | 3 | 0x0202
[7 empty] | METER_CPHASE_POWER |  | METER_CPHASE_POWER | 3 | 0x13E1
[7 empty] | MONTHLY_POWERYIELDS |  | MONTHLY_POWERYIELDS | 3 | 0x1408
[7 empty] | MPPT1_CURRENT |  | MPPT1_CURRENT | 3 | 0x1394
[7 empty] | MPPT2_CURRENT |  | MPPT2_CURRENT | 3 | 0x1396
[7 empty] | MPPT2_VOLTAGE |  | MPPT2_VOLTAGE | 3 | 0x1395
[7 empty] | MPPT_10CURRENT |  | MPPT_10CURRENT | 3 | 0x140D
[7 empty] | MPPT_10VOLTAGE |  | MPPT_10VOLTAGE | 3 | 0x140C
[7 empty] | MPPT_11CURRENT |  | MPPT_11CURRENT | 3 | 0x140F
[7 empty] | MPPT_11VOLTAGE |  | MPPT_11VOLTAGE | 3 | 0x140E
[7 empty] | MPPT_12CURRENT |  | MPPT_12CURRENT | 3 | 0x1411
[7 empty] | MPPT_12VOLTAGE |  | MPPT_12VOLTAGE | 3 | 0x1410
[7 empty] | MPPT_13CURRENT |  | MPPT_13CURRENT | 3 | 0x1443
[7 empty] | MPPT_13VOLTAGE |  | MPPT_13VOLTAGE | 3 | 0x1442
[7 empty] | MPPT_14CURRENT |  | MPPT_14CURRENT | 3 | 0x1445
[7 empty] | MPPT_14VOLTAGE |  | MPPT_14VOLTAGE | 3 | 0x1444
[7 empty] | MPPT_15VOLTAGE |  | MPPT_15VOLTAGE | 3 | 0x1446
[7 empty] | MPPT_16CURRENT |  | MPPT_16CURRENT | 3 | 0x1447
[7 empty] | MPPT_16VOLTAGE |  | MPPT_16VOLTAGE | 3 | 0x1448
[7 empty] | MPPT_3CURRENT |  | MPPT_3CURRENT | 3 | 0x1398
[7 empty] | MPPT_3VOLTAGE |  | MPPT_3VOLTAGE | 3 | 0x1397
[7 empty] | MPPT_4CURRENT |  | MPPT_4CURRENT | 3 | 0x13FC
[7 empty] | MPPT_5CURRENT |  | MPPT_5CURRENT | 3 | 0x13FE
[7 empty] | MPPT_5VOLTAGE |  | MPPT_5VOLTAGE | 3 | 0x13FD
[7 empty] | MPPT_6CURRENT |  | MPPT_6CURRENT | 3 | 0x1400
[7 empty] | MPPT_6VOLTAGE |  | MPPT_6VOLTAGE | 3 | 0x13FF
[7 empty] | MPPT_7CURRENT |  | MPPT_7CURRENT | 3 | 0x1402
[7 empty] | MPPT_7VOLTAGE |  | MPPT_7VOLTAGE | 3 | 0x1401
[7 empty] | MPPT_8CURRENT |  | MPPT_8CURRENT | 3 | 0x1404
[7 empty] | MPPT_8VOLTAGE |  | MPPT_8VOLTAGE | 3 | 0x1403
[7 empty] | MPPT_9CURRENT |  | MPPT_9CURRENT | 3 | 0x140B
[7 empty] | NEGATIVEVOLTAGE_TO_THEGROUND |  | NEGATIVEVOLTAGE_TO_THEGROUND | 3 | 0x141A
[7 empty] | NOMINAL_ACTIVEPOWER |  | NOMINAL_ACTIVEPOWER | 3 | 0x1389
[7 empty] | NOMINAL_REACTIVEPOWER |  | NOMINAL_REACTIVEPOWER | 3 | 0x13B9
[7 empty] | OUTPUT_TYPE |  | OUTPUT_TYPE | 3 | 0x138A
[7 empty] | PIDOVERVOLTAGE_OVERCURRENTPROTECTION |  | PIDOVERVOLTAGE_OVERCURRENTPROTECTION | 3 | 0x01B2
[7 empty] | PID_ALARM_CODE |  | PID_ALARM_CODE | 3 | 0x141F
[7 empty] | PID_WORK_STATE |  | PID_WORK_STATE | 3 | 0x141E
[7 empty] | POWERLIMITATIONSWITCH |  | POWERLIMITATIONSWITCH | 3 | 0x138F
[7 empty] | POWER_APOWER_BPOWER_C |  | POWER_APOWER_BPOWER_C | 3 | 0x13C9
[7 empty] | POWER_FACTOR |  | POWER_FACTOR | 3 | 0x13AB
[7 empty] | PRESENT_COUNTRY |  | PRESENT_COUNTRY | 3 | 0x13FA
[7 empty] | PROTOCOL_NUM |  | PROTOCOL_NUM | 3 | 0x1356
[7 empty] | PROTOCOL_VER |  | PROTOCOL_VER | 3 | 0x1358
[7 empty] | PV_GROUNDING_FAULT |  | PV_GROUNDING_FAULT | 3 | 0x0640
[7 empty] | PV_POWER |  | PV_POWER | 3 | 0x1399
[7 empty] | PV_STRING_COUNT |  | PV_STRING_COUNT | 3 | 0x0008
[7 empty] | QP_EXIT_POWER_RATIO |  | QP_EXIT_POWER_RATIO | 3 | 0x1405
[7 empty] | QU_ENTER_POWER |  | QU_ENTER_POWER | 3 | 0x1419
[7 empty] | REACTIVE_POWER |  | REACTIVE_POWER | 3 | 0x13A9
[7 empty] | REACTIVE_POWER_REGULATION_SETPOINT |  | REACTIVE_POWER_REGULATION_SETPOINT | 3 | 0x13D7
[7 empty] | REGULATION_SETPOINT |  | REGULATION_SETPOINT | 3 | 0x13D6
[7 empty] | REG_0X_AA_YES0X55_NO |  | REG_0X_AA_YES0X55_NO | 3 | 0x1406
[7 empty] | REG_0_10_CURVE_A1_CURVE_B |  | REG_0_10_CURVE_A1_CURVE_B | 3 | 0x13F1
[7 empty] | REG_10001100 |  | REG_10001100 | 3 | 0x13CD
[7 empty] | REG_15001500 |  | REG_15001500 | 3 | 0x2C0C
[7 empty] | REG_1500_1500 |  | REG_1500_1500 | 3 | 0x2C25
[7 empty] | REG_150_150 |  | REG_150_150 | 3 | 0x002C
[7 empty] | REG_166_166 |  | REG_166_166 | 3 | 0x013D
[7 empty] | REG_170_170 |  | REG_170_170 | 3 | 0x0072
[7 empty] | REG_1710_1710 |  | REG_1710_1710 | 3 | 0x2C43
[7 empty] | REG_179179 |  | REG_179179 | 3 | 0x2C10
[7 empty] | REG_180_180 |  | REG_180_180 | 3 | 0x002D
[7 empty] | REG_1998_1998 |  | REG_1998_1998 | 3 | 0x2C46
[7 empty] | REG_2001000 |  | REG_2001000 | 3 | 0x13CA
[7 empty] | REG_2112_2112 |  | REG_2112_2112 | 3 | 0x2C26
[7 empty] | REG_218218 |  | REG_218218 | 3 | 0x2C00
[7 empty] | REG_247_247 |  | REG_247_247 | 3 | 0x0137
[7 empty] | REG_264264 |  | REG_264264 | 3 | 0x2C01
[7 empty] | REG_300_300 |  | REG_300_300 | 3 | 0x0136
[7 empty] | REG_330330 |  | REG_330330 | 3 | 0x2C02
[7 empty] | REG_400_400 |  | REG_400_400 | 3 | 0x0138
[7 empty] | REG_450450 |  | REG_450450 | 3 | 0x2C22
[7 empty] | REG_500_500CURVE_A_IS_VALID |  | REG_500_500CURVE_A_IS_VALID | 3 | 0x13D8
[7 empty] | REG_500_500CURVE_B_IS_VALID |  | REG_500_500CURVE_B_IS_VALID | 3 | 0x13BA
[7 empty] | REG_555_555 |  | REG_555_555 | 3 | 0x014C
[7 empty] | REG_625_625 |  | REG_625_625 | 3 | 0x013B
[7 empty] | REG_660660 |  | REG_660660 | 3 | 0x2C06
[7 empty] | REG_750_750 |  | REG_750_750 | 3 | 0x2C1C
[7 empty] | REG_8001000 |  | REG_8001000 | 3 | 0x1413
[7 empty] | REG_9001000 |  | REG_9001000 | 3 | 0x13CC
[7 empty] | REVERSE_CONNECTION_ALARM_OF_THE_METER_CT |  | REVERSE_CONNECTION_ALARM_OF_THE_METER_CT | 3 | 0x0054
[7 empty] | SEE_APPENDIX_2EXCEPT_SG5_5RS_JP |  | SEE_APPENDIX_2EXCEPT_SG5_5RS_JP | 3 | 0x13D9
[7 empty] | SEE_APPENDIX_5 |  | SEE_APPENDIX_5 | 3 | 0x1393
[7 empty] | SEE_APPENDIX_5EXCEPT_SG5_5RS_JP |  | SEE_APPENDIX_5EXCEPT_SG5_5RS_JP | 3 | 0x13FB
[7 empty] | SERIAL_NUMBER |  | SERIAL_NUMBER | 3 | 0x137E
[7 empty] | STRING_10CURRENT |  | STRING_10CURRENT | 3 | 0x1B6E
[7 empty] | STRING_11CURRENT |  | STRING_11CURRENT | 3 | 0x1B6F
[7 empty] | STRING_12CURRENT |  | STRING_12CURRENT | 3 | 0x1B70
[7 empty] | STRING_13CURRENT |  | STRING_13CURRENT | 3 | 0x1B71
[7 empty] | STRING_14CURRENT |  | STRING_14CURRENT | 3 | 0x1B72
[7 empty] | STRING_15CURRENT |  | STRING_15CURRENT | 3 | 0x1B73
[7 empty] | STRING_16CURRENT |  | STRING_16CURRENT | 3 | 0x1B74
[7 empty] | STRING_17CURRENT |  | STRING_17CURRENT | 3 | 0x1B75
[7 empty] | STRING_18CURRENT |  | STRING_18CURRENT | 3 | 0x1B76
[7 empty] | STRING_19CURRENT |  | STRING_19CURRENT | 3 | 0x1B77
[7 empty] | STRING_20CURRENT |  | STRING_20CURRENT | 3 | 0x1B78
[7 empty] | STRING_21CURRENT |  | STRING_21CURRENT | 3 | 0x1B79
[7 empty] | STRING_22CURRENT |  | STRING_22CURRENT | 3 | 0x1B7A
[7 empty] | STRING_23CURRENT |  | STRING_23CURRENT | 3 | 0x1B7B
[7 empty] | STRING_24CURRENT |  | STRING_24CURRENT | 3 | 0x1B7C
[7 empty] | STRING_25CURRENT |  | STRING_25CURRENT | 3 | 0x1B7D
[7 empty] | STRING_26CURRENT |  | STRING_26CURRENT | 3 | 0x1B7E
[7 empty] | STRING_27CURRENT |  | STRING_27CURRENT | 3 | 0x1B7F
[7 empty] | STRING_28CURRENT |  | STRING_28CURRENT | 3 | 0x1B80
[7 empty] | STRING_29CURRENT |  | STRING_29CURRENT | 3 | 0x1B81
[7 empty] | STRING_2CURRENT |  | STRING_2CURRENT | 3 | 0x1B66
[7 empty] | STRING_30CURRENT |  | STRING_30CURRENT | 3 | 0x1B82
[7 empty] | STRING_31CURRENT |  | STRING_31CURRENT | 3 | 0x1B83
[7 empty] | STRING_32CURRENT |  | STRING_32CURRENT | 3 | 0x1B84
[7 empty] | STRING_3CURRENT |  | STRING_3CURRENT | 3 | 0x1B67
[7 empty] | STRING_4CURRENT |  | STRING_4CURRENT | 3 | 0x1B68
[7 empty] | STRING_5CURRENT |  | STRING_5CURRENT | 3 | 0x1B69
[7 empty] | STRING_6CURRENT |  | STRING_6CURRENT | 3 | 0x1B6A
[7 empty] | STRING_7CURRENT |  | STRING_7CURRENT | 3 | 0x1B6B
[7 empty] | STRING_8CURRENT |  | STRING_8CURRENT | 3 | 0x1B6C
[7 empty] | STRING_9CURRENT |  | STRING_9CURRENT | 3 | 0x1B6D
[7 empty] | STRING_CURRENT_REFLUX |  | STRING_CURRENT_REFLUX | 3 | 0x060C
[7 empty] | SYSTEM_HARDWARE_FAULT |  | SYSTEM_HARDWARE_FAULT | 3 | 0x0650
[7 empty] | THE_INVERTER_IS_INITIALIZING_AND_SYNCHRONIZING_WITH_THEGRID |  | THE_INVERTER_IS_INITIALIZING_AND_SYNCHRONIZING_WITH_THEGRID | 3 | 0x1600
[7 empty] | THE_INVERTER_IS_IN_THE_INITIAL_POWER_ON_STANDBY_STATE |  | THE_INVERTER_IS_IN_THE_INITIAL_POWER_ON_STANDBY_STATE | 3 | 0x1200
[7 empty] | TOTAL_APPARENTPOWER |  | TOTAL_APPARENTPOWER | 3 | 0x1391
[7 empty] | TOTAL_DIRECTENERGYCONSUMPTION |  | TOTAL_DIRECTENERGYCONSUMPTION | 3 | 0x13EF
[7 empty] | TOTAL_EXPORTENERGY |  | TOTAL_EXPORTENERGY | 3 | 0x13E7
[7 empty] | TOTAL_FAULT_BIT_DEVICE_IS_INFAULT_STOP_STATE |  | TOTAL_FAULT_BIT_DEVICE_IS_INFAULT_STOP_STATE | 3 | 0x0012
[7 empty] | TOTAL_FAULT_STATE_BIT_BIT18 |  | TOTAL_FAULT_STATE_BIT_BIT18 | 3 | 0x0009
[7 empty] | TOTAL_IMPORTENERGY |  | TOTAL_IMPORTENERGY | 3 | 0x13EB
[7 empty] | TOTAL_POWERYIELDS |  | TOTAL_POWERYIELDS | 3 | 0x138C
[7 empty] | TOTAL_RUNNING_TIME |  | TOTAL_RUNNING_TIME | 3 | 0x138E
[7 empty] | TOTAL_RUN_BIT_DEVICE_IS_GRID_CONNECTED_RUNNING |  | TOTAL_RUN_BIT_DEVICE_IS_GRID_CONNECTED_RUNNING | 3 | 0x0011
[7 empty] | TOTAL_RUN_STATE_BIT_BIT17 |  | TOTAL_RUN_STATE_BIT_BIT17 | 3 | 0x000B
[7 empty] | UNINITIALIZED |  | UNINITIALIZED | 3 | 0x1111
[7 empty] | VALID_FOR_INVERTERS_SG320HX |  | VALID_FOR_INVERTERS_SG320HX | 3 | 0x7F3A
[7 empty] | VALID_FOR_INVERTERS_SG320HXSG350HXSG285HXSG333HXSG350HX_US |  | VALID_FOR_INVERTERS_SG320HXSG350HXSG285HXSG333HXSG350HX_US | 3 | 0x7F39
[7 empty] | WARNING_INFORMATION_IS_DETECTED |  | WARNING_INFORMATION_IS_DETECTED | 3 | 0x9100
[7 empty] | XINJIANG_POWER_GRID_REQUIREMENTS |  | XINJIANG_POWER_GRID_REQUIREMENTS | 3 | 0x1414