## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | ABB
프로토콜 버전
설비 타입 | inverter
MPPT | 3
String | 3
String 모니터링 | No (MPPT당 1 String)
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | ABB_TRIO_Modbus_RTU.pdf
추출 일시 | 2026-04-03 15:58
H01 매칭 | 26/26
DER 매칭 | 33/33
추출 레지스터 | 146
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Configuration fault (bad model) | 0x0078 | 03 | U16 |  | RO
2 | Dynamic ModeReactive Power Set Point:Reactive Power expressed asratio of Max apparent power (interm of cosφ) | 0x00DC | 03 | U16 |  | RO
3 | Permanent ModeReactive Power Set Point:Reactive Power expressed asratio of Max apparent power (interm of cosφ) | 0x00DE | 03 | U16 |  | RO
4 | Dynamic ModeReactive Power Set Point:Reactive Power expressed aspercentage of Max apparentpower in % steps | 0x00E1 | 03 | S16 |  | RO
5 | Permanent ModeReactive Power Set Point:Reactive Power expressed aspercentage of Max apparentpower in % steps | 0x00E3 | 03 | S16 |  | RO
6 | Dynamic ModeReactive Power Set Point:Reactive Power expressed aspercentage of Nominal Power in% steps | 0x01FB | 03 | S16 |  | RO
7 | Permanent ModeReactive Power Set Point:Reactive Power expressed aspercentage of Nominal Power in% steps | 0x01FF | 03 | S16 |  | RO
8 | Model Type | 0x03FE | 03 | ASCII |  | RO
9 | Daily Energy | 0x042E | 03 | U32 |  | RO | daily_energy
10 | Total Energy | 0x0430 | 03 | U32 |  | RO | cumulative_energy
11 | INNER_TEMP | 0x0460 | 03 | U16 |  | RO | temperature | Internal Temperature
12 | INNER_TEMP | 0x0462 | 03 | U16 |  | RO | temperature | Inverter Temperature
13 | DEVICE_MODEL | 0x0E43 | 03 | ASCII |  | RO |  | Product model
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Wrong input mode | 0x0011 | 03 | U16 |  | RO
2 | Remove “Reset by Hand” latch-state | 0x00B5 | 03 | U16 |  | RO
3 | Timeout for Dynamic mode | 0x00BF | 03 | U16 |  | RO
4 | Dynamic Mode | 0x00D2 | 03 | U16 |  | RO
5 | Permanent Mode | 0x00D4 | 03 | U16 |  | RO
6 | Set active mode | 0x01F6 | 03 | U16 |  | RO
7 | Timeout for Dynamic mode | 0x01F8 | 03 | U16 |  | RO
8 | Reactive Power control mode | 0x01FA | 03 | U16 |  | RO
9 | Dynamic Mode | 0x01FC | 03 | U16 |  | RO
10 | Permanent Mode | 0x0200 | 03 | U16 |  | RO
11 | Remove “Reset by Hand” latch-state | 0x0322 | 03 | U16 |  | RO
12 | Global State | 0x041A | 03 | U16 |  | RO | inverter_status
13 | Alarm State | 0x041B | 03 | U16 |  | RO
14 | DC/DC Converter State | 0x041C | 03 | U16 |  | RO
15 | DC/AC Converter State | 0x041D | 03 | U16 |  | RO
16 | Derating State | 0x041E | 03 | U16 |  | RO
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Post-alarm actions (recovery) | 0x0007 | 03 | U16 |  | RO
2 | Post-alarm actions (pause) | 0x0008 | 03 | U16 |  | RO
3 | Ground fault | 0x0009 | 03 | U16 |  | RO
4 | Over-temperature fault | 0x000A | 03 | U16 |  | RO
5 | Grid protection interface self-test fault | 0x000D | 03 | U16 |  | RO
6 | Leakage fault | 0x000F | 03 | U16 |  | RO
7 | Internal error | 0x0010 | 03 | U16 |  | RO
8 | Grid fault | 0x0012 | 03 | U16 |  | RO
9 | Cap. Fault | 0x0014 | 03 | U16 |  | RO
10 | Internal error | 0x0015 | 03 | U16 |  | RO
11 | Internal error | 0x0016 | 03 | U16 |  | RO
12 | Leak fault | 0x0017 | 03 | U16 |  | RO
13 | Under-temperature fault | 0x0018 | 03 | U16 |  | RO
14 | Internal error | 0x001C | 03 | U16 |  | RO
15 | Grounding-kit fault | 0x001D | 03 | U16 |  | RO
16 | SW bundle not valid fault | 0x001E | 03 | U16 |  | RO
17 | Communication error | 0x0023 | 03 | U16 |  | RO
18 | Temperature sensors fault | 0x0029 | 03 | U16 |  | RO
19 | Grid sequence fault | 0x002A | 03 | U16 |  | RO
20 | Internal error | 0x002C | 03 | U16 |  | RO
21 | Internal error | 0x002D | 03 | U16 |  | RO
22 | Arc fault | 0x0033 | 03 | U16 |  | RO
23 | Arc detector self-test fault | 0x0035 | 03 | U16 |  | RO
24 | AFDD fault | 0x0052 | 03 | U16 |  | RO
25 | Internal error | 0x005B | 03 | U16 |  | RO
26 | Grid conn. fault | 0x005F | 03 | U16 |  | RO
27 | Arc detector wrong configuration fault | 0x0076 | 03 | U16 |  | RO
28 | Power stage communication fault | 0x0096 | 03 | U16 |  | RO
29 | Configuration fault (bad global-settings) | 0x0097 | 03 | U16 |  | RO
30 | Aux. Bulk Feed Conn. Error | 0x00A7 | 03 | U16 |  | RO
31 | Ground Kit Self Test Error | 0x00AA | 03 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 26/26
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | HANDLER | O | - | - | U16 | W |  | handler 계산: 1순위: PDF Total DC Power, 2순위: sum(MPPT_N_power)
13 | cumulative_energy | PDF | O | 0x0430 | Total Energy | U32
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x041A | Global State | U16 |  |  | 0=Initializing, 1=Connecting to g, 2=Connected to gr, 3=Bulk over-volta, 4=Output over-cur, 5=IGBT fault... (+26)
16 | alarm1 | PDF | O | 0x0009 | Ground fault | U16
17 | alarm2 | PDF | O | 0x0010 | Internal error | U16
18 | alarm3 | PDF | O | 0x0015 | Internal error | U16
19 | mppt1_voltage | PDF | O | 0x0456 | Voltage on DC Input #1 | U16
20 | mppt1_current | PDF | O | 0x0458 | Current on DC Input #1 | U16
21 | mppt2_voltage | PDF | O | 0x045C | Voltage on DC Input #2 | U16
22 | mppt2_current | PDF | O | 0x045E | Current on DC Input #2 | U16
23 | mppt3_voltage | PDF | O | 0x046C | Voltage on DC Input #3 | U16
24 | mppt3_current | PDF | O | 0x046E | Current on DC Input #3 | U16
25 | string1_current | HANDLER | O | 0x0458 | Current on DC Input #1 | U16 | A
26 | string2_current | HANDLER | O | 0x045E | Current on DC Input #2 | U16 | A
27 | string3_current | HANDLER | O | 0x046E | Current on DC Input #3 | U16 | A

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 3ch / String 3ch
MPPT 채널 수 | 3
String 채널 수 | 3
String 모니터링 | No (MPPT당 1 String)
MPPT 채널 H01 매칭 (6개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x0456 | Voltage on DC Input #1 | U16
2 | mppt1_current | PDF | O | 0x0458 | Current on DC Input #1 | U16
3 | mppt2_voltage | PDF | O | 0x045C | Voltage on DC Input #2 | U16
4 | mppt2_current | PDF | O | 0x045E | Current on DC Input #2 | U16
5 | mppt3_voltage | PDF | O | 0x046C | Voltage on DC Input #3 | U16
6 | mppt3_current | PDF | O | 0x046E | Current on DC Input #3 | U16
String 채널 H01 매칭 (3개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | 0x0458 | Current on DC Input #1 | U16 | A
2 | string2_current | HANDLER | O | 0x045E | Current on DC Input #2 | U16 | A
3 | string3_current | HANDLER | O | 0x046E | Current on DC Input #3 | U16 | A
MONITORING 전체 (78개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | 0x0B | 0x0000 | 03 | U16 |  | RO
2 | Waiting sun or grid | 0x0001 | 03 | U16 |  | RO
3 | 0x04 | 0x0002 | 03 | U16 |  | RO
4 | Initializing (system startup) | 0x0003 | 03 | U16 |  | RO
5 | Connecting to grid (switching-on DC/DC) | 0x0004 | 03 | U16 |  | RO
6 | Connecting to grid (switching-on DC/AC) | 0x0005 | 03 | U16 |  | RO
7 | Connected to grid | 0x0006 | 03 | U16 |  | RO
8 | Bulk UV | 0x000B | 03 | U16 |  | RO
9 | Connecting to grid (grid protection interface self-test) | 0x000C | 03 | U16 |  | RO
10 | Connecting to grid (safety checks) | 0x000E | 03 | U16 |  | RO
11 | Over temperature | 0x0013 | 03 | U16 |  | RO
12 | Executing auto-test | 0x001B | 03 | U16 |  | RO
13 | DC injection | 0x001F | 03 | U16 |  | RO
14 | IGBT not ready | 0x0021 | 03 | U16 |  | RO
15 | Mid-bulk over-voltage | 0x0024 | 03 | U16 |  | RO
16 | Riso low | 0x0026 | 03 | U16 |  | RO
17 | 0xF6 | 0x0028 | 03 | U16 |  | RO
18 | Undertemperature | 0x0030 | 03 | U16 |  | RO
19 | 0x02 | 0x0031 | 03 | U16 |  | RO
20 | Riso low | 0x0036 | 03 | U16 |  | RO
21 | Island. Detected | 0x003E | 03 | U16 |  | RO
22 | Riso Test Fail | 0x004E | 03 | U16 |  | RO
23 | AFDD activated | 0x004F | 03 | U16 |  | RO
24 | AFDD wrong conf. | 0x0055 | 03 | U16 |  | RO
25 | Periodic Grid Off | 0x005A | 03 | U16 |  | RO
26 | Latch-Manual ent | 0x0060 | 03 | U16 |  | RO
27 | Power stage off-line | 0x0074 | 03 | U16 |  | RO
28 | Arc detector self-test | 0x0077 | 03 | U16 |  | RO
29 | Latch with “Reset by hand” | 0x007C | 03 | U16 |  | RO
30 | 4s step | 0x0080 | 03 | U16 |  | RO
31 | Wrong Sequence | 0x0098 | 03 | U16 |  | RO
32 | BackFeed OC | 0x009C | 03 | U16 |  | RO
33 | Transient Time for Permanent | 0x00BE | 03 | U16 |  | RO
34 | Transient Options for | 0x00C6 | 03 | U16 |  | RO
35 | Reset Reactive Power or PowerFactor (PF) management | 0x00CD | 03 | U16 |  | RO
36 | Reset Active Powermanagement | 0x00D7 | 03 | U16 |  | RO
37 | Not programmed | 0x00FF | 03 | U16 |  | RO
38 | 1s step | 0x0100 | 03 | U16 |  | RO
39 | Heartbeat counter | 0x012C | 03 | U16 |  | RO
40 | Inverter - Grid Reactive Power | 0x012D | 03 | U16 |  | RO | reactive_power
41 | Inverter - Grid Voltage | 0x012F | 03 | U16 |  | RO
42 | Inverter - Grid Active Power | 0x0131 | 03 | U16 |  | RO | ac_power
43 | Inverter - Grid Current | 0x0133 | 03 | U16 |  | RO
44 | 1s step | 0x0180 | 03 | U16 |  | RO
45 | Accuracy | 0x01F5 | 03 | U16 |  | RO
46 | Transient Time for Permanent | 0x01F7 | 03 | U16 |  | RO
47 | Transient Options for | 0x01F9 | 03 | U16 |  | RO
48 | Reset Active Powermanagement | 0x0203 | 03 | U16 |  | RO
49 | Reset Reactive Power or PowerFactor (PF) management | 0x0204 | 03 | U16 |  | RO
50 | Enable/Disable “Reset by Hand”function | 0x0321 | 03 | U16 |  | RO
51 | Partial Energy | 0x0432 | 03 | U32 |  | RO
52 | Weekly Energy | 0x0434 | 03 | U32 |  | RO
53 | Monthly Energy | 0x0436 | 03 | U32 |  | RO
54 | Yearly Energy | 0x0438 | 03 | U32 |  | RO
55 | Mean Grid Voltage | 0x0442 | 03 | U16 |  | RO
56 | Mean Output Current | 0x0444 | 03 | U16 |  | RO
57 | Output Active Power: | 0x0446 | 03 | U16 |  | RO
58 | Output Active Power: | 0x0448 | 03 | U16 |  | RO
59 | Output Active Power: | 0x044A | 03 | U16 |  | RO
60 | Output Active Power: | 0x044C | 03 | U16 |  | RO
61 | Reactive Power: | 0x044E | 03 | U16 |  | RO | reactive_power
62 | Power Factor: | 0x0450 | 03 | U16 |  | RO | power_factor
63 | Mean Grid Frequency | 0x0452 | 03 | U16 |  | RO
64 | Active Power on DC Input #1 | 0x0454 | 03 | U16 |  | RO | mppt1_power
65 | Voltage on DC Input #1 | 0x0456 | 03 | U16 |  | RO | mppt1_voltage
66 | Current on DC Input #1 | 0x0458 | 03 | U16 |  | RO | mppt1_current
67 | Active Power on DC Input #2 | 0x045A | 03 | U16 |  | RO | mppt2_power
68 | Voltage on DC Input #2 | 0x045C | 03 | U16 |  | RO | mppt2_voltage
69 | Current on DC Input #2 | 0x045E | 03 | U16 |  | RO | mppt2_current
70 | Isolation Resistance | 0x0466 | 03 | U16 |  | RO
71 | Max Leakage Current | 0x0468 | 03 | U16 |  | RO
72 | Active Power on DC Input #3 | 0x046A | 03 | U16 |  | RO | mppt3_power
73 | Voltage on DC Input #3 | 0x046C | 03 | U16 |  | RO | mppt3_voltage
74 | Current on DC Input #3 | 0x046E | 03 | U16 |  | RO | mppt3_current
75 | Family product | 0x0E42 | 03 | ASCII |  | RO
76 | Major release | 0x0E44 | 03 | ASCII |  | RO
77 | Minor release | 0x0E45 | 03 | ASCII |  | RO
78 | Build version | 0x0E46 | 03 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)