## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=3, STR=3)
제조사 | ABB
용량 | -
MPPT | 3
String/MPPT | 1
Total Strings | 3
H01 매칭 | 26/27
DER 매칭 | 33/33
총 레지스터 | 138
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Configuration fault (bad model) | 0x0078 | U16 |  | RO
2 | Dynamic ModeReactive Power Set Point:Reactive Power expressed asratio of Max apparent power (interm of cosφ) | 0x00DC | U16 |  | RO
3 | Permanent ModeReactive Power Set Point:Reactive Power expressed asratio of Max apparent power (interm of cosφ) | 0x00DE | U16 |  | RO
4 | Dynamic ModeReactive Power Set Point:Reactive Power expressed aspercentage of Max apparentpower in % steps | 0x00E1 | S16 |  | RO
5 | Permanent ModeReactive Power Set Point:Reactive Power expressed aspercentage of Max apparentpower in % steps | 0x00E3 | S16 |  | RO
6 | Dynamic ModeReactive Power Set Point:Reactive Power expressed aspercentage of Nominal Power in% steps | 0x01FB | S16 |  | RO
7 | Permanent ModeReactive Power Set Point:Reactive Power expressed aspercentage of Nominal Power in% steps | 0x01FF | S16 |  | RO
8 | Model Type | 0x03FE | ASCII |  | RO
9 | Daily Energy | 0x042E | U32 |  | RO | daily_energy
10 | Total Energy | 0x0430 | U32 |  | RO | cumulative_energy
11 | INNER_TEMP | 0x0460 | U16 |  | RO | temperature | Internal Temperature
12 | INNER_TEMP | 0x0462 | U16 |  | RO | temperature | Inverter Temperature
13 | DEVICE_MODEL | 0x0E43 | ASCII |  | RO |  | Product model
H01 MONITORING (78개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | 0x0B | 0x0000 | U16 |  | RO
2 | Waiting sun or grid | 0x0001 | U16 |  | RO
3 | 0x04 | 0x0002 | U16 |  | RO
4 | Initializing (system startup) | 0x0003 | U16 |  | RO
5 | Connecting to grid (switching-on DC/DC) | 0x0004 | U16 |  | RO
6 | Connecting to grid (switching-on DC/AC) | 0x0005 | U16 |  | RO
7 | Connected to grid | 0x0006 | U16 |  | RO
8 | Bulk UV | 0x000B | U16 |  | RO
9 | Connecting to grid (grid protection interface self-test) | 0x000C | U16 |  | RO
10 | Connecting to grid (safety checks) | 0x000E | U16 |  | RO
11 | Over temperature | 0x0013 | U16 |  | RO
12 | Executing auto-test | 0x001B | U16 |  | RO
13 | DC injection | 0x001F | U16 |  | RO
14 | IGBT not ready | 0x0021 | U16 |  | RO
15 | Mid-bulk over-voltage | 0x0024 | U16 |  | RO
16 | Riso low | 0x0026 | U16 |  | RO
17 | 0xF6 | 0x0028 | U16 |  | RO
18 | Undertemperature | 0x0030 | U16 |  | RO
19 | 0x02 | 0x0031 | U16 |  | RO
20 | Riso low | 0x0036 | U16 |  | RO
21 | Island. Detected | 0x003E | U16 |  | RO
22 | Riso Test Fail | 0x004E | U16 |  | RO
23 | AFDD activated | 0x004F | U16 |  | RO
24 | AFDD wrong conf. | 0x0055 | U16 |  | RO
25 | Periodic Grid Off | 0x005A | U16 |  | RO
26 | Latch-Manual ent | 0x0060 | U16 |  | RO
27 | Power stage off-line | 0x0074 | U16 |  | RO
28 | Arc detector self-test | 0x0077 | U16 |  | RO
29 | Latch with “Reset by hand” | 0x007C | U16 |  | RO
30 | 4s step | 0x0080 | U16 |  | RO
31 | Wrong Sequence | 0x0098 | U16 |  | RO
32 | BackFeed OC | 0x009C | U16 |  | RO
33 | Transient Time for Permanent | 0x00BE | U16 |  | RO
34 | Transient Options for | 0x00C6 | U16 |  | RO
35 | Reset Reactive Power or PowerFactor (PF) management | 0x00CD | U16 |  | RO
36 | Reset Active Powermanagement | 0x00D7 | U16 |  | RO
37 | Not programmed | 0x00FF | U16 |  | RO
38 | 1s step | 0x0100 | U16 |  | RO
39 | Heartbeat counter | 0x012C | U16 |  | RO
40 | Inverter - Grid Reactive Power | 0x012D | U16 |  | RO | reactive_power
41 | Inverter - Grid Voltage | 0x012F | U16 |  | RO
42 | Inverter - Grid Active Power | 0x0131 | U16 |  | RO | ac_power
43 | Inverter - Grid Current | 0x0133 | U16 |  | RO
44 | 1s step | 0x0180 | U16 |  | RO
45 | Accuracy | 0x01F5 | U16 |  | RO
46 | Transient Time for Permanent | 0x01F7 | U16 |  | RO
47 | Transient Options for | 0x01F9 | U16 |  | RO
48 | Reset Active Powermanagement | 0x0203 | U16 |  | RO
49 | Reset Reactive Power or PowerFactor (PF) management | 0x0204 | U16 |  | RO
50 | Enable/Disable “Reset by Hand”function | 0x0321 | U16 |  | RO
51 | Partial Energy | 0x0432 | U32 |  | RO
52 | Weekly Energy | 0x0434 | U32 |  | RO
53 | Monthly Energy | 0x0436 | U32 |  | RO
54 | Yearly Energy | 0x0438 | U32 |  | RO
55 | Mean Grid Voltage | 0x0442 | U16 |  | RO
56 | Mean Output Current | 0x0444 | U16 |  | RO
57 | Output Active Power: | 0x0446 | U16 |  | RO
58 | Output Active Power: | 0x0448 | U16 |  | RO
59 | Output Active Power: | 0x044A | U16 |  | RO
60 | Output Active Power: | 0x044C | U16 |  | RO
61 | Reactive Power: | 0x044E | U16 |  | RO | reactive_power
62 | Power Factor: | 0x0450 | U16 |  | RO | power_factor
63 | Mean Grid Frequency | 0x0452 | U16 |  | RO
64 | Active Power on DC Input #1 | 0x0454 | U16 |  | RO | mppt1_power
65 | Voltage on DC Input #1 | 0x0456 | U16 |  | RO | mppt1_voltage
66 | Current on DC Input #1 | 0x0458 | U16 |  | RO | mppt1_current
67 | Active Power on DC Input #2 | 0x045A | U16 |  | RO | mppt2_power
68 | Voltage on DC Input #2 | 0x045C | U16 |  | RO | mppt2_voltage
69 | Current on DC Input #2 | 0x045E | U16 |  | RO | mppt2_current
70 | Isolation Resistance | 0x0466 | U16 |  | RO
71 | Max Leakage Current | 0x0468 | U16 |  | RO
72 | Active Power on DC Input #3 | 0x046A | U16 |  | RO | mppt3_power
73 | Voltage on DC Input #3 | 0x046C | U16 |  | RO | mppt3_voltage
74 | Current on DC Input #3 | 0x046E | U16 |  | RO | mppt3_current
75 | Family product | 0x0E42 | ASCII |  | RO
76 | Major release | 0x0E44 | ASCII |  | RO
77 | Minor release | 0x0E45 | ASCII |  | RO
78 | Build version | 0x0E46 | U16 |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Wrong input mode | 0x0011 | U16 |  | RO
2 | Remove “Reset by Hand” latch-state | 0x00B5 | U16 |  | RO
3 | Timeout for Dynamic mode | 0x00BF | U16 |  | RO
4 | Dynamic Mode | 0x00D2 | U16 |  | RO
5 | Permanent Mode | 0x00D4 | U16 |  | RO
6 | Set active mode | 0x01F6 | U16 |  | RO
7 | Timeout for Dynamic mode | 0x01F8 | U16 |  | RO
8 | Reactive Power control mode | 0x01FA | U16 |  | RO
9 | Dynamic Mode | 0x01FC | U16 |  | RO
10 | Permanent Mode | 0x0200 | U16 |  | RO
11 | Remove “Reset by Hand” latch-state | 0x0322 | U16 |  | RO
12 | Global State | 0x041A | U16 |  | RO | inverter_status
13 | Alarm State | 0x041B | U16 |  | RO
14 | DC/DC Converter State | 0x041C | U16 |  | RO
15 | DC/AC Converter State | 0x041D | U16 |  | RO
16 | Derating State | 0x041E | U16 |  | RO
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Post-alarm actions (recovery) | 0x0007 | U16 |  | RO
2 | Post-alarm actions (pause) | 0x0008 | U16 |  | RO
3 | Ground fault | 0x0009 | U16 |  | RO
4 | Over-temperature fault | 0x000A | U16 |  | RO
5 | Grid protection interface self-test fault | 0x000D | U16 |  | RO
6 | Leakage fault | 0x000F | U16 |  | RO
7 | Internal error | 0x0010 | U16 |  | RO
8 | Grid fault | 0x0012 | U16 |  | RO
9 | Cap. Fault | 0x0014 | U16 |  | RO
10 | Internal error | 0x0015 | U16 |  | RO
11 | Internal error | 0x0016 | U16 |  | RO
12 | Leak fault | 0x0017 | U16 |  | RO
13 | Under-temperature fault | 0x0018 | U16 |  | RO
14 | Internal error | 0x001C | U16 |  | RO
15 | Grounding-kit fault | 0x001D | U16 |  | RO
16 | SW bundle not valid fault | 0x001E | U16 |  | RO
17 | Communication error | 0x0023 | U16 |  | RO
18 | Temperature sensors fault | 0x0029 | U16 |  | RO
19 | Grid sequence fault | 0x002A | U16 |  | RO
20 | Internal error | 0x002C | U16 |  | RO
21 | Internal error | 0x002D | U16 |  | RO
22 | Arc fault | 0x0033 | U16 |  | RO
23 | Arc detector self-test fault | 0x0035 | U16 |  | RO
24 | AFDD fault | 0x0052 | U16 |  | RO
25 | Internal error | 0x005B | U16 |  | RO
26 | Grid conn. fault | 0x005F | U16 |  | RO
27 | Arc detector wrong configuration fault | 0x0076 | U16 |  | RO
28 | Power stage communication fault | 0x0096 | U16 |  | RO
29 | Configuration fault (bad global-settings) | 0x0097 | U16 |  | RO
30 | Aux. Bulk Feed Conn. Error | 0x00A7 | U16 |  | RO
31 | Ground Kit Self Test Error | 0x00AA | U16 |  | RO

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | ABB
용량 | -
MPPT | 3 (PDF max 3개)
String | 3 (1/MPPT)
H01 매칭 | 26/27
DER 매칭 | 33/33
총 레지스터 | 138
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 13
MONITORING | 78
STATUS | 16
ALARM | 31
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | HANDLER | O | - | -
13 | cumulative_energy | PDF | O | 0x0430 | Total Energy
14 | cumulative_energy_low | PDF | - | - | -
15 | status | PDF | O | 0x041A | Global State
16 | alarm1 | PDF | O | 0x0009 | Ground fault
17 | alarm2 | PDF | O | 0x0010 | Internal error
18 | alarm3 | PDF | O | 0x0015 | Internal error
19 | mppt1_voltage | PDF | O | 0x0456 | Voltage on DC Input #1
20 | mppt1_current | PDF | O | 0x0458 | Current on DC Input #1
21 | mppt2_voltage | PDF | O | 0x045C | Voltage on DC Input #2
22 | mppt2_current | PDF | O | 0x045E | Current on DC Input #2
23 | mppt3_voltage | PDF | O | 0x046C | Voltage on DC Input #3
24 | mppt3_current | PDF | O | 0x046E | Current on DC Input #3
25 | string1_current | HANDLER | O | 0x0458 | Current on DC Input #1
26 | string2_current | HANDLER | O | 0x045E | Current on DC Input #2
27 | string3_current | HANDLER | O | 0x046E | Current on DC Input #3