## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | EG4-18KPV-12LV-Modbus-Protocol
프로토콜 버전
설비 타입 | inverter
MPPT | 3
String | 3
String 모니터링 | No (MPPT당 1 String)
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | EG4-18KPV-12LV-Modbus-Protocol.pdf
추출 일시 | 2026-04-03 15:58
H01 매칭 | 26/26
DER 매칭 | 33/33
추출 레지스터 | 198
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | DEVICE_MODEL (PDF) | PDF |  | TEXT |  | RO |  | EG4 18KPV-12LV
2 | SN[6] -Product code | 0x0005 | 04 | U16 |  | RO
3 | BUS Voltage high | 0x0013 | 04 | U16 |  | RO
4 | RunningTime H | 0x0046 | 04 | U16 |  | RO
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | State | 0x0000 | 04 | U16 |  | RO | inverter_status | see operating mode definitiontable
2 | BatStatus0 BMS_ | 0x0055 | 04 | U16 |  | RO
3 | BatStatus1 BMS_ | 0x0056 | 04 | U16 |  | RO
4 | BatStatus2 BMS_ | 0x0057 | 04 | U16 |  | RO
5 | BatStatus3 BMS_ | 0x0058 | 04 | U16 |  | RO
6 | BatStatus4 BMS_ | 0x0059 | 04 | U16 |  | RO
7 | BatStatus5 BMS_ | 0x005A | 04 | U16 |  | RO
8 | BatStatus6 BMS_ | 0x005B | 04 | U16 |  | RO
9 | BatStatus7 BMS_ | 0x005C | 04 | U16 |  | RO
10 | BatStatus8 BMS_ | 0x005D | 04 | U16 |  | RO
11 | BatStatus9 BMS_ | 0x005E | 04 | U16 |  | RO
12 | BatStatus INV_ | 0x005F | 04 | U16 |  | RO
13 | BMSFWUpdateState | 0x0069 | 04 | U16 |  | RO
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | FaultCode L | 0x003C | 04 | U16 |  | RO
2 | FaultCode H | 0x003D | 04 | U16 |  | RO
3 | WarningCode L | 0x003E | 04 | U16 |  | RO
4 | WarningCode H | 0x003F | 04 | U16 |  | RO
5 | uwAutoTestDefaultTime | 0x0049 | 04 | U16 |  | RO
6 | FaultCode BMS_ | 0x0063 | 04 | U16 |  | RO
7 | WarningCode BMS_ | 0x0064 | 04 | U16 |  | RO
8 | AFCIFlag.ArcAlarmCH1 | 0x0090 | 04 | U16 |  | RO |  | Bit0

## 2_H01
H01 모니터링 매칭 — 26/26
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | HANDLER | O | - | - | U16 | W |  | handler 계산: 1순위: PDF Total DC Power, 2순위: sum(MPPT_N_power)
13 | cumulative_energy | PDF | O | 0x002E | Einv all L_ | U16 | kWh | 0.1 | kWh→Wh (*1000)
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x0000 | State | U16 |  |  | 113=SetComposedPhas, 114=ClearFunction, 115=OVFDerateStartP, 116=PtoUserStartdis, 118=VbatStartDerati, 119=wCT PowerOffset... (+5)
16 | alarm1 | PDF | O | 0x003C | FaultCode L | U16 |  |  | 0=Internal commun, 1=Model fault (E0, 8=Paralleling CAN, 9=Master unit los, 10=Multiple master, 11=AC input incons... (+10)
17 | alarm2 | PDF | O | 0x003D | FaultCode H | U16
18 | alarm3 | PDF | O | 0x003E | WarningCode L | U16
19 | mppt1_voltage | PDF | O | 0x0001 | Vpv1 | U16 | V | 0.1
20 | mppt1_current | HANDLER | O | - | - | U16 | A |  | handler 계산: mppt1_power / mppt1_voltage
21 | mppt2_voltage | PDF | O | 0x0002 | Vpv2 | U16 | V | 0.1
22 | mppt2_current | HANDLER | O | - | - | U16 | A |  | handler 계산: mppt2_power / mppt2_voltage
23 | mppt3_voltage | PDF | O | 0x0003 | Vpv3 | U16 | V | 0.1
24 | mppt3_current | HANDLER | O | - | - | U16 | A |  | handler 계산: mppt3_power / mppt3_voltage
25 | string1_current | HANDLER | O | - | - | U16 | A
26 | string2_current | HANDLER | O | - | - | U16 | A
27 | string3_current | HANDLER | O | - | - | U16 | A

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 3ch / String 3ch
MPPT 채널 수 | 3
String 채널 수 | 3
String 모니터링 | No (MPPT당 1 String)
MPPT 채널 H01 매칭 (6개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x0001 | Vpv1 | U16 | V | 0.1
2 | mppt1_current | HANDLER | O | - | - | U16 | A |  | handler 계산: mppt1_power / mppt1_voltage
3 | mppt2_voltage | PDF | O | 0x0002 | Vpv2 | U16 | V | 0.1
4 | mppt2_current | HANDLER | O | - | - | U16 | A |  | handler 계산: mppt2_power / mppt2_voltage
5 | mppt3_voltage | PDF | O | 0x0003 | Vpv3 | U16 | V | 0.1
6 | mppt3_current | HANDLER | O | - | - | U16 | A |  | handler 계산: mppt3_power / mppt3_voltage
String 채널 H01 매칭 (3개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | - | - | U16 | A
2 | string2_current | HANDLER | O | - | - | U16 | A
3 | string3_current | HANDLER | O | - | - | U16 | A
MONITORING 전체 (174개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Vpv1 | 0x0001 | 04 | U16 | V 0.1 | RO | mppt1_voltage
2 | Bit0 | 0x0001 | 03 | U16 |  | RO
3 | Vpv2 | 0x0002 | 04 | U16 | V 0.1 | RO | mppt2_voltage
4 | illegal dataaddress | 0x0002 | 03 | U16 |  | RO
5 | Vpv3 | 0x0003 | 04 | U16 | V 0.1 | RO | mppt3_voltage
6 | illegal data value | 0x0003 | 03 | U16 |  | RO
7 | Slave read andwrite failure | 0x0004 | 04 | U16 |  | RO
8 | Slave is busy | 0x0006 | 04 | U16 |  | RO
9 | Ppv1 | 0x0007 | 04 | U16 |  | RO | mppt1_power
10 | Ppv2 | 0x0008 | 04 | U16 |  | RO | mppt2_power
11 | Ppv3 | 0x0009 | 04 | U16 |  | RO | mppt3_power
12 | Pcharge | 0x000A | 04 | U16 |  | RO
13 | Pdischarge | 0x000B | 04 | U16 |  | RO
14 | L1_VOLTAGE | 0x000C | 04 | U16 | V 0.1 | RO | r_voltage
15 | L2_VOLTAGE | 0x000D | 04 | U16 | V 0.1 | RO | s_voltage
16 | L3_VOLTAGE | 0x000E | 04 | U16 | V 0.1 | RO | t_voltage
17 | L1_FREQUENCY | 0x000F | 04 | U16 | Hz 0.01 | RO | frequency
18 | Pinv | 0x0010 | 04 | U16 |  | RO
19 | Prec | 0x0011 | 04 | U16 |  | RO
20 | IinvRMS | 0x0012 | 04 | U16 | A 0.01 | RO
21 | VepsR | 0x0014 | 04 | U16 | V 0.1 | RO
22 | VepsS | 0x0015 | 04 | U16 | V 0.1 | RO
23 | VepsT | 0x0016 | 04 | U16 | V 0.1 | RO
24 | Feps | 0x0017 | 04 | U16 | Hz 0.01 | RO
25 | Peps | 0x0018 | 04 | U16 |  | RO
26 | Seps | 0x0019 | 04 | U16 |  | RO
27 | Ptogrid | 0x001A | 04 | U16 |  | RO
28 | Ptouser | 0x001B | 04 | U16 |  | RO
29 | Epv1 day_ | 0x001C | 04 | U16 | kWh 0.1 | RO
30 | Epv2 day_ | 0x001D | 04 | U16 | kWh 0.1 | RO
31 | Epv3 day_ | 0x001E | 04 | U16 | kWh 0.1 | RO
32 | Einv day_ | 0x001F | 04 | U16 | kWh 0.1 | RO | daily_energy
33 | Erec day_ | 0x0020 | 04 | U16 | kWh 0.1 | RO
34 | Echg day_ | 0x0021 | 04 | U16 | kWh 0.1 | RO
35 | Edischg day_ | 0x0022 | 04 | U16 | kWh 0.1 | RO
36 | Eeps day_ | 0x0023 | 04 | U16 | kWh 0.1 | RO
37 | Etogrid day_ | 0x0024 | 04 | U16 | kWh 0.1 | RO
38 | Etouser day_ | 0x0025 | 04 | U16 | kWh 0.1 | RO
39 | GridVoltLimit3High | 0x0026 | 04 | U16 | V 0.1 | RO
40 | GridVoltLimit3LowTime | 0x0027 | 04 | U16 |  | RO
41 | Epv1 all L_ | 0x0028 | 04 | U16 | kWh 0.1 | RO
42 | Epv1 all H_ | 0x0029 | 04 | U16 | kWh 0.1 | RO
43 | Epv2 all L_ | 0x002A | 04 | U16 | kWh 0.1 | RO
44 | Epv2 all H_ | 0x002B | 04 | U16 | kWh 0.1 | RO
45 | Epv3 all L_ | 0x002C | 04 | U16 | kWh 0.1 | RO
46 | Epv3 all H_ | 0x002D | 04 | U16 | kWh 0.1 | RO
47 | Einv all L_ | 0x002E | 04 | U16 | kWh 0.1 | RO | cumulative_energy
48 | Einv all H_ | 0x002F | 04 | U16 | kWh 0.1 | RO | cumulative_energy
49 | Erec all L_ | 0x0030 | 04 | U16 | kWh 0.1 | RO
50 | Erec all H_ | 0x0031 | 04 | U16 | kWh 0.1 | RO
51 | Echg all L_ | 0x0032 | 04 | U16 | kWh 0.1 | RO
52 | Echg all H_ | 0x0033 | 04 | U16 | kWh 0.1 | RO
53 | Edischg all L_ | 0x0034 | 04 | U16 | kWh 0.1 | RO
54 | Edischg all H_ | 0x0035 | 04 | U16 | kWh 0.1 | RO
55 | Eeps all L_ | 0x0036 | 04 | U16 | kWh 0.1 | RO
56 | Eeps all H_ | 0x0037 | 04 | U16 | kWh 0.1 | RO
57 | Etogrid all L_ | 0x0038 | 04 | U16 | kWh 0.1 | RO
58 | Etogrid all H_ | 0x0039 | 04 | U16 | kWh 0.1 | RO
59 | Etouser all L_ | 0x003A | 04 | U16 | kWh 0.1 | RO
60 | Etouser all H_ | 0x003B | 04 | U16 | kWh 0.1 | RO
61 | Tinner | 0x0040 | 04 | U16 |  | RO
62 | Tradiator1 | 0x0041 | 04 | U16 |  | RO
63 | Tradiator2 | 0x0042 | 04 | U16 |  | RO
64 | Tbat | 0x0043 | 04 | U16 |  | RO
65 | ACChgStartHour | 0x0044 | 04 | U16 |  | RO
66 | ACChgEndHour | 0x0045 | 04 | U16 |  | RO
67 | AutoTestStart | 0x0047 | 04 | U16 |  | RO
68 | wAutoTestLimit | 0x0048 | 04 | U16 |  | RO
69 | uwAutoTestTripValue | 0x004A | 04 | U16 |  | RO
70 | uwAutoTestTripTime | 0x004B | 04 | U16 |  | RO
71 | ChgFirstStartHour | 0x004C | 04 | U16 |  | RO
72 | ACInputType | 0x004D | 04 | U16 |  | RO
73 | ChgFirstStartHour1 | 0x004E | 04 | U16 |  | RO
74 | ChgFirstStartHour2 | 0x0050 | 04 | U16 |  | RO
75 | MaxChgCurr | 0x0051 | 04 | U16 | A 0.01 | RO
76 | MaxDischgCurr | 0x0052 | 04 | U16 | A 0.01 | RO
77 | ChargeVoltRef | 0x0053 | 04 | U16 | V 0.1 | RO
78 | DischgCutVolt | 0x0054 | 04 | U16 | V 0.1 | RO
79 | BatParallelNum | 0x0060 | 04 | U16 |  | RO
80 | BatCapacity | 0x0061 | 04 | U16 |  | RO
81 | BatCurrent BMS_ | 0x0062 | 04 | U16 | A 0.01 | RO
82 | ChargeCurr | 0x0065 | 04 | U16 |  | RO
83 | MinCellVolt BMS_ | 0x0066 | 04 | U16 | V 0.001 | RO
84 | MaxCellTemp BMS_ | 0x0067 | 04 | U16 | ℃ 0.1 | RO
85 | MinCellTemp BMS_ | 0x0068 | 04 | U16 | ℃ 0.1 | RO
86 | CycleCnt BMS_ | 0x006A | 04 | U16 |  | RO
87 | BatVoltSample INV_ | 0x006B | 04 | U16 | V 0.1 | RO
88 | 0.1℃ | 0x006C | 04 | U16 | ℃ 0.1 | RO
89 | 0.1℃ | 0x006D | 04 | U16 | ℃ 0.1 | RO
90 | 0.1℃ | 0x006E | 04 | U16 | ℃ 0.1 | RO
91 | 0.1℃ | 0x006F | 04 | U16 | ℃ 0.1 | RO
92 | 0.1℃ | 0x0070 | 04 | U16 | ℃ 0.1 | RO
93 | MasterOrSlave | 0x0071 | 04 | U16 |  | RO
94 | ClearFunction | 0x0072 | 04 | U16 |  | RO
95 | OVFDerateStartPoint | 0x0073 | 04 | U16 | Hz 0.01 | RO
96 | PtoUserStartdischg | 0x0074 | 04 | U16 |  | RO
97 | VbatStartDerating | 0x0076 | 04 | U16 | V 0.1 | RO
98 | wCT PowerOffset_ | 0x0077 | 04 | U16 |  | RO
99 | VBusP | 0x0078 | 04 | U16 | V 0.1 | RO
100 | GenVolt | 0x0079 | 04 | U16 | V 0.1 | RO
101 | GenFreq | 0x007A | 04 | U16 | Hz 0.01 | RO
102 | GenPower | 0x007B | 04 | U16 |  | RO
103 | Egen day_ | 0x007C | 04 | U16 | kWh 0.1 | RO
104 | Egen all L_ | 0x007D | 04 | U16 | kWh 0.1 | RO
105 | Egen all H_ | 0x007E | 04 | U16 | kWh 0.1 | RO
106 | EPSVoltL1N | 0x007F | 04 | U16 | V 0.1 | RO
107 | EPSVoltL2N | 0x0080 | 04 | U16 | V 0.1 | RO
108 | Peps L1N_ | 0x0081 | 04 | U16 |  | RO
109 | Peps L2N_ | 0x0082 | 04 | U16 |  | RO
110 | Seps L1N_ | 0x0083 | 04 | U16 |  | RO
111 | BatCellVoltLow | 0x0084 | 04 | U16 | V 0.1 | RO
112 | EepsL1N day_ | 0x0085 | 04 | U16 | kWh 0.1 | RO
113 | EepsL2N day_ | 0x0086 | 04 | U16 | kWh 0.1 | RO
114 | EepsL1N all L_ | 0x0087 | 04 | U16 | kWh 0.1 | RO
115 | EepsL1N all H_ | 0x0088 | 04 | U16 | kWh 0.1 | RO
116 | EepsL2N all L_ | 0x0089 | 04 | U16 | kWh 0.1 | RO
117 | EepsL2N all H_ | 0x008A | 04 | U16 | kWh 0.1 | RO
118 | DischgPowerPercentCMD | 0x008B | 04 | U16 | % 0.1 | RO
119 | AFCI CurrCH1_ | 0x008C | 04 | U16 |  | RO
120 | AFCI CurrCH2_ | 0x008D | 04 | U16 |  | RO
121 | AFCI CurrCH3_ | 0x008E | 04 | U16 |  | RO
122 | AFCI CurrCH4_ | 0x008F | 04 | U16 |  | RO
123 | AFCI ArcCH1_ | 0x0091 | 04 | U16 |  | RO
124 | AFCI ArcCH2_ | 0x0092 | 04 | U16 |  | RO
125 | AFCI ArcCH3_ | 0x0093 | 04 | U16 |  | RO
126 | AFCI ArcCH4_ | 0x0094 | 04 | U16 |  | RO
127 | AFCI MaxArcCH1_ | 0x0095 | 04 | U16 |  | RO
128 | AFCI MaxArcCH2_ | 0x0096 | 04 | U16 |  | RO
129 | AFCI MaxArcCH3_ | 0x0097 | 04 | U16 |  | RO
130 | AFCI MaxArcCH4_ | 0x0098 | 04 | U16 |  | RO
131 | ACFirstEndHour | 0x0099 | 04 | U16 |  | RO
132 | ACFirstStartHour1 | 0x009A | 04 | U16 |  | RO
133 | ACFirstEndHour1 | 0x009B | 04 | U16 |  | RO
134 | ACFirstStartHour2 | 0x009C | 04 | U16 |  | RO
135 | ACFirstEndHour2 | 0x009D | 04 | U16 |  | RO
136 | ACChgStartVolt | 0x009E | 04 | U16 | V 0.1 | RO
137 | ACChgEndVolt | 0x009F | 04 | U16 | V 0.1 | RO
138 | ACChgStartSOC | 0x00A0 | 04 | U16 |  | RO
139 | ACChgEndSOC | 0x00A1 | 04 | U16 |  | RO
140 | BatLowVoltage | 0x00A2 | 04 | U16 | V 0.1 | RO
141 | BatLowBackVoltage | 0x00A3 | 04 | U16 | V 0.1 | RO
142 | BatLowSOC | 0x00A4 | 04 | U16 |  | RO
143 | BatLowBackSOC | 0x00A5 | 04 | U16 |  | RO
144 | BatLowtoUtilityVoltage | 0x00A6 | 04 | U16 | V 0.1 | RO
145 | BatLowtoUtilitySOC | 0x00A7 | 04 | U16 |  | RO
146 | ACCharge Bat Current | 0x00A8 | 04 | U16 | A | RO
147 | OngridEOD Voltage_ | 0x00A9 | 04 | U16 | V 0.1 | RO
148 | SOCCurve BatVolt1_ | 0x00AB | 04 | U16 | V 0.1 | RO
149 | SOCCurve BatVolt 2_ | 0x00AC | 04 | U16 | V 0.1 | RO
150 | SOCCurve SOC1_ | 0x00AD | 04 | U16 | % 1 | RO
151 | SOCCurve SOC2_ | 0x00AE | 04 | U16 | % 1 | RO
152 | SOCCurve InnerResistance_ | 0x00AF | 04 | U16 |  | RO
153 | MaxGridInputPower | 0x00B0 | 04 | U16 | W | RO
154 | GenRatePower | 0x00B1 | 04 | U16 | W | RO
155 | uFunctionEn2.ACCTDirection | 0x00B3 | 04 | U16 |  | RO
156 | AFCIArcThreshold | 0x00B4 | 04 | U16 |  | RO
157 | VoltWatt V1_ | 0x00B5 | 04 | U16 | V 0.1 | RO
158 | VoltWatt V2_ | 0x00B6 | 04 | U16 | V 0.1 | RO
159 | VoltWatt DelayTime_ | 0x00B7 | 04 | U16 |  | RO
160 | VoltWatt P2_ | 0x00B8 | 04 | U16 |  | RO
161 | Vref QV_ | 0x00B9 | 04 | U16 | V 0.1 | RO
162 | Vref filtertime_ | 0x00BA | 04 | U16 |  | RO
163 | Q3 QV_ | 0x00BB | 04 | U16 |  | RO
164 | Q4 QV_ | 0x00BC | 04 | U16 |  | RO
165 | P1 QP_ | 0x00BD | 04 | U16 |  | RO
166 | P2 QP_ | 0x00BE | 04 | U16 |  | RO
167 | P3 QP_ | 0x00BF | 04 | U16 |  | RO
168 | P4 QP_ | 0x00C0 | 04 | U16 |  | RO
169 | UVFIncreaseRatio | 0x00C1 | 04 | U16 | Hz | RO
170 | GenChgStartVolt | 0x00C2 | 04 | U16 | V 0.1 | RO
171 | GenChgEndVolt | 0x00C3 | 04 | U16 | V 0.1 | RO
172 | GenChgStartSOC | 0x00C4 | 04 | U16 |  | RO
173 | GenChgEndSOC | 0x00C5 | 04 | U16 |  | RO
174 | MaxGenChgBatCurr | 0x00C6 | 04 | U16 | A | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)