## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | 1
프로토콜 버전 | V3.5
설비 타입 | inverter
MPPT | 12
String | 24
String 모니터링 | Yes
IV Scan | Yes
IV Data Points | 100
IV Trackers | 2
원본 파일 | 1_KSG1.250K.Inverter.Modbus.Communication.Protocol.3.5.pdf
추출 일시 | 2026-04-03 15:58
H01 매칭 | 65/65
DER 매칭 | 33/33
추출 레지스터 | 409
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | PBUS voltage | 0x0BC4 | 04 | U16 | V 0.1 | RO
2 | NBUS voltage | 0x0BC5 | 04 | U16 | V 0.1 | RO |  | 1-5K not have.
3 | INNER_TEMP | 0x0BD2 | 04 | S16 |  | RO | temperature | Module temperature ¦ 1-5K not have.
4 | Total energy yield | 0x0BDE | 04 | U32 | Kwh 0.1 | RO | cumulative_energy
5 | Daily energy yield | 0x0BE2 | 04 | U16 | Kwh | RO | cumulative_energy
6 | Apparent power | 0x0BEC | 04 | S32 | VA 1 | RO
7 | DC insulation resistance | 0x0BF1 | 04 | U16 |  | RO |  | 1-5K not have.
8 | Running Time | 0x0C12 | 04 | U32 |  | RO
9 | Number of gridconnection | 0x0C16 | 04 | U32 |  | RO
10 | Setting value of ratedpower for anti backflow | 0x0C7C | 04 | U16 |  | RO
11 | Machine model | 0x0C80 | 04 | ASCII |  | RO |  | ASCII code
12 | Inverter SN | 0x0C86 | 04 | ASCII |  | RO |  | ASCII character
13 | LCD Model Setting | 0x0C94 | 04 | U16 |  | RO |  | Table 3.3.5
14 | Inverter Model（New） | 0x0C95 | 04 | ASCII |  | RO |  | ASCII character
15 | Setting Inverter SN | 0x0CEF | 04 | ASCII |  | RO
16 | LCD Model Setting | 0x0D04 | 04 | U16 |  | RO
17 | DEVICE_MODEL | 0x0D05 | 04 | U16 |  | RO |  | Inverter Model
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Operating mode of theinverter | 0x0BD6 | 04 | U16 |  | RO | inverter_status | Table 3.1.4
2 | Input mode | 0x0BDD | 04 | U16 |  | RO |  | Table 3.1.8
3 | I/V Scan-status | 0x0C36 | 04 | U16 | V | RO |  | Table 3.1.15
4 | Grid protected mode | 0x0CAE | 04 | U16 |  | RO
5 | Set the reactivecontrol mode | 0x0FA6 | 04 | U16 |  | RO |  | Table 3.4.5
6 | Input ModeSettings | 0x0FAC | 04 | U16 |  | RO
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | AC Relay Fault | 0x000E | 04 | U16 |  | RO
2 | DSP alarm code | 0x0BD3 | 04 | U16 |  | RO |  | Table 3.1.2
3 | DSP error code | 0x0BD4 | 04 | U32 |  | RO |  | Table 3.1.3
4 | ARM alarm code | 0x0BDC | 04 | U16 |  | RO |  | Table 3.1.6
5 | Fuse alarm information | 0x0C81 | 04 | U32 |  | RO
6 | Over temperaturederating warningenable | 0x0C9B | 04 | U16 |  | RO
7 | Fault recovery time | 0x0CB0 | 04 | U16 |  | RO
8 | Clear FaultRecord | 0x0FC1 | 04 | U16 |  | RO
9 | Cancel power factor control (defaultpower factor: 1) | 0xFFFF | 04 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 65/65
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x0B96 | PV12 input power | S32 | W | 1
13 | cumulative_energy | PDF | O | 0x0BE0 | Annual energy yield | U32 | Kwh |  | Kwh→Wh (*1000)
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x0BD6 | Operating mode of theinverter | U16 |  |  | 0=System initiali, 1=Waiting, 2=Pre-detection, 3=Normal, 4=Error, 5=Permanent error... (+4)
16 | alarm1 | PDF | O | 0x0BD3 | DSP alarm code | U16 |  |  | 16=Remote Off, 17=reserve, 18=SPI Communicati, 19=SPI2 Communicat, 20=GFCI Over Fault, 21=GFCI Device Fau... (+10)
17 | alarm2 | PDF | O | 0x0BD4 | DSP error code | U32
18 | alarm3 | PDF | O | 0x0BDC | ARM alarm code | U16
19 | mppt1_voltage | PDF | O | 0x0BB8 | PV1 input voltage | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x0BBB | PV1 input current | U16 | A | 0.01
21 | mppt2_voltage | PDF | O | 0x0BB9 | PV2 input voltage | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x0BBC | PV2 input current | U16 | A | 0.01
23 | mppt3_voltage | PDF | O | 0x0BBA | PV3 input voltage | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x0BBD | PV3 input current | U16 | A | 0.01
25 | mppt4_voltage | PDF | O | 0x0BB4 | PV4 input voltage | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x0BB5 | PV4 input current | S16 | A | 0.01
27 | mppt5_voltage | PDF | O | 0x0BB0 | PV5 input voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x0BB1 | PV5 input current | S16 | A | 0.01
29 | mppt6_voltage | PDF | O | 0x0BAC | PV6 input voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x0BAD | PV6 input current | S16 | A | 0.01
31 | mppt7_voltage | PDF | O | 0x0BA8 | PV7 input voltage | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x0BA9 | PV7 input current | S16 | A | 0.01
33 | mppt8_voltage | PDF | O | 0x0BA4 | PV8 input voltage | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x0BA5 | PV8 input current | S16 | A | 0.01
35 | mppt9_voltage | PDF | O | 0x0BA0 | PV9 input voltage | U16 | V | 0.1
36 | mppt9_current | PDF | O | 0x0BA1 | PV9 input current | S16 | A | 0.01
37 | mppt10_voltage | PDF | O | 0x0B9C | PV10 input voltage | U16 | V | 0.1
38 | mppt10_current | PDF | O | 0x0B9D | PV10 input current | S16 | A | 0.01
39 | mppt11_voltage | PDF | O | 0x0B98 | PV11 input voltage | U16 | V | 0.1
40 | mppt11_current | PDF | O | 0x0B99 | PV11 input current | S16 | A | 0.01
41 | mppt12_voltage | PDF | O | 0x0B94 | PV12 input voltage | U16 | V | 0.1
42 | mppt12_current | PDF | O | 0x0B95 | PV12 input current | S16 | A | 0.01
43 | string1_current | PDF | O | 0x0BF8 | PV1 String current 1 | S16 | A | 0.01
44 | string2_current | PDF | O | 0x0BF9 | PV1 String current 2 | S16 | A | 0.01
45 | string3_current | PDF | O | 0x0BFA | PV1 String current 3 | S16 | A | 0.01
46 | string4_current | PDF | O | 0x0BFB | PV1 String current 4 | S16 | A | 0.01
47 | string5_current | PDF | O | 0x0BFC | PV2 String current 1 | S16 | A | 0.01
48 | string6_current | PDF | O | 0x0BFD | PV2 String current 2 | S16 | A | 0.01
49 | string7_current | PDF | O | 0x0BFE | PV2 String current 3 | S16 | A | 0.01
50 | string8_current | PDF | O | 0x0BFF | PV2 String current 4 | S16 | A | 0.01
51 | string9_current | PDF | O | 0x0C00 | PV3 String current 1 | S16 | A | 0.01
52 | string10_current | PDF | O | 0x0C01 | PV3 String current 2 | S16 | A | 0.01
53 | string11_current | PDF | O | 0x0C02 | PV3 String current 3 | S16 | A | 0.01
54 | string12_current | PDF | O | 0x0C03 | PV3 String current 4 | S16 | A | 0.01
55 | string13_current | PDF | O | 0x0C04 | PV4 String current 1 | S16 | A | 0.01
56 | string14_current | PDF | O | 0x0C05 | PV4 String current 2 | S16 | A | 0.01
57 | string15_current | PDF | O | 0x0C06 | PV4 String current 3 | S16 | A | 0.01
58 | string16_current | PDF | O | 0x0C07 | PV4 String current 4 | S16 | A | 0.01
59 | string17_current | PDF | O | 0x0C08 | PV5 String current 1 | S16 | A | 0.01
60 | string18_current | PDF | O | 0x0C09 | PV5 String current 2 | S16 | A | 0.01
61 | string19_current | PDF | O | 0x0C0A | PV5 String current 3 | S16 | A | 0.01
62 | string20_current | PDF | O | 0x0C0B | PV5 String current 4 | S16 | A | 0.01
63 | string21_current | PDF | O | 0x0C0C | PV6 String current 1 | S16 | A | 0.01
64 | string22_current | PDF | O | 0x0C0D | PV6 String current 2 | S16 | A | 0.01
65 | string23_current | PDF | O | 0x0C0E | PV6 String current 3 | S16 | A | 0.01
66 | string24_current | PDF | O | 0x0C0F | PV6 String current 4 | S16 | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 12ch / String 24ch
MPPT 채널 수 | 12
String 채널 수 | 24
String 모니터링 | Yes
MPPT 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x0BB8 | PV1 input voltage | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x0BBB | PV1 input current | U16 | A | 0.01
3 | mppt2_voltage | PDF | O | 0x0BB9 | PV2 input voltage | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x0BBC | PV2 input current | U16 | A | 0.01
5 | mppt3_voltage | PDF | O | 0x0BBA | PV3 input voltage | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x0BBD | PV3 input current | U16 | A | 0.01
7 | mppt4_voltage | PDF | O | 0x0BB4 | PV4 input voltage | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x0BB5 | PV4 input current | S16 | A | 0.01
9 | mppt5_voltage | PDF | O | 0x0BB0 | PV5 input voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x0BB1 | PV5 input current | S16 | A | 0.01
11 | mppt6_voltage | PDF | O | 0x0BAC | PV6 input voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x0BAD | PV6 input current | S16 | A | 0.01
13 | mppt7_voltage | PDF | O | 0x0BA8 | PV7 input voltage | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x0BA9 | PV7 input current | S16 | A | 0.01
15 | mppt8_voltage | PDF | O | 0x0BA4 | PV8 input voltage | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x0BA5 | PV8 input current | S16 | A | 0.01
17 | mppt9_voltage | PDF | O | 0x0BA0 | PV9 input voltage | U16 | V | 0.1
18 | mppt9_current | PDF | O | 0x0BA1 | PV9 input current | S16 | A | 0.01
19 | mppt10_voltage | PDF | O | 0x0B9C | PV10 input voltage | U16 | V | 0.1
20 | mppt10_current | PDF | O | 0x0B9D | PV10 input current | S16 | A | 0.01
21 | mppt11_voltage | PDF | O | 0x0B98 | PV11 input voltage | U16 | V | 0.1
22 | mppt11_current | PDF | O | 0x0B99 | PV11 input current | S16 | A | 0.01
23 | mppt12_voltage | PDF | O | 0x0B94 | PV12 input voltage | U16 | V | 0.1
24 | mppt12_current | PDF | O | 0x0B95 | PV12 input current | S16 | A | 0.01
String 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x0BF8 | PV1 String current 1 | S16 | A | 0.01
2 | string2_current | PDF | O | 0x0BF9 | PV1 String current 2 | S16 | A | 0.01
3 | string3_current | PDF | O | 0x0BFA | PV1 String current 3 | S16 | A | 0.01
4 | string4_current | PDF | O | 0x0BFB | PV1 String current 4 | S16 | A | 0.01
5 | string5_current | PDF | O | 0x0BFC | PV2 String current 1 | S16 | A | 0.01
6 | string6_current | PDF | O | 0x0BFD | PV2 String current 2 | S16 | A | 0.01
7 | string7_current | PDF | O | 0x0BFE | PV2 String current 3 | S16 | A | 0.01
8 | string8_current | PDF | O | 0x0BFF | PV2 String current 4 | S16 | A | 0.01
9 | string9_current | PDF | O | 0x0C00 | PV3 String current 1 | S16 | A | 0.01
10 | string10_current | PDF | O | 0x0C01 | PV3 String current 2 | S16 | A | 0.01
11 | string11_current | PDF | O | 0x0C02 | PV3 String current 3 | S16 | A | 0.01
12 | string12_current | PDF | O | 0x0C03 | PV3 String current 4 | S16 | A | 0.01
13 | string13_current | PDF | O | 0x0C04 | PV4 String current 1 | S16 | A | 0.01
14 | string14_current | PDF | O | 0x0C05 | PV4 String current 2 | S16 | A | 0.01
15 | string15_current | PDF | O | 0x0C06 | PV4 String current 3 | S16 | A | 0.01
16 | string16_current | PDF | O | 0x0C07 | PV4 String current 4 | S16 | A | 0.01
17 | string17_current | PDF | O | 0x0C08 | PV5 String current 1 | S16 | A | 0.01
18 | string18_current | PDF | O | 0x0C09 | PV5 String current 2 | S16 | A | 0.01
19 | string19_current | PDF | O | 0x0C0A | PV5 String current 3 | S16 | A | 0.01
20 | string20_current | PDF | O | 0x0C0B | PV5 String current 4 | S16 | A | 0.01
21 | string21_current | PDF | O | 0x0C0C | PV6 String current 1 | S16 | A | 0.01
22 | string22_current | PDF | O | 0x0C0D | PV6 String current 2 | S16 | A | 0.01
23 | string23_current | PDF | O | 0x0C0E | PV6 String current 3 | S16 | A | 0.01
24 | string24_current | PDF | O | 0x0C0F | PV6 String current 4 | S16 | A | 0.01
MONITORING 전체 (340개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Fan A Lock | 0x0000 | 04 | U16 | A | RO
2 | Invalid function code | 0x0001 | 04 | U16 |  | RO
3 | Bytecount | 0x0001 |  | U16 |  | RO
4 | Invalid data address | 0x0002 | 04 | U16 |  | RO
5 | PV Parallel Open | 0x0007 | 04 | U16 |  | RO
6 | NULL | 0x0008 | 04 | U16 |  | RO
7 | Hard Inverter Current Over | 0x0009 | 04 | U16 |  | RO
8 | Inverter Current Over | 0x000A | 04 | U16 |  | RO
9 | Inverter Dc Currernt Over | 0x000B | 04 | U16 |  | RO
10 | Ambient Temperature Over | 0x000C | 04 | U16 |  | RO
11 | Sink Temperature Over | 0x000D | 04 | U16 |  | RO
12 | Reserve | 0x000F | 04 | U16 |  | RO
13 | Bit17 | 0x0011 | 04 | U16 |  | RO
14 | Bit18 | 0x0012 | 04 | U16 |  | RO
15 | Bit19 | 0x0013 | 04 | U16 |  | RO
16 | Bit20 | 0x0014 | 04 | U16 |  | RO
17 | Bit21 | 0x0015 | 04 | U16 |  | RO
18 | Bit22 | 0x0016 | 04 | U16 |  | RO
19 | Bit23 | 0x0017 | 04 | U16 |  | RO
20 | Bit24 | 0x0018 | 04 | U16 |  | RO
21 | Bit25 | 0x0019 | 04 | U16 |  | RO
22 | Bit26 | 0x001A | 04 | U16 |  | RO
23 | Bit27 | 0x001B | 04 | U16 |  | RO
24 | Bit28 | 0x001C | 04 | U16 |  | RO
25 | Bit29 | 0x001D | 04 | U16 |  | RO
26 | Bit30 | 0x001E | 04 | U16 |  | RO
27 | Bit31 | 0x001F | 04 | U16 |  | RO
28 | BluE-10KT-M1 | 0x007B | 04 | U16 |  | RO
29 | BluE-12KT-M0 | 0x007C | 04 | U16 |  | RO
30 | BluE-12KT-M1 | 0x007D | 04 | U16 |  | RO
31 | BluE-15KT-M0 | 0x007E | 04 | U16 |  | RO
32 | BluE-15KT-M1 | 0x007F | 04 | U16 |  | RO
33 | BluE-15KT-M2 | 0x0080 | 04 | U16 |  | RO
34 | BluE-15KT-M3 | 0x0081 | 04 | U16 |  | RO
35 | BluE-17KT-M0 | 0x0082 | 04 | U16 |  | RO
36 | BluE-17KT-M1 | 0x0083 | 04 | U16 |  | RO
37 | BluE-20KT-M0 | 0x0084 | 04 | U16 |  | RO
38 | BluE-20KT-M1 | 0x0085 | 04 | U16 |  | RO
39 | BluE-22KT-M0 | 0x0086 | 04 | U16 |  | RO
40 | BluE-22KT-M1 | 0x0087 | 04 | U16 |  | RO
41 | BluE-23KT-M0 | 0x0088 | 04 | U16 |  | RO
42 | BluE-23KT-M1 | 0x0089 | 04 | U16 |  | RO
43 | BluE-25KT-M0 | 0x008A | 04 | U16 |  | RO
44 | BluE-25KT-M1 | 0x008B | 04 | U16 |  | RO
45 | G80KT | 0x00A8 | 04 | U16 |  | RO
46 | G80KT1 | 0x00A9 | 04 | U16 |  | RO
47 | G75KT | 0x00AA | 04 | U16 |  | RO
48 | G75KT1 | 0x00AB | 04 | U16 |  | RO
49 | G70KT | 0x00AC | 04 | U16 |  | RO
50 | G70KT1 | 0x00AD | 04 | U16 |  | RO
51 | G60KT | 0x00AE | 04 | U16 |  | RO
52 | G60KT1 | 0x00AF | 04 | U16 |  | RO
53 | G50KT | 0x00B0 | 04 | U16 |  | RO
54 | G50KT1 | 0x00B1 | 04 | U16 |  | RO
55 | G40KT | 0x00B2 | 04 | U16 |  | RO
56 | G40KT1 | 0x00B3 | 04 | U16 |  | RO
57 | G40KT2 | 0x00B4 | 04 | U16 |  | RO
58 | G40KT3 | 0x00B5 | 04 | U16 |  | RO
59 | BluE-3KT-M2 | 0x00C8 | 04 | U16 |  | RO
60 | BluE-3KT-M3 | 0x00C9 | 04 | U16 |  | RO
61 | BluE-3KT-M4 | 0x00CA | 04 | U16 |  | RO
62 | BluE-3KT-M5 | 0x00CB | 04 | U16 |  | RO
63 | BluE-3.6KT-M2 | 0x00CC | 04 | U16 |  | RO
64 | BluE-3.6KT-M3 | 0x00CD | 04 | U16 |  | RO
65 | BluE-3.6KT-M4 | 0x00CE | 04 | U16 |  | RO
66 | BluE-3.6KT-M5 | 0x00CF | 04 | U16 |  | RO
67 | BluE-4KT-M2 | 0x00D0 | 04 | U16 |  | RO
68 | BluE-4KT-M3 | 0x00D1 | 04 | U16 |  | RO
69 | BluE-4KT-M4 | 0x00D2 | 04 | U16 |  | RO
70 | BluE-4KT-M5 | 0x00D3 | 04 | U16 |  | RO
71 | BluE-5KT-M2 | 0x00D4 | 04 | U16 |  | RO
72 | BluE-5KT-M3 | 0x00D5 | 04 | U16 |  | RO
73 | BluE-5KT-M4 | 0x00D6 | 04 | U16 |  | RO
74 | BluE-5KT-M5 | 0x00D7 | 04 | U16 |  | RO
75 | BluE-6KT-M2 | 0x00D8 | 04 | U16 |  | RO
76 | BluE-6KT-M3 | 0x00D9 | 04 | U16 |  | RO
77 | BluE-6KT-M4 | 0x00DA | 04 | U16 |  | RO
78 | BluE-6KT-M5 | 0x00DB | 04 | U16 |  | RO
79 | BluE-8KT-M2 | 0x00DC | 04 | U16 |  | RO
80 | BluE-8KT-M3 | 0x00DD | 04 | U16 |  | RO
81 | BluE-8KT-M4 | 0x00DE | 04 | U16 |  | RO
82 | BluE-8KT-M5 | 0x00DF | 04 | U16 |  | RO
83 | BluE-10KT-M2 | 0x00E0 | 04 | U16 |  | RO
84 | BluE-10KT-M3 | 0x00E1 | 04 | U16 |  | RO
85 | BluE-10KT-M4 | 0x00E2 | 04 | U16 |  | RO
86 | BluE-10KT-M5 | 0x00E3 | 04 | U16 |  | RO
87 | BluE-12KT-M2 | 0x00E4 | 04 | U16 |  | RO
88 | BluE-12KT-M3 | 0x00E5 | 04 | U16 |  | RO
89 | BluE-12KT-M4 | 0x00E6 | 04 | U16 |  | RO
90 | BluE-12KT-M5 | 0x00E7 | 04 | U16 |  | RO
91 | BluE-15KT-M4 | 0x00E8 | 04 | U16 |  | RO
92 | BluE-15KT-M5 | 0x00E9 | 04 | U16 |  | RO
93 | BluE-17KT-M2 | 0x00EA | 04 | U16 |  | RO
94 | BluE-17KT-M3 | 0x00EB | 04 | U16 |  | RO
95 | BluE-17KT-M4 | 0x00EC | 04 | U16 |  | RO
96 | BluE-17KT-M5 | 0x00ED | 04 | U16 |  | RO
97 | BluE-20KT-M2 | 0x00EE | 04 | U16 |  | RO
98 | BluE-20KT-M3 | 0x00EF | 04 | U16 |  | RO
99 | BluE-20KT-M4 | 0x00F0 | 04 | U16 |  | RO
100 | BluE-20KT-M5 | 0x00F1 | 04 | U16 |  | RO
101 | BluE-22KT-M2 | 0x00F2 | 04 | U16 |  | RO
102 | BluE-22KT-M3 | 0x00F3 | 04 | U16 |  | RO
103 | BluE-22KT-M4 | 0x00F4 | 04 | U16 |  | RO
104 | BluE-22KT-M5 | 0x00F5 | 04 | U16 |  | RO
105 | BluE-23KT-M2 | 0x00F6 | 04 | U16 |  | RO
106 | BluE-23KT-M3 | 0x00F7 | 04 | U16 |  | RO
107 | BluE-23KT-M4 | 0x00F8 | 04 | U16 |  | RO
108 | BluE-23KT-M5 | 0x00F9 | 04 | U16 |  | RO
109 | BluE-25KT-M2 | 0x00FA | 04 | U16 |  | RO
110 | BluE-25KT-M3 | 0x00FB | 04 | U16 |  | RO
111 | BluE-25KT-M4 | 0x00FC | 04 | U16 |  | RO
112 | BluE-25KT-M5 | 0x00FD | 04 | U16 |  | RO
113 | 3329/3130 | 0x02BC | 04 | U16 | % 0.1 | RO
114 | 3326/3127 | 0x0514 | 04 | U16 | % 0.1 | RO
115 | 3309/3060 | 0x05DC | 04 | U16 | V 0.01 | RO
116 | PV12 input voltage | 0x0B94 | 04 | U16 | V 0.1 | RO | mppt12_voltage
117 | PV12 input current | 0x0B95 | 04 | S16 | A 0.01 | RO | mppt12_current
118 | PV12 input power | 0x0B96 | 04 | S32 | W 1 | RO | pv_power
119 | PV11 input voltage | 0x0B98 | 04 | U16 | V 0.1 | RO | mppt11_voltage
120 | PV11 input current | 0x0B99 | 04 | S16 | A 0.01 | RO | mppt11_current
121 | PV11 input power | 0x0B9A | 04 | S32 | W 1 | RO | pv_power
122 | PV10 input voltage | 0x0B9C | 04 | U16 | V 0.1 | RO | mppt10_voltage
123 | PV10 input current | 0x0B9D | 04 | S16 | A 0.01 | RO | mppt10_current
124 | PV10 input power | 0x0B9E | 04 | S32 | W 1 | RO | pv_power
125 | PV9 input voltage | 0x0BA0 | 04 | U16 | V 0.1 | RO | mppt9_voltage
126 | PV9 input current | 0x0BA1 | 04 | S16 | A 0.01 | RO | mppt9_current
127 | PV9 input power | 0x0BA2 | 04 | S32 | W 1 | RO | pv_power
128 | PV8 input voltage | 0x0BA4 | 04 | U16 | V 0.1 | RO | mppt8_voltage
129 | PV8 input current | 0x0BA5 | 04 | S16 | A 0.01 | RO | mppt8_current
130 | PV8 input power | 0x0BA6 | 04 | S32 | W 1 | RO | pv_power
131 | PV7 input voltage | 0x0BA8 | 04 | U16 | V 0.1 | RO | mppt7_voltage
132 | PV7 input current | 0x0BA9 | 04 | S16 | A 0.01 | RO | mppt7_current
133 | PV7 input power | 0x0BAA | 04 | S32 | W 1 | RO | pv_power
134 | PV6 input voltage | 0x0BAC | 04 | U16 | V 0.1 | RO | mppt6_voltage
135 | PV6 input current | 0x0BAD | 04 | S16 | A 0.01 | RO | mppt6_current
136 | PV6 input power | 0x0BAE | 04 | S32 | W 1 | RO | pv_power
137 | PV5 input voltage | 0x0BB0 | 04 | U16 | V 0.1 | RO | mppt5_voltage
138 | PV5 input current | 0x0BB1 | 04 | S16 | A 0.01 | RO | mppt5_current
139 | PV5 input power | 0x0BB2 | 04 | S32 | W 1 | RO | pv_power
140 | PV4 input voltage | 0x0BB4 | 04 | U16 | V 0.1 | RO | mppt4_voltage
141 | PV4 input current | 0x0BB5 | 04 | S16 | A 0.01 | RO | mppt4_current
142 | PV4 input power | 0x0BB6 | 04 | S32 | W 1 | RO | pv_power
143 | PV1 input voltage | 0x0BB8 | 04 | U16 | V 0.1 | RO | mppt1_voltage
144 | PV2 input voltage | 0x0BB9 | 04 | U16 | V 0.1 | RO | mppt2_voltage
145 | PV3 input voltage | 0x0BBA | 04 | U16 | V 0.1 | RO | mppt3_voltage
146 | PV1 input current | 0x0BBB | 04 | U16 | A 0.01 | RO | mppt1_current
147 | PV2 input current | 0x0BBC | 04 | U16 | A 0.01 | RO | mppt2_current
148 | PV3 input current | 0x0BBD | 04 | U16 | A 0.01 | RO | mppt3_current
149 | PV1 input power | 0x0BBE | 04 | S32 | W 1 | RO | pv_power
150 | PV2 input power | 0x0BC0 | 04 | S32 | W 1 | RO | pv_power
151 | PV3 input power | 0x0BC2 | 04 | S32 | W 1 | RO | pv_power
152 | RS-phase grid voltage | 0x0BC6 | 04 | U16 | V 0.1 | RO
153 | ST-phase grid voltage | 0x0BC7 | 04 | U16 | V 0.1 | RO
154 | TR-phase grid voltage | 0x0BC8 | 04 | U16 | V 0.1 | RO
155 | RS-phase grid frequency | 0x0BC9 | 04 | U16 | Hz 0.01 | RO
156 | ST-phase grid frequency | 0x0BCA | 04 | U16 | Hz 0.01 | RO
157 | TR-phase grid frequency | 0x0BCB | 04 | U16 | Hz 0.01 | RO
158 | R-phase grid-tied current | 0x0BCC | 04 | U16 | A 0.01 | RO
159 | S-phase grid-tied current | 0x0BCD | 04 | U16 | A 0.01 | RO
160 | T-phase grid-tied current | 0x0BCE | 04 | U16 | A 0.01 | RO
161 | Grid-tied power | 0x0BCF | 04 | S32 | W 1 | RO
162 | Radiator temperature | 0x0BD1 | 04 | S16 |  | RO
163 | Reserve. | 0x0BDA | 04 | U32 |  | RO
164 | Annual energy yield | 0x0BE0 | 04 | U32 | Kwh | RO | cumulative_energy
165 | Power-on voltage | 0x0BE3 | 04 | U16 | V 0.1 | RO
166 | Power-on delay | 0x0BE4 | 04 | U16 |  | RO
167 | Lower grid voltagethreshold | 0x0BE5 | 04 | U16 | V 0.1 | RO
168 | Upper grid voltagethreshold | 0x0BE6 | 04 | U16 | V 0.1 | RO
169 | Lower grid frequencythreshold | 0x0BE7 | 04 | U16 | Hz 0.01 | RO
170 | Upper grid frequencythreshold | 0x0BE8 | 04 | U16 | Hz 0.01 | RO
171 | Preset power factor | 0x0BE9 | 04 | U16 |  | RO
172 | Preset active power | 0x0BEA | 04 | U16 |  | RO
173 | Preset reactive power | 0x0BEB | 04 | U16 | KVar 1 | RO
174 | Reactive power | 0x0BEE | 04 | S32 |  | RO | reactive_power
175 | Power factor | 0x0BF0 | 04 | U16 |  | RO | power_factor
176 | Overfrequency derating | 0x0BF2 | 04 | U16 |  | RO
177 | Overfrequency deratingthreshold | 0x0BF3 | 04 | U16 |  | RO
178 | Derating rate | 0x0BF4 | 04 | U16 | Hz 0.01 | RO
179 | PV1 String current 1 | 0x0BF8 | 04 | S16 | A 0.01 | RO | string1_current
180 | PV1 String current 2 | 0x0BF9 | 04 | S16 | A 0.01 | RO | string2_current
181 | PV1 String current 3 | 0x0BFA | 04 | S16 | A 0.01 | RO | string3_current
182 | PV1 String current 4 | 0x0BFB | 04 | S16 | A 0.01 | RO | string4_current
183 | PV2 String current 1 | 0x0BFC | 04 | S16 | A 0.01 | RO | string5_current
184 | PV2 String current 2 | 0x0BFD | 04 | S16 | A 0.01 | RO | string6_current
185 | PV2 String current 3 | 0x0BFE | 04 | S16 | A 0.01 | RO | string7_current
186 | PV2 String current 4 | 0x0BFF | 04 | S16 | A 0.01 | RO | string8_current
187 | PV3 String current 1 | 0x0C00 | 04 | S16 | A 0.01 | RO | string9_current
188 | PV3 String current 2 | 0x0C01 | 04 | S16 | A 0.01 | RO | string10_current
189 | PV3 String current 3 | 0x0C02 | 04 | S16 | A 0.01 | RO | string11_current
190 | PV3 String current 4 | 0x0C03 | 04 | S16 | A 0.01 | RO | string12_current
191 | PV4 String current 1 | 0x0C04 | 04 | S16 | A 0.01 | RO | string13_current
192 | PV4 String current 2 | 0x0C05 | 04 | S16 | A 0.01 | RO | string14_current
193 | PV4 String current 3 | 0x0C06 | 04 | S16 | A 0.01 | RO | string15_current
194 | PV4 String current 4 | 0x0C07 | 04 | S16 | A 0.01 | RO | string16_current
195 | PV5 String current 1 | 0x0C08 | 04 | S16 | A 0.01 | RO | string17_current
196 | PV5 String current 2 | 0x0C09 | 04 | S16 | A 0.01 | RO | string18_current
197 | PV5 String current 3 | 0x0C0A | 04 | S16 | A 0.01 | RO | string19_current
198 | PV5 String current 4 | 0x0C0B | 04 | S16 | A 0.01 | RO | string20_current
199 | PV6 String current 1 | 0x0C0C | 04 | S16 | A 0.01 | RO | string21_current
200 | PV6 String current 2 | 0x0C0D | 04 | S16 | A 0.01 | RO | string22_current
201 | PV6 String current 3 | 0x0C0E | 04 | S16 | A 0.01 | RO | string23_current
202 | PV6 String current 4 | 0x0C0F | 04 | S16 | A 0.01 | RO | string24_current
203 | Reserve | 0x0C10 | 04 | U16 |  | RO
204 | Reserve | 0x0C11 | 04 | U16 |  | RO
205 | Generating Time | 0x0C14 | 04 | U32 |  | RO
206 | Power Peak After Starting | 0x0C18 | 04 | U32 | W | RO
207 | Day Generation | 0x0C1A | 04 | U32 | W | RO
208 | Week Generation | 0x0C1C | 04 | U32 | Kwh | RO
209 | Month Generation | 0x0C1E | 04 | U32 | Kwh | RO
210 | Last N days Generation | 0x0C20 | 04 | U32 | Kwh | RO
211 | Value of N | 0x0C22 | 04 | U16 |  | RO
212 | Year | 0x0C23 | 04 | U16 |  | RO
213 | Month | 0x0C24 | 04 | U16 |  | RO
214 | Date | 0x0C25 | 04 | U16 |  | RO
215 | Hour | 0x0C26 | 04 | U16 |  | RO
216 | Minute | 0x0C27 | 04 | U16 |  | RO
217 | Second | 0x0C28 | 04 | U16 |  | RO
218 | Week | 0x0C29 | 04 | U16 |  | RO
219 | Back-current Power LimitSetting | 0x0C2A | 04 | U16 |  | RO
220 | Reserve | 0x0C2C | 04 | U16 |  | RO
221 | 485Address(2) | 0x0C2D | 04 | U16 |  | RO
222 | 485 Agreement | 0x0C2F | 04 | U16 |  | RO
223 | 485 Address(1) | 0x0C30 | 04 | U16 |  | RO
224 | Three-phase System | 0x0C32 | 04 | U16 |  | RO
225 | Remote Control Enable | 0x0C33 | 04 | U16 |  | RO
226 | String Test Threshold | 0x0C34 | 04 | U16 | A | RO
227 | Setting Value ofSelf-check | 0x0C35 | 04 | U16 |  | RO
228 | QV Curve | 0x0C37 | 04 | U16 |  | RO
229 | R-phase VoltageCalibration Factor | 0x0C3D | 04 | U16 |  | RO
230 | S-phase VoltageCalibration Factor | 0x0C3E | 04 | U16 |  | RO
231 | T-phase VoltageCalibration Factor | 0x0C3F | 04 | U16 |  | RO
232 | R-phase CurrentCalibration Factor | 0x0C40 | 04 | U16 |  | RO
233 | S-phase Calibration Factor | 0x0C41 | 04 | U16 |  | RO
234 | T-phase CurrentCalibration Factor | 0x0C42 | 04 | U16 |  | RO
235 | Battery VoltageCalibration Factor | 0x0C43 | 04 | U16 |  | RO
236 | Bluetooth enable | 0x0C44 | 04 | U16 |  | RO
237 | Underfrequencyincrease slope | 0x0C4A | 04 | U16 |  | RO
238 | FrozenUpFreqEnbUnder frequencyincrease | 0x0C4B | 04 | U16 |  | RO
239 | FrozenUpFreqUnderfrequencyincrease threshold | 0x0C4C | 04 | U16 | Hz 0.01 | RO
240 | Slow increase in power | 0x0C4D | 04 | U16 |  | RO
241 | Overfrequency powerreduction percentage | 0x0C4E | 04 | U16 |  | RO
242 | FrozenUpVoltStartStarting value ofovervoltage derating | 0x0C4F | 04 | U16 | V 0.1 | RO
243 | FrozenUpVoltEndEnd value ofovervoltage derating | 0x0C50 | 04 | U16 | V 0.1 | RO
244 | PLC area code | 0x0C7A | 04 | U16 |  | RO
245 | Bluetooth name format | 0x0C7B | 04 | U16 |  | RO
246 | Anti backflow meterconfiguration | 0x0C83 | 04 | U16 |  | RO
247 | Correction value ofanti reverse currentmeter | 0x0C84 | 04 | S16 |  | RO
248 | CT ratio | 0x0C85 | 04 | U16 |  | RO
249 | PV1 currentcalibrationcoefficient | 0x0C8E | 04 | U16 |  | RO
250 | PV2 currentcalibrationcoefficient | 0x0C8F | 04 | U16 |  | RO
251 | PV3~PV12 currentcalibrationcoefficient | 0x0C90 | 04 | U16 |  | RO
252 | PLC MAC Address | 0x0C91 | 04 | U16 |  | RO
253 | Power change rate | 0x0C9A | 04 | U16 |  | RO
254 | Upper limit offrequency responsedead band | 0x0C9F | 04 | U16 | Hz 0.01 | RO
255 | Lower limit offrequency responsedead band | 0x0CA0 | 04 | U16 | Hz 0.01 | RO
256 | Over frequencyderating coefficient | 0x0CA1 | 04 | U16 |  | RO
257 | Underfrequencyamplificationcoefficient | 0x0CA2 | 04 | U16 |  | RO
258 | Maximum Derating | 0x0CA3 | 04 | U16 |  | RO
259 | Maximum increase | 0x0CA4 | 04 | U16 |  | RO
260 | Daily power generation(0.1Kwh) | 0x0CA9 | 04 | U16 | Kwh 0.1 | RO
261 | Accumulated loadelectricityconsumption on the gridside | 0x0CAA | 04 | U32 |  | RO
262 | Active reactive curve | 0x0CAD | 04 | U16 |  | RO
263 | Grid type | 0x0CAF | 04 | U16 |  | RO
264 | Night SVG function | 0x0CB1 | 04 | U16 |  | RO
265 | R-phase voltagecalibrationcoefficient 2 | 0x0CB3 | 04 | U16 |  | RO
266 | Reserve (860 Register) | 0x0CB4 | 04 | U16 |  | RO
267 | Clock information | 0x0CE4 | 04 | U16 |  | RO
268 | Week | 0x0CEA | 04 | ASCII |  | RO
269 | QV Active Factor | 0x0CEB | 04 | U16 |  | RO
270 | Setting PLC MAC | 0x0CFB | 04 | U16 |  | RO
271 | QV Curve (2) | 0x0CFE | 04 | U16 |  | RO
272 | Remotepower-off | 0x0FA1 | 04 | U16 |  | RO
273 | Revoke remotepower-off | 0x0FA2 | 04 | U16 |  | RO
274 | Set the powerfactor | 0x0FA3 | 04 | U16 |  | RO
275 | Set the activepower | 0x0FA4 | 04 | U16 |  | RO
276 | Set the reactivepower | 0x0FA5 | 04 | S16 | KVar 1 | RO
277 | Overfrequencyderating | 0x0FA7 | 04 | U16 |  | RO
278 | Overfrequency | 0x0FA8 | 04 | U16 | Hz 0.01 | RO
279 | Set the deratingrate | 0x0FA9 | 04 | U16 |  | RO
280 | Set the activepower | 0x0FAA | 04 | U16 |  | RO
281 | LOGO Settings | 0x0FAB | 04 | U16 |  | RO
282 | GridConnectionStandardSettings | 0x0FAD | 04 | U16 |  | RO
283 | StartVoltageSettings | 0x0FAE | 04 | U16 |  | RO
284 | Start DelaySettings | 0x0FAF | 04 | U16 |  | RO
285 | Grid VoltageLower LimitSettings | 0x0FB0 | 04 | U16 |  | RO
286 | Grid VoltageUpper LimitSettings | 0x0FB1 | 04 | U16 |  | RO
287 | Grid FrequencyLower LimitSettings | 0x0FB2 | 04 | U16 |  | RO
288 | GridFrequencyUpper LimitSettings | 0x0FB3 | 04 | U16 |  | RO
289 | Back CurrentPower LimitSettings | 0x0FB4 | 04 | U16 |  | RO
290 | OvervoltageDeratingThresholdValue | 0x0FB5 | 04 | U16 | % 0.1 | RO
291 | Reserve | 0x0FB6 | 04 | U16 |  | RO
292 | 485 AddressSettings(U2) | 0x0FB7 | 04 | U16 |  | RO
293 | 485 ProtocolSettings | 0x0FB9 | 04 | U16 |  | RO
294 | 485 AddressSettings(U4) | 0x0FBA | 04 | U16 |  | RO
295 | Three-phaseSettings | 0x0FBC | 04 | U16 |  | RO
296 | RemoteControlSettings | 0x0FBD | 04 | U16 |  | RO
297 | String TestThresholdValue Settings | 0x0FBE | 04 | STRINGING |  | RO
298 | Self-check(Enable) | 0x0FBF | 04 | U16 |  | RO
299 | Self-check(Disable) | 0x0FC0 | 04 | U16 |  | RO
300 | Factory DataReset | 0x0FC2 | 04 | U16 |  | RO
301 | Start I/V Scan | 0x0FC3 | 04 | U16 | V | RO
302 | Active PowerIncrement(KW) | 0x0FC4 | 04 | S16 | KW | RO
303 | GRID_TOTAL_ACTIVE_POWER | 0x0FC5 | 04 | S16 |  | RO | ac_power
304 | Active PowerSettings(Decimals) | 0x0FC7 | 04 | U16 | % 0.1 | RO
305 | R-phaseVoltageCalibrationFactor | 0x0FC8 | 04 | U16 |  | RO
306 | S-phaseVoltageCalibrationFactor | 0x0FC9 | 04 | U16 |  | RO
307 | T-phaseVoltageCalibrationFactor | 0x0FCA | 04 | U16 |  | RO
308 | R-phaseCurrentCalibrationFactor | 0x0FCB | 04 | U16 |  | RO
309 | S-phaseCalibrationFactor | 0x0FCC | 04 | U16 |  | RO
310 | T-phaseCurrentCalibrationFactor | 0x0FCD | 04 | U16 |  | RO
311 | Battery VoltageCalibrationFactor | 0x0FCE | 04 | U16 |  | RO
312 | Reserve(358registers) | 0x0FCF | 04 | U16 |  | RO
313 | Record | 0x112F | 04 | U16 |  | RO
314 | PV1 Voltage Point 1 | 0x1388 | 04 | U16 | V 0.1 | RO
315 | PV1 Current Point 1 | 0x1389 | 04 | S16 | A 0.01 | RO
316 | PV1 Voltage Point 2 | 0x138A | 04 | U16 | V 0.1 | RO
317 | PV1 Current Point 2 | 0x138B | 04 | S16 | A 0.01 | RO
318 | PV1 Voltage Point 99 | 0x144C | 04 | U16 | V 0.1 | RO
319 | PV1 Current Point 99 | 0x144D | 04 | S16 | A 0.01 | RO
320 | PV1 Voltage Point 100 | 0x144E | 04 | U16 | V 0.1 | RO
321 | PV1 Current Point 100 | 0x144F | 04 | S16 | A 0.01 | RO
322 | PV2 Voltage Point 1 | 0x1450 | 04 | U16 | V 0.1 | RO
323 | PV2 Current Point 1 | 0x1451 | 04 | S16 | A 0.01 | RO
324 | PV2 Voltage Point 2 | 0x1452 | 04 | U16 | V 0.1 | RO
325 | PV2 Current Point 2 | 0x1453 | 04 | S16 | A 0.01 | RO
326 | PV2 Voltage Point 99 | 0x1514 | 04 | U16 | V 0.1 | RO
327 | PV2 Current Point 99 | 0x1515 | 04 | S16 | A 0.01 | RO
328 | PV2 Voltage Point 100 | 0x1516 | 04 | U16 | V 0.1 | RO
329 | PV2 Current Point 100 | 0x1517 | 04 | S16 | A 0.01 | RO
330 | PV3 Voltage and CurrentPoint | 0x1518 | 04 | U16 |  | RO
331 | PV4 Voltage and CurrentPoint | 0x15E0 | 04 | U16 |  | RO
332 | PV5 Voltage and CurrentPoint | 0x16A8 | 04 | U16 |  | RO
333 | PV6 Voltage and CurrentPoint | 0x1770 | 04 | U16 |  | RO
334 | PV7 Voltage and CurrentPoint | 0x1838 | 04 | U16 |  | RO
335 | PV8 Voltage and CurrentPoint | 0x1900 | 04 | U16 |  | RO
336 | PV9 Voltage and CurrentPoint | 0x19C8 | 04 | U16 |  | RO
337 | PV10 Voltage and CurrentPoint | 0x1A90 | 04 | U16 |  | RO
338 | PV11 Voltage and CurrentPoint | 0x1B58 | 04 | U16 |  | RO
339 | PV12 Voltage and CurrentPoint | 0x1C20 | 04 | U16 |  | RO
340 | Aging Enable | 0x2328 | 04 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## 5_IV
IV Scan 매핑 — data_points=100
IV Scan Command | 0x0CB2
Data Points | 100
Trackers | 2
Strings/Tracker | 0
IV Scan Command
Name | Address | Type | R/W | Description
IV_CURVE_SCAN | 0x0CB2 | U16 | RW | W: 0=Stop, 1=Start / R: 0=Idle, 1=Running, 2=Finished
IV Data 레지스터 매핑
No | Type | Name | Address | Regs | Data Type | Scale
1 | Tracker Voltage | Tracker 1 voltage | 0x1388 | 100 | U16 | 0.1V
2 | Tracker Voltage | Tracker 2 voltage | 0x1450 | 100 | U16 | 0.1V