## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=12, STR=24)
제조사 | 1
용량 | -
MPPT | 12
String/MPPT | 2
Total Strings | 24
H01 매칭 | 65/66
DER 매칭 | 33/33
총 레지스터 | 372
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | PBUS voltage | 0x0BC4 | U16 | V 0.1 | RO
2 | NBUS voltage | 0x0BC5 | U16 | V 0.1 | RO |  | 1-5K not have.
3 | INNER_TEMP | 0x0BD2 | S16 |  | RO | temperature | Module temperature ¦ 1-5K not have.
4 | Total energy yield | 0x0BDE | U32 | Kwh 0.1 | RO | cumulative_energy
5 | Daily energy yield | 0x0BE2 | U16 | Kwh | RO | cumulative_energy
6 | Apparent power | 0x0BEC | S32 | VA 1 | RO
7 | DC insulation resistance | 0x0BF1 | U16 |  | RO |  | 1-5K not have.
8 | Running Time | 0x0C12 | U32 |  | RO
9 | Number of gridconnection | 0x0C16 | U32 |  | RO
10 | Setting value of ratedpower for anti backflow | 0x0C7C | U16 |  | RO
11 | Machine model | 0x0C80 | ASCII |  | RO |  | ASCII code
12 | Inverter SN | 0x0C86 | ASCII |  | RO |  | ASCII character
13 | LCD Model Setting | 0x0C94 | U16 |  | RO |  | Table 3.3.5
14 | Inverter Model（New） | 0x0C95 | ASCII |  | RO |  | ASCII character
15 | Setting Inverter SN | 0x0CEF | ASCII |  | RO
16 | LCD Model Setting | 0x0D04 | U16 |  | RO
17 | DEVICE_MODEL | 0x0D05 | U16 |  | RO |  | Inverter Model
H01 MONITORING (340개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Fan A Lock | 0x0000 | U16 | A | RO
2 | Invalid function code | 0x0001 | U16 |  | RO
3 | Bytecount | 0x0001 | U16 |  | RO
4 | Invalid data address | 0x0002 | U16 |  | RO
5 | PV Parallel Open | 0x0007 | U16 |  | RO
6 | NULL | 0x0008 | U16 |  | RO
7 | Hard Inverter Current Over | 0x0009 | U16 |  | RO
8 | Inverter Current Over | 0x000A | U16 |  | RO
9 | Inverter Dc Currernt Over | 0x000B | U16 |  | RO
10 | Ambient Temperature Over | 0x000C | U16 |  | RO
11 | Sink Temperature Over | 0x000D | U16 |  | RO
12 | Reserve | 0x000F | U16 |  | RO
13 | Bit17 | 0x0011 | U16 |  | RO
14 | Bit18 | 0x0012 | U16 |  | RO
15 | Bit19 | 0x0013 | U16 |  | RO
16 | Bit20 | 0x0014 | U16 |  | RO
17 | Bit21 | 0x0015 | U16 |  | RO
18 | Bit22 | 0x0016 | U16 |  | RO
19 | Bit23 | 0x0017 | U16 |  | RO
20 | Bit24 | 0x0018 | U16 |  | RO
21 | Bit25 | 0x0019 | U16 |  | RO
22 | Bit26 | 0x001A | U16 |  | RO
23 | Bit27 | 0x001B | U16 |  | RO
24 | Bit28 | 0x001C | U16 |  | RO
25 | Bit29 | 0x001D | U16 |  | RO
26 | Bit30 | 0x001E | U16 |  | RO
27 | Bit31 | 0x001F | U16 |  | RO
28 | BluE-10KT-M1 | 0x007B | U16 |  | RO
29 | BluE-12KT-M0 | 0x007C | U16 |  | RO
30 | BluE-12KT-M1 | 0x007D | U16 |  | RO
31 | BluE-15KT-M0 | 0x007E | U16 |  | RO
32 | BluE-15KT-M1 | 0x007F | U16 |  | RO
33 | BluE-15KT-M2 | 0x0080 | U16 |  | RO
34 | BluE-15KT-M3 | 0x0081 | U16 |  | RO
35 | BluE-17KT-M0 | 0x0082 | U16 |  | RO
36 | BluE-17KT-M1 | 0x0083 | U16 |  | RO
37 | BluE-20KT-M0 | 0x0084 | U16 |  | RO
38 | BluE-20KT-M1 | 0x0085 | U16 |  | RO
39 | BluE-22KT-M0 | 0x0086 | U16 |  | RO
40 | BluE-22KT-M1 | 0x0087 | U16 |  | RO
41 | BluE-23KT-M0 | 0x0088 | U16 |  | RO
42 | BluE-23KT-M1 | 0x0089 | U16 |  | RO
43 | BluE-25KT-M0 | 0x008A | U16 |  | RO
44 | BluE-25KT-M1 | 0x008B | U16 |  | RO
45 | G80KT | 0x00A8 | U16 |  | RO
46 | G80KT1 | 0x00A9 | U16 |  | RO
47 | G75KT | 0x00AA | U16 |  | RO
48 | G75KT1 | 0x00AB | U16 |  | RO
49 | G70KT | 0x00AC | U16 |  | RO
50 | G70KT1 | 0x00AD | U16 |  | RO
51 | G60KT | 0x00AE | U16 |  | RO
52 | G60KT1 | 0x00AF | U16 |  | RO
53 | G50KT | 0x00B0 | U16 |  | RO
54 | G50KT1 | 0x00B1 | U16 |  | RO
55 | G40KT | 0x00B2 | U16 |  | RO
56 | G40KT1 | 0x00B3 | U16 |  | RO
57 | G40KT2 | 0x00B4 | U16 |  | RO
58 | G40KT3 | 0x00B5 | U16 |  | RO
59 | BluE-3KT-M2 | 0x00C8 | U16 |  | RO
60 | BluE-3KT-M3 | 0x00C9 | U16 |  | RO
61 | BluE-3KT-M4 | 0x00CA | U16 |  | RO
62 | BluE-3KT-M5 | 0x00CB | U16 |  | RO
63 | BluE-3.6KT-M2 | 0x00CC | U16 |  | RO
64 | BluE-3.6KT-M3 | 0x00CD | U16 |  | RO
65 | BluE-3.6KT-M4 | 0x00CE | U16 |  | RO
66 | BluE-3.6KT-M5 | 0x00CF | U16 |  | RO
67 | BluE-4KT-M2 | 0x00D0 | U16 |  | RO
68 | BluE-4KT-M3 | 0x00D1 | U16 |  | RO
69 | BluE-4KT-M4 | 0x00D2 | U16 |  | RO
70 | BluE-4KT-M5 | 0x00D3 | U16 |  | RO
71 | BluE-5KT-M2 | 0x00D4 | U16 |  | RO
72 | BluE-5KT-M3 | 0x00D5 | U16 |  | RO
73 | BluE-5KT-M4 | 0x00D6 | U16 |  | RO
74 | BluE-5KT-M5 | 0x00D7 | U16 |  | RO
75 | BluE-6KT-M2 | 0x00D8 | U16 |  | RO
76 | BluE-6KT-M3 | 0x00D9 | U16 |  | RO
77 | BluE-6KT-M4 | 0x00DA | U16 |  | RO
78 | BluE-6KT-M5 | 0x00DB | U16 |  | RO
79 | BluE-8KT-M2 | 0x00DC | U16 |  | RO
80 | BluE-8KT-M3 | 0x00DD | U16 |  | RO
81 | BluE-8KT-M4 | 0x00DE | U16 |  | RO
82 | BluE-8KT-M5 | 0x00DF | U16 |  | RO
83 | BluE-10KT-M2 | 0x00E0 | U16 |  | RO
84 | BluE-10KT-M3 | 0x00E1 | U16 |  | RO
85 | BluE-10KT-M4 | 0x00E2 | U16 |  | RO
86 | BluE-10KT-M5 | 0x00E3 | U16 |  | RO
87 | BluE-12KT-M2 | 0x00E4 | U16 |  | RO
88 | BluE-12KT-M3 | 0x00E5 | U16 |  | RO
89 | BluE-12KT-M4 | 0x00E6 | U16 |  | RO
90 | BluE-12KT-M5 | 0x00E7 | U16 |  | RO
91 | BluE-15KT-M4 | 0x00E8 | U16 |  | RO
92 | BluE-15KT-M5 | 0x00E9 | U16 |  | RO
93 | BluE-17KT-M2 | 0x00EA | U16 |  | RO
94 | BluE-17KT-M3 | 0x00EB | U16 |  | RO
95 | BluE-17KT-M4 | 0x00EC | U16 |  | RO
96 | BluE-17KT-M5 | 0x00ED | U16 |  | RO
97 | BluE-20KT-M2 | 0x00EE | U16 |  | RO
98 | BluE-20KT-M3 | 0x00EF | U16 |  | RO
99 | BluE-20KT-M4 | 0x00F0 | U16 |  | RO
100 | BluE-20KT-M5 | 0x00F1 | U16 |  | RO
101 | BluE-22KT-M2 | 0x00F2 | U16 |  | RO
102 | BluE-22KT-M3 | 0x00F3 | U16 |  | RO
103 | BluE-22KT-M4 | 0x00F4 | U16 |  | RO
104 | BluE-22KT-M5 | 0x00F5 | U16 |  | RO
105 | BluE-23KT-M2 | 0x00F6 | U16 |  | RO
106 | BluE-23KT-M3 | 0x00F7 | U16 |  | RO
107 | BluE-23KT-M4 | 0x00F8 | U16 |  | RO
108 | BluE-23KT-M5 | 0x00F9 | U16 |  | RO
109 | BluE-25KT-M2 | 0x00FA | U16 |  | RO
110 | BluE-25KT-M3 | 0x00FB | U16 |  | RO
111 | BluE-25KT-M4 | 0x00FC | U16 |  | RO
112 | BluE-25KT-M5 | 0x00FD | U16 |  | RO
113 | 3329/3130 | 0x02BC | U16 | % 0.1 | RO
114 | 3326/3127 | 0x0514 | U16 | % 0.1 | RO
115 | 3309/3060 | 0x05DC | U16 | V 0.01 | RO
116 | PV12 input voltage | 0x0B94 | U16 | V 0.1 | RO | mppt12_voltage
117 | PV12 input current | 0x0B95 | S16 | A 0.01 | RO | mppt12_current
118 | PV12 input power | 0x0B96 | S32 | W 1 | RO | pv_power
119 | PV11 input voltage | 0x0B98 | U16 | V 0.1 | RO | mppt11_voltage
120 | PV11 input current | 0x0B99 | S16 | A 0.01 | RO | mppt11_current
121 | PV11 input power | 0x0B9A | S32 | W 1 | RO | pv_power
122 | PV10 input voltage | 0x0B9C | U16 | V 0.1 | RO | mppt10_voltage
123 | PV10 input current | 0x0B9D | S16 | A 0.01 | RO | mppt10_current
124 | PV10 input power | 0x0B9E | S32 | W 1 | RO | pv_power
125 | PV9 input voltage | 0x0BA0 | U16 | V 0.1 | RO | mppt9_voltage
126 | PV9 input current | 0x0BA1 | S16 | A 0.01 | RO | mppt9_current
127 | PV9 input power | 0x0BA2 | S32 | W 1 | RO | pv_power
128 | PV8 input voltage | 0x0BA4 | U16 | V 0.1 | RO | mppt8_voltage
129 | PV8 input current | 0x0BA5 | S16 | A 0.01 | RO | mppt8_current
130 | PV8 input power | 0x0BA6 | S32 | W 1 | RO | pv_power
131 | PV7 input voltage | 0x0BA8 | U16 | V 0.1 | RO | mppt7_voltage
132 | PV7 input current | 0x0BA9 | S16 | A 0.01 | RO | mppt7_current
133 | PV7 input power | 0x0BAA | S32 | W 1 | RO | pv_power
134 | PV6 input voltage | 0x0BAC | U16 | V 0.1 | RO | mppt6_voltage
135 | PV6 input current | 0x0BAD | S16 | A 0.01 | RO | mppt6_current
136 | PV6 input power | 0x0BAE | S32 | W 1 | RO | pv_power
137 | PV5 input voltage | 0x0BB0 | U16 | V 0.1 | RO | mppt5_voltage
138 | PV5 input current | 0x0BB1 | S16 | A 0.01 | RO | mppt5_current
139 | PV5 input power | 0x0BB2 | S32 | W 1 | RO | pv_power
140 | PV4 input voltage | 0x0BB4 | U16 | V 0.1 | RO | mppt4_voltage
141 | PV4 input current | 0x0BB5 | S16 | A 0.01 | RO | mppt4_current
142 | PV4 input power | 0x0BB6 | S32 | W 1 | RO | pv_power
143 | PV1 input voltage | 0x0BB8 | U16 | V 0.1 | RO | mppt1_voltage
144 | PV2 input voltage | 0x0BB9 | U16 | V 0.1 | RO | mppt2_voltage
145 | PV3 input voltage | 0x0BBA | U16 | V 0.1 | RO | mppt3_voltage
146 | PV1 input current | 0x0BBB | U16 | A 0.01 | RO | mppt1_current
147 | PV2 input current | 0x0BBC | U16 | A 0.01 | RO | mppt2_current
148 | PV3 input current | 0x0BBD | U16 | A 0.01 | RO | mppt3_current
149 | PV1 input power | 0x0BBE | S32 | W 1 | RO | pv_power
150 | PV2 input power | 0x0BC0 | S32 | W 1 | RO | pv_power
151 | PV3 input power | 0x0BC2 | S32 | W 1 | RO | pv_power
152 | RS-phase grid voltage | 0x0BC6 | U16 | V 0.1 | RO
153 | ST-phase grid voltage | 0x0BC7 | U16 | V 0.1 | RO
154 | TR-phase grid voltage | 0x0BC8 | U16 | V 0.1 | RO
155 | RS-phase grid frequency | 0x0BC9 | U16 | Hz 0.01 | RO
156 | ST-phase grid frequency | 0x0BCA | U16 | Hz 0.01 | RO
157 | TR-phase grid frequency | 0x0BCB | U16 | Hz 0.01 | RO
158 | R-phase grid-tied current | 0x0BCC | U16 | A 0.01 | RO
159 | S-phase grid-tied current | 0x0BCD | U16 | A 0.01 | RO
160 | T-phase grid-tied current | 0x0BCE | U16 | A 0.01 | RO
161 | Grid-tied power | 0x0BCF | S32 | W 1 | RO
162 | Radiator temperature | 0x0BD1 | S16 |  | RO
163 | Reserve. | 0x0BDA | U32 |  | RO
164 | Annual energy yield | 0x0BE0 | U32 | Kwh | RO | cumulative_energy
165 | Power-on voltage | 0x0BE3 | U16 | V 0.1 | RO
166 | Power-on delay | 0x0BE4 | U16 |  | RO
167 | Lower grid voltagethreshold | 0x0BE5 | U16 | V 0.1 | RO
168 | Upper grid voltagethreshold | 0x0BE6 | U16 | V 0.1 | RO
169 | Lower grid frequencythreshold | 0x0BE7 | U16 | Hz 0.01 | RO
170 | Upper grid frequencythreshold | 0x0BE8 | U16 | Hz 0.01 | RO
171 | Preset power factor | 0x0BE9 | U16 |  | RO
172 | Preset active power | 0x0BEA | U16 |  | RO
173 | Preset reactive power | 0x0BEB | U16 | KVar 1 | RO
174 | Reactive power | 0x0BEE | S32 |  | RO | reactive_power
175 | Power factor | 0x0BF0 | U16 |  | RO | power_factor
176 | Overfrequency derating | 0x0BF2 | U16 |  | RO
177 | Overfrequency deratingthreshold | 0x0BF3 | U16 |  | RO
178 | Derating rate | 0x0BF4 | U16 | Hz 0.01 | RO
179 | PV1 String current 1 | 0x0BF8 | S16 | A 0.01 | RO | string1_current
180 | PV1 String current 2 | 0x0BF9 | S16 | A 0.01 | RO | string2_current
181 | PV1 String current 3 | 0x0BFA | S16 | A 0.01 | RO | string3_current
182 | PV1 String current 4 | 0x0BFB | S16 | A 0.01 | RO | string4_current
183 | PV2 String current 1 | 0x0BFC | S16 | A 0.01 | RO | string5_current
184 | PV2 String current 2 | 0x0BFD | S16 | A 0.01 | RO | string6_current
185 | PV2 String current 3 | 0x0BFE | S16 | A 0.01 | RO | string7_current
186 | PV2 String current 4 | 0x0BFF | S16 | A 0.01 | RO | string8_current
187 | PV3 String current 1 | 0x0C00 | S16 | A 0.01 | RO | string9_current
188 | PV3 String current 2 | 0x0C01 | S16 | A 0.01 | RO | string10_current
189 | PV3 String current 3 | 0x0C02 | S16 | A 0.01 | RO | string11_current
190 | PV3 String current 4 | 0x0C03 | S16 | A 0.01 | RO | string12_current
191 | PV4 String current 1 | 0x0C04 | S16 | A 0.01 | RO | string13_current
192 | PV4 String current 2 | 0x0C05 | S16 | A 0.01 | RO | string14_current
193 | PV4 String current 3 | 0x0C06 | S16 | A 0.01 | RO | string15_current
194 | PV4 String current 4 | 0x0C07 | S16 | A 0.01 | RO | string16_current
195 | PV5 String current 1 | 0x0C08 | S16 | A 0.01 | RO | string17_current
196 | PV5 String current 2 | 0x0C09 | S16 | A 0.01 | RO | string18_current
197 | PV5 String current 3 | 0x0C0A | S16 | A 0.01 | RO | string19_current
198 | PV5 String current 4 | 0x0C0B | S16 | A 0.01 | RO | string20_current
199 | PV6 String current 1 | 0x0C0C | S16 | A 0.01 | RO | string21_current
200 | PV6 String current 2 | 0x0C0D | S16 | A 0.01 | RO | string22_current
201 | PV6 String current 3 | 0x0C0E | S16 | A 0.01 | RO | string23_current
202 | PV6 String current 4 | 0x0C0F | S16 | A 0.01 | RO | string24_current
203 | Reserve | 0x0C10 | U16 |  | RO
204 | Reserve | 0x0C11 | U16 |  | RO
205 | Generating Time | 0x0C14 | U32 |  | RO
206 | Power Peak After Starting | 0x0C18 | U32 | W | RO
207 | Day Generation | 0x0C1A | U32 | W | RO
208 | Week Generation | 0x0C1C | U32 | Kwh | RO
209 | Month Generation | 0x0C1E | U32 | Kwh | RO
210 | Last N days Generation | 0x0C20 | U32 | Kwh | RO
211 | Value of N | 0x0C22 | U16 |  | RO
212 | Year | 0x0C23 | U16 |  | RO
213 | Month | 0x0C24 | U16 |  | RO
214 | Date | 0x0C25 | U16 |  | RO
215 | Hour | 0x0C26 | U16 |  | RO
216 | Minute | 0x0C27 | U16 |  | RO
217 | Second | 0x0C28 | U16 |  | RO
218 | Week | 0x0C29 | U16 |  | RO
219 | Back-current Power LimitSetting | 0x0C2A | U16 |  | RO
220 | Reserve | 0x0C2C | U16 |  | RO
221 | 485Address(2) | 0x0C2D | U16 |  | RO
222 | 485 Agreement | 0x0C2F | U16 |  | RO
223 | 485 Address(1) | 0x0C30 | U16 |  | RO
224 | Three-phase System | 0x0C32 | U16 |  | RO
225 | Remote Control Enable | 0x0C33 | U16 |  | RO
226 | String Test Threshold | 0x0C34 | U16 | A | RO
227 | Setting Value ofSelf-check | 0x0C35 | U16 |  | RO
228 | QV Curve | 0x0C37 | U16 |  | RO
229 | R-phase VoltageCalibration Factor | 0x0C3D | U16 |  | RO
230 | S-phase VoltageCalibration Factor | 0x0C3E | U16 |  | RO
231 | T-phase VoltageCalibration Factor | 0x0C3F | U16 |  | RO
232 | R-phase CurrentCalibration Factor | 0x0C40 | U16 |  | RO
233 | S-phase Calibration Factor | 0x0C41 | U16 |  | RO
234 | T-phase CurrentCalibration Factor | 0x0C42 | U16 |  | RO
235 | Battery VoltageCalibration Factor | 0x0C43 | U16 |  | RO
236 | Bluetooth enable | 0x0C44 | U16 |  | RO
237 | Underfrequencyincrease slope | 0x0C4A | U16 |  | RO
238 | FrozenUpFreqEnbUnder frequencyincrease | 0x0C4B | U16 |  | RO
239 | FrozenUpFreqUnderfrequencyincrease threshold | 0x0C4C | U16 | Hz 0.01 | RO
240 | Slow increase in power | 0x0C4D | U16 |  | RO
241 | Overfrequency powerreduction percentage | 0x0C4E | U16 |  | RO
242 | FrozenUpVoltStartStarting value ofovervoltage derating | 0x0C4F | U16 | V 0.1 | RO
243 | FrozenUpVoltEndEnd value ofovervoltage derating | 0x0C50 | U16 | V 0.1 | RO
244 | PLC area code | 0x0C7A | U16 |  | RO
245 | Bluetooth name format | 0x0C7B | U16 |  | RO
246 | Anti backflow meterconfiguration | 0x0C83 | U16 |  | RO
247 | Correction value ofanti reverse currentmeter | 0x0C84 | S16 |  | RO
248 | CT ratio | 0x0C85 | U16 |  | RO
249 | PV1 currentcalibrationcoefficient | 0x0C8E | U16 |  | RO
250 | PV2 currentcalibrationcoefficient | 0x0C8F | U16 |  | RO
251 | PV3~PV12 currentcalibrationcoefficient | 0x0C90 | U16 |  | RO
252 | PLC MAC Address | 0x0C91 | U16 |  | RO
253 | Power change rate | 0x0C9A | U16 |  | RO
254 | Upper limit offrequency responsedead band | 0x0C9F | U16 | Hz 0.01 | RO
255 | Lower limit offrequency responsedead band | 0x0CA0 | U16 | Hz 0.01 | RO
256 | Over frequencyderating coefficient | 0x0CA1 | U16 |  | RO
257 | Underfrequencyamplificationcoefficient | 0x0CA2 | U16 |  | RO
258 | Maximum Derating | 0x0CA3 | U16 |  | RO
259 | Maximum increase | 0x0CA4 | U16 |  | RO
260 | Daily power generation(0.1Kwh) | 0x0CA9 | U16 | Kwh 0.1 | RO
261 | Accumulated loadelectricityconsumption on the gridside | 0x0CAA | U32 |  | RO
262 | Active reactive curve | 0x0CAD | U16 |  | RO
263 | Grid type | 0x0CAF | U16 |  | RO
264 | Night SVG function | 0x0CB1 | U16 |  | RO
265 | R-phase voltagecalibrationcoefficient 2 | 0x0CB3 | U16 |  | RO
266 | Reserve (860 Register) | 0x0CB4 | U16 |  | RO
267 | Clock information | 0x0CE4 | U16 |  | RO
268 | Week | 0x0CEA | ASCII |  | RO
269 | QV Active Factor | 0x0CEB | U16 |  | RO
270 | Setting PLC MAC | 0x0CFB | U16 |  | RO
271 | QV Curve (2) | 0x0CFE | U16 |  | RO
272 | Remotepower-off | 0x0FA1 | U16 |  | RO
273 | Revoke remotepower-off | 0x0FA2 | U16 |  | RO
274 | Set the powerfactor | 0x0FA3 | U16 |  | RO
275 | Set the activepower | 0x0FA4 | U16 |  | RO
276 | Set the reactivepower | 0x0FA5 | S16 | KVar 1 | RO
277 | Overfrequencyderating | 0x0FA7 | U16 |  | RO
278 | Overfrequency | 0x0FA8 | U16 | Hz 0.01 | RO
279 | Set the deratingrate | 0x0FA9 | U16 |  | RO
280 | Set the activepower | 0x0FAA | U16 |  | RO
281 | LOGO Settings | 0x0FAB | U16 |  | RO
282 | GridConnectionStandardSettings | 0x0FAD | U16 |  | RO
283 | StartVoltageSettings | 0x0FAE | U16 |  | RO
284 | Start DelaySettings | 0x0FAF | U16 |  | RO
285 | Grid VoltageLower LimitSettings | 0x0FB0 | U16 |  | RO
286 | Grid VoltageUpper LimitSettings | 0x0FB1 | U16 |  | RO
287 | Grid FrequencyLower LimitSettings | 0x0FB2 | U16 |  | RO
288 | GridFrequencyUpper LimitSettings | 0x0FB3 | U16 |  | RO
289 | Back CurrentPower LimitSettings | 0x0FB4 | U16 |  | RO
290 | OvervoltageDeratingThresholdValue | 0x0FB5 | U16 | % 0.1 | RO
291 | Reserve | 0x0FB6 | U16 |  | RO
292 | 485 AddressSettings(U2) | 0x0FB7 | U16 |  | RO
293 | 485 ProtocolSettings | 0x0FB9 | U16 |  | RO
294 | 485 AddressSettings(U4) | 0x0FBA | U16 |  | RO
295 | Three-phaseSettings | 0x0FBC | U16 |  | RO
296 | RemoteControlSettings | 0x0FBD | U16 |  | RO
297 | String TestThresholdValue Settings | 0x0FBE | STRINGING |  | RO
298 | Self-check(Enable) | 0x0FBF | U16 |  | RO
299 | Self-check(Disable) | 0x0FC0 | U16 |  | RO
300 | Factory DataReset | 0x0FC2 | U16 |  | RO
301 | Start I/V Scan | 0x0FC3 | U16 | V | RO
302 | Active PowerIncrement(KW) | 0x0FC4 | S16 | KW | RO
303 | GRID_TOTAL_ACTIVE_POWER | 0x0FC5 | S16 |  | RO | ac_power
304 | Active PowerSettings(Decimals) | 0x0FC7 | U16 | % 0.1 | RO
305 | R-phaseVoltageCalibrationFactor | 0x0FC8 | U16 |  | RO
306 | S-phaseVoltageCalibrationFactor | 0x0FC9 | U16 |  | RO
307 | T-phaseVoltageCalibrationFactor | 0x0FCA | U16 |  | RO
308 | R-phaseCurrentCalibrationFactor | 0x0FCB | U16 |  | RO
309 | S-phaseCalibrationFactor | 0x0FCC | U16 |  | RO
310 | T-phaseCurrentCalibrationFactor | 0x0FCD | U16 |  | RO
311 | Battery VoltageCalibrationFactor | 0x0FCE | U16 |  | RO
312 | Reserve(358registers) | 0x0FCF | U16 |  | RO
313 | Record | 0x112F | U16 |  | RO
314 | PV1 Voltage Point 1 | 0x1388 | U16 | V 0.1 | RO
315 | PV1 Current Point 1 | 0x1389 | S16 | A 0.01 | RO
316 | PV1 Voltage Point 2 | 0x138A | U16 | V 0.1 | RO
317 | PV1 Current Point 2 | 0x138B | S16 | A 0.01 | RO
318 | PV1 Voltage Point 99 | 0x144C | U16 | V 0.1 | RO
319 | PV1 Current Point 99 | 0x144D | S16 | A 0.01 | RO
320 | PV1 Voltage Point 100 | 0x144E | U16 | V 0.1 | RO
321 | PV1 Current Point 100 | 0x144F | S16 | A 0.01 | RO
322 | PV2 Voltage Point 1 | 0x1450 | U16 | V 0.1 | RO
323 | PV2 Current Point 1 | 0x1451 | S16 | A 0.01 | RO
324 | PV2 Voltage Point 2 | 0x1452 | U16 | V 0.1 | RO
325 | PV2 Current Point 2 | 0x1453 | S16 | A 0.01 | RO
326 | PV2 Voltage Point 99 | 0x1514 | U16 | V 0.1 | RO
327 | PV2 Current Point 99 | 0x1515 | S16 | A 0.01 | RO
328 | PV2 Voltage Point 100 | 0x1516 | U16 | V 0.1 | RO
329 | PV2 Current Point 100 | 0x1517 | S16 | A 0.01 | RO
330 | PV3 Voltage and CurrentPoint | 0x1518 | U16 |  | RO
331 | PV4 Voltage and CurrentPoint | 0x15E0 | U16 |  | RO
332 | PV5 Voltage and CurrentPoint | 0x16A8 | U16 |  | RO
333 | PV6 Voltage and CurrentPoint | 0x1770 | U16 |  | RO
334 | PV7 Voltage and CurrentPoint | 0x1838 | U16 |  | RO
335 | PV8 Voltage and CurrentPoint | 0x1900 | U16 |  | RO
336 | PV9 Voltage and CurrentPoint | 0x19C8 | U16 |  | RO
337 | PV10 Voltage and CurrentPoint | 0x1A90 | U16 |  | RO
338 | PV11 Voltage and CurrentPoint | 0x1B58 | U16 |  | RO
339 | PV12 Voltage and CurrentPoint | 0x1C20 | U16 |  | RO
340 | Aging Enable | 0x2328 | U16 |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Operating mode of theinverter | 0x0BD6 | U16 |  | RO | inverter_status | Table 3.1.4
2 | Input mode | 0x0BDD | U16 |  | RO |  | Table 3.1.8
3 | I/V Scan-status | 0x0C36 | U16 | V | RO |  | Table 3.1.15
4 | Grid protected mode | 0x0CAE | U16 |  | RO
5 | Set the reactivecontrol mode | 0x0FA6 | U16 |  | RO |  | Table 3.4.5
6 | Input ModeSettings | 0x0FAC | U16 |  | RO
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | AC Relay Fault | 0x000E | U16 |  | RO
2 | DSP alarm code | 0x0BD3 | U16 |  | RO |  | Table 3.1.2
3 | DSP error code | 0x0BD4 | U32 |  | RO |  | Table 3.1.3
4 | ARM alarm code | 0x0BDC | U16 |  | RO |  | Table 3.1.6
5 | Fuse alarm information | 0x0C81 | U32 |  | RO
6 | Over temperaturederating warningenable | 0x0C9B | U16 |  | RO
7 | Fault recovery time | 0x0CB0 | U16 |  | RO
8 | Clear FaultRecord | 0x0FC1 | U16 |  | RO
9 | Cancel power factor control (defaultpower factor: 1) | 0xFFFF | U16 |  | RO

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | 1
용량 | -
MPPT | 12 (PDF max 12개)
String | 24 (2/MPPT)
H01 매칭 | 65/66
DER 매칭 | 33/33
총 레지스터 | 372
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 17
MONITORING | 340
STATUS | 6
ALARM | 9
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | PDF | O | 0x0B96 | PV12 input power
13 | cumulative_energy | PDF | O | 0x0BE0 | Annual energy yield
14 | cumulative_energy_low | PDF | - | - | -
15 | status | PDF | O | 0x0BD6 | Operating mode of theinverter
16 | alarm1 | PDF | O | 0x0BD3 | DSP alarm code
17 | alarm2 | PDF | O | 0x0BD4 | DSP error code
18 | alarm3 | PDF | O | 0x0BDC | ARM alarm code
19 | mppt1_voltage | PDF | O | 0x0BB8 | PV1 input voltage
20 | mppt1_current | PDF | O | 0x0BBB | PV1 input current
21 | mppt2_voltage | PDF | O | 0x0BB9 | PV2 input voltage
22 | mppt2_current | PDF | O | 0x0BBC | PV2 input current
23 | mppt3_voltage | PDF | O | 0x0BBA | PV3 input voltage
24 | mppt3_current | PDF | O | 0x0BBD | PV3 input current
25 | mppt4_voltage | PDF | O | 0x0BB4 | PV4 input voltage
26 | mppt4_current | PDF | O | 0x0BB5 | PV4 input current
27 | mppt5_voltage | PDF | O | 0x0BB0 | PV5 input voltage
28 | mppt5_current | PDF | O | 0x0BB1 | PV5 input current
29 | mppt6_voltage | PDF | O | 0x0BAC | PV6 input voltage
30 | mppt6_current | PDF | O | 0x0BAD | PV6 input current
31 | mppt7_voltage | PDF | O | 0x0BA8 | PV7 input voltage
32 | mppt7_current | PDF | O | 0x0BA9 | PV7 input current
33 | mppt8_voltage | PDF | O | 0x0BA4 | PV8 input voltage
34 | mppt8_current | PDF | O | 0x0BA5 | PV8 input current
35 | mppt9_voltage | PDF | O | 0x0BA0 | PV9 input voltage
36 | mppt9_current | PDF | O | 0x0BA1 | PV9 input current
37 | mppt10_voltage | PDF | O | 0x0B9C | PV10 input voltage
38 | mppt10_current | PDF | O | 0x0B9D | PV10 input current
39 | mppt11_voltage | PDF | O | 0x0B98 | PV11 input voltage
40 | mppt11_current | PDF | O | 0x0B99 | PV11 input current
41 | mppt12_voltage | PDF | O | 0x0B94 | PV12 input voltage
42 | mppt12_current | PDF | O | 0x0B95 | PV12 input current
43 | string1_current | PDF | O | 0x0BF8 | PV1 String current 1
44 | string2_current | PDF | O | 0x0BF9 | PV1 String current 2
45 | string3_current | PDF | O | 0x0BFA | PV1 String current 3
46 | string4_current | PDF | O | 0x0BFB | PV1 String current 4
47 | string5_current | PDF | O | 0x0BFC | PV2 String current 1
48 | string6_current | PDF | O | 0x0BFD | PV2 String current 2
49 | string7_current | PDF | O | 0x0BFE | PV2 String current 3
50 | string8_current | PDF | O | 0x0BFF | PV2 String current 4
51 | string9_current | PDF | O | 0x0C00 | PV3 String current 1
52 | string10_current | PDF | O | 0x0C01 | PV3 String current 2
53 | string11_current | PDF | O | 0x0C02 | PV3 String current 3
54 | string12_current | PDF | O | 0x0C03 | PV3 String current 4
55 | string13_current | PDF | O | 0x0C04 | PV4 String current 1
56 | string14_current | PDF | O | 0x0C05 | PV4 String current 2
57 | string15_current | PDF | O | 0x0C06 | PV4 String current 3
58 | string16_current | PDF | O | 0x0C07 | PV4 String current 4
59 | string17_current | PDF | O | 0x0C08 | PV5 String current 1
60 | string18_current | PDF | O | 0x0C09 | PV5 String current 2
61 | string19_current | PDF | O | 0x0C0A | PV5 String current 3
62 | string20_current | PDF | O | 0x0C0B | PV5 String current 4
63 | string21_current | PDF | O | 0x0C0C | PV6 String current 1
64 | string22_current | PDF | O | 0x0C0D | PV6 String current 2
65 | string23_current | PDF | O | 0x0C0E | PV6 String current 3
66 | string24_current | PDF | O | 0x0C0F | PV6 String current 4