## Register_Mapping
No | Section | Source_Addr_Hex | Source_Addr_Dec | Source_Name | Source_Type | Source_Unit | Source_Scale | Source_RW | Source_Regs | → | Solarize_Name | Solarize_Addr_Hex | Match_Type | Notes
--- DEA-AVM Realtime Data ---
1 | DEA-AVM Realtime Data | 0x03E8 | 1000 | L1 Current | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW | 0x03E8 | Auto
2 | DEA-AVM Realtime Data | 0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_HIGH | 0x03E9 | Auto
3 | DEA-AVM Realtime Data | 0x03EA | 1002 | L2 Current | S32 | 0.1A | 0.1 | RO | 2 | → | DEA_L2_CURRENT_LOW | 0x03EA | Auto
4 | DEA-AVM Realtime Data | 0x03EA | 1002 | L2 Current | S32 | 0.1A | 0.1 | RO | 2 | → | DEA_L2_CURRENT_LOW | 0x03EA | Auto
5 | DEA-AVM Realtime Data | 0x03EB | 1003 | DEA_L2_CURRENT_HIGH | U16 |  |  | RO | 1 | → | DEA_L2_CURRENT_HIGH | 0x03EB | Auto
6 | DEA-AVM Realtime Data | 0x03EC | 1004 | L3 Current | U16 |  |  | RO | 1 | → | DEA_L3_CURRENT_LOW | 0x03EC | Auto
7 | DEA-AVM Realtime Data | 0x03ED | 1005 | DEA_L3_CURRENT_HIGH | U16 |  |  | RO | 1 | → | DEA_L3_CURRENT_HIGH | 0x03ED | Auto
8 | DEA-AVM Realtime Data | 0x03EE | 1006 | L1 Voltage | U16 |  |  | RO | 1 | → | DEA_L1_VOLTAGE_LOW | 0x03EE | Auto
9 | DEA-AVM Realtime Data | 0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | U16 |  |  | RO | 1 | → | DEA_L1_VOLTAGE_HIGH | 0x03EF | Auto
10 | DEA-AVM Realtime Data | 0x03F0 | 1008 | L2 Voltage | U16 |  |  | RO | 1 | → | DEA_L2_VOLTAGE_LOW | 0x03F0 | Auto
11 | DEA-AVM Realtime Data | 0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | U16 |  |  | RO | 1 | → | DEA_L2_VOLTAGE_HIGH | 0x03F1 | Auto
12 | DEA-AVM Realtime Data | 0x03F2 | 1010 | L3 Voltage | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_LOW | 0x03F2 | Auto
13 | DEA-AVM Realtime Data | 0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH | 0x03F3 | Auto
14 | DEA-AVM Realtime Data | 0x03F4 | 1012 | Grid total Active Power | U16 |  |  | RO | 1 | → | DEA_TOTAL_ACTIVE_POWER_LOW | 0x03F4 | Auto
15 | DEA-AVM Realtime Data | 0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | U16 |  |  | RO | 1 | → | DEA_TOTAL_ACTIVE_POWER_HIGH | 0x03F5 | Auto
16 | DEA-AVM Realtime Data | 0x03F6 | 1014 | Grid total Reactive Power | U16 |  |  | RO | 1 | → | DEA_TOTAL_REACTIVE_POWER_LOW | 0x03F6 | Auto
17 | DEA-AVM Realtime Data | 0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | U16 |  |  | RO | 1 | → | DEA_TOTAL_REACTIVE_POWER_HIGH | 0x03F7 | Auto
18 | DEA-AVM Realtime Data | 0x03F8 | 1016 | Power Factor | U16 |  |  | RO | 1 | → | DEA_POWER_FACTOR_LOW | 0x03F8 | Auto
19 | DEA-AVM Realtime Data | 0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | U16 |  |  | RO | 1 | → | DEA_POWER_FACTOR_HIGH | 0x03F9 | Auto
20 | DEA-AVM Realtime Data | 0x03FA | 1018 | Frequency | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW | 0x03FA | Auto
21 | DEA-AVM Realtime Data | 0x03FB | 1019 | DEA_FREQUENCY_HIGH | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH | 0x03FB | Auto
22 | DEA-AVM Realtime Data | 0x03FC | 1020 | Status Flag 1 | U16 |  |  | RO | 1 | → | DEA_STATUS_FLAG_LOW | 0x03FC | Auto
--- DER-AVM Parameters ---
23 | DER-AVM Parameters | 0x03FC | 1020 | PV8 fuse open check mask, [0,1] | U16 |  |  | RO | 1 | → | DEA_STATUS_FLAG_LOW | 0x03FC | Auto
--- DEA-AVM Realtime Data ---
24 | DEA-AVM Realtime Data | 0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | U16 |  |  | RO | 1 | → | DEA_STATUS_FLAG_HIGH | 0x03FD | Auto
--- DER-AVM Parameters ---
25 | DER-AVM Parameters | 0x07D0 | 2000 | Power factor setting | S16 | 0.001 |  | RW | 1 | → | DER_POWER_FACTOR_SET | 0x07D0 | Auto
26 | DER-AVM Parameters | 0x07D1 | 2001 | Action mode | U16 |  |  | RO | 1 | → | DER_ACTION_MODE | 0x07D1 | Auto
27 | DER-AVM Parameters | 0x07D2 | 2002 | Reactive power percent | U16 |  |  | RO | 1 | → | DER_REACTIVE_POWER_PCT | 0x07D2 | Auto
28 | DER-AVM Parameters | 0x07D3 | 2003 | Active power percent setting | U16 |  |  | RO | 1 | → | DER_ACTIVE_POWER_PCT | 0x07D3 | Auto
29 | DER-AVM Parameters | 0x0834 | 2100 | Inverter off | U16 |  |  | RO | 1 | → | INVERTER_ON_OFF | 0x0834 | Auto
30 | DER-AVM Parameters | 0x0835 | 2101 | Clear PV insulation warning | U16 |  |  | RO | 1 | → | CLEAR_PV_INSULATION_WARNING | 0x0835 | Auto
--- Inverter Realtime Data ---
31 | Inverter Realtime Data | 0x1001 | 4097 | L1 Voltage | U16 | 0.1V | 0.1 | RO | 1 | → | L1_VOLTAGE | 0x1001 | Auto
32 | Inverter Realtime Data | 0x1002 | 4098 | L1 Current | U16 |  |  | RO | 1 | → | L1_CURRENT | 0x1002 | Auto
33 | Inverter Realtime Data | 0x1003 | 4099 | L1 Power | U16 |  |  | RO | 1 | → | L1_POWER_LOW | 0x1003 | Auto
34 | Inverter Realtime Data | 0x1004 | 4100 | L1_POWER_HIGH | U16 |  |  | RO | 1 | → | L1_POWER_HIGH | 0x1004 | Auto
35 | Inverter Realtime Data | 0x1005 | 4101 | L1 Frequency | U16 |  |  | RO | 1 | → | L1_FREQUENCY | 0x1005 | Auto
36 | Inverter Realtime Data | 0x1006 | 4102 | L2 Voltage | U16 |  |  | RO | 1 | → | L2_VOLTAGE | 0x1006 | Auto
37 | Inverter Realtime Data | 0x1007 | 4103 | L2 Current | U16 |  |  | RO | 1 | → | L2_CURRENT | 0x1007 | Auto
38 | Inverter Realtime Data | 0x1008 | 4104 | L2 Power | U16 |  |  | RO | 1 | → | L2_POWER_LOW | 0x1008 | Auto
39 | Inverter Realtime Data | 0x1009 | 4105 | L2_POWER_HIGH | U16 |  |  | RO | 1 | → | L2_POWER_HIGH | 0x1009 | Auto
40 | Inverter Realtime Data | 0x100A | 4106 | L2 Frequency | U16 |  |  | RO | 1 | → | L2_FREQUENCY | 0x100A | Auto
41 | Inverter Realtime Data | 0x100B | 4107 | L3 Voltage | U16 |  |  | RO | 1 | → | L3_VOLTAGE | 0x100B | Auto
42 | Inverter Realtime Data | 0x100C | 4108 | L3 Current | U16 |  |  | RO | 1 | → | L3_CURRENT | 0x100C | Auto
43 | Inverter Realtime Data | 0x100D | 4109 | L3 Power | U16 |  |  | RO | 1 | → | L3_POWER_LOW | 0x100D | Auto
44 | Inverter Realtime Data | 0x100E | 4110 | L3_POWER_HIGH | U16 |  |  | RO | 1 | → | L3_POWER_HIGH | 0x100E | Auto
45 | Inverter Realtime Data | 0x100F | 4111 | L3 Frequency | U16 |  |  | RO | 1 | → | L3_FREQUENCY | 0x100F | Auto
46 | Inverter Realtime Data | 0x1010 | 4112 | MPPT1 Voltage | U16 |  |  | RO | 1 | → | MPPT1_VOLTAGE | 0x1010 | Auto
47 | Inverter Realtime Data | 0x1011 | 4113 | MPPT1 Current | U16 |  |  | RO | 1 | → | MPPT1_CURRENT | 0x1011 | Auto
48 | Inverter Realtime Data | 0x1012 | 4114 | MPPT1 Power | U16 |  |  | RO | 1 | → | MPPT1_POWER_LOW | 0x1012 | Auto
49 | Inverter Realtime Data | 0x1013 | 4115 | MPPT1_POWER_HIGH | U16 |  |  | RO | 1 | → | MPPT1_POWER_HIGH | 0x1013 | Auto
50 | Inverter Realtime Data | 0x1014 | 4116 | MPPT2 Voltage | U16 |  |  | RO | 1 | → | MPPT2_VOLTAGE | 0x1014 | Auto
51 | Inverter Realtime Data | 0x1015 | 4117 | MPPT2 Current | U16 |  |  | RO | 1 | → | MPPT2_CURRENT | 0x1015 | Auto
52 | Inverter Realtime Data | 0x1016 | 4118 | MPPT2 Power | U16 |  |  | RO | 1 | → | MPPT2_POWER_LOW | 0x1016 | Auto
53 | Inverter Realtime Data | 0x1017 | 4119 | MPPT2_POWER_HIGH | U16 |  |  | RO | 1 | → | MPPT2_POWER_HIGH | 0x1017 | Auto
54 | Inverter Realtime Data | 0x1018 | 4120 | MPPT3 Voltage | U16 |  |  | RO | 1 | → | MPPT3_VOLTAGE | 0x1018 | Auto
55 | Inverter Realtime Data | 0x1019 | 4121 | MPPT3 Current | U16 |  |  | RO | 1 | → | MPPT3_CURRENT | 0x1019 | Auto
56 | Inverter Realtime Data | 0x101A | 4122 | MPPT3 Power | U16 |  |  | RO | 1 | → | MPPT3_POWER_LOW | 0x101A | Auto
57 | Inverter Realtime Data | 0x101B | 4123 | MPPT3_POWER_HIGH | U16 |  |  | RO | 1 | → | MPPT3_POWER_HIGH | 0x101B | Auto
58 | Inverter Realtime Data | 0x101C | 4124 | Inner Temperature | U16 |  |  | RO | 1 | → | INNER_TEMP | 0x101C | Auto
59 | Inverter Realtime Data | 0x101D | 4125 | Inverter Mode | U16 |  |  | RO | 1 | → | INVERTER_MODE | 0x101D | Auto
--- DER-AVM Parameters ---
60 | DER-AVM Parameters | 0x101D | 4125 | PV8 fuse open data, [0,1] | U16 |  |  | RO | 1 | → | INVERTER_MODE | 0x101D | Auto
--- Inverter Realtime Data ---
61 | Inverter Realtime Data | 0x101E | 4126 | Error Code1 | U16 |  |  | RO | 1 | → | ERROR_CODE1 | 0x101E | Auto
62 | Inverter Realtime Data | 0x101F | 4127 | Error Code2 | U16 |  |  | RO | 1 | → | ERROR_CODE2 | 0x101F | Auto
--- DER-AVM Parameters ---
63 | DER-AVM Parameters | 0x101F | 4127 | Boost abnormal | U16 |  |  | RO | 1 | → | ERROR_CODE2 | 0x101F | Auto
--- Inverter Realtime Data ---
64 | Inverter Realtime Data | 0x1020 | 4128 | Error Code3 | U16 |  |  | RO | 1 | → | ERROR_CODE3 | 0x1020 | Auto
--- DER-AVM Parameters ---
65 | DER-AVM Parameters | 0x1020 | 4128 | AC moving average voltage high | U16 |  |  | RO | 15 | → | ERROR_CODE3 | 0x1020 | Auto
66 | DER-AVM Parameters | 0x1020 | 4128 | AC moving average voltage high | U16 |  |  | RO | 1 | → | ERROR_CODE3 | 0x1020 | Auto
--- Inverter Realtime Data ---
67 | Inverter Realtime Data | 0x1021 | 4129 | Total Energy | U16 |  |  | RO | 1 | → | TOTAL_ENERGY_LOW | 0x1021 | Auto
68 | Inverter Realtime Data | 0x1021 | 4129 | energy is 220.836kWh, | U16 | Wh |  | RO | 1 | → | TOTAL_ENERGY_LOW | 0x1021 | Auto
69 | Inverter Realtime Data | 0x1022 | 4130 | TOTAL_ENERGY_HIGH | U16 |  |  | RO | 1 | → | TOTAL_ENERGY_HIGH | 0x1022 | Auto
70 | Inverter Realtime Data | 0x1023 | 4131 | Total generation time | U16 |  |  | RO | 1 | → | TOTAL_GENERATION_TIME_LOW | 0x1023 | Auto
71 | Inverter Realtime Data | 0x1024 | 4132 | TOTAL_GENERATION_TIME_HIGH | U16 |  |  | RO | 1 | → | TOTAL_GENERATION_TIME_HIGH | 0x1024 | Auto
72 | Inverter Realtime Data | 0x1027 | 4135 | Today Energy | U16 |  |  | RO | 1 | → | TODAY_ENERGY_LOW | 0x1027 | Auto
73 | Inverter Realtime Data | 0x1028 | 4136 | TODAY_ENERGY_HIGH | U16 |  |  | RO | 1 | → | TODAY_ENERGY_HIGH | 0x1028 | Auto
74 | Inverter Realtime Data | 0x1034 | 4148 | Fuse open data | U16 |  |  | RO | 1 | → | FUSE_OPEN_DATA_LOW | 0x1034 | Auto
75 | Inverter Realtime Data | 0x1037 | 4151 | Grid total Active Power | U16 |  |  | RO | 1 | → | GRID_TOTAL_ACTIVE_POWER_LOW | 0x1037 | Auto
76 | Inverter Realtime Data | 0x1038 | 4152 | GRID_TOTAL_ACTIVE_POWER_HIGH | U16 |  |  | RO | 1 | → | GRID_TOTAL_ACTIVE_POWER_HIGH | 0x1038 | Auto
77 | Inverter Realtime Data | 0x1039 | 4153 | Grid total Reactive Power | U16 |  |  | RO | 1 | → | GRID_TOTAL_REACTIVE_POWER_LOW | 0x1039 | Auto
78 | Inverter Realtime Data | 0x103A | 4154 | GRID_TOTAL_REACTIVE_POWER_HIGH | U16 |  |  | RO | 1 | → | GRID_TOTAL_REACTIVE_POWER_HIGH | 0x103A | Auto
79 | Inverter Realtime Data | 0x103B | 4155 | PV Today Peak Power | U16 |  |  | RO | 1 | → | PV_TODAY_PEAK_POWER_LOW | 0x103B | Auto
80 | Inverter Realtime Data | 0x103D | 4157 | Power Factor | U16 |  |  | RO | 1 | → | POWER_FACTOR | 0x103D | Auto
81 | Inverter Realtime Data | 0x103E | 4158 | MPPT4 Voltage | U16 |  |  | RO | 1 | → | MPPT4_VOLTAGE | 0x103E | Auto
82 | Inverter Realtime Data | 0x103F | 4159 | MPPT4 Current | U16 |  |  | RO | 1 | → | MPPT4_CURRENT | 0x103F | Auto
83 | Inverter Realtime Data | 0x1040 | 4160 | MPPT4 Power | U16 |  |  | RO | 1 | → | MPPT4_POWER_LOW | 0x1040 | Auto
84 | Inverter Realtime Data | 0x1041 | 4161 | MPPT4_POWER_HIGH | U16 |  |  | RO | 1 | → | MPPT4_POWER_HIGH | 0x1041 | Auto
85 | Inverter Realtime Data | 0x1048 | 4168 | PV total input power | U16 |  |  | RO | 1 | → | PV_TOTAL_INPUT_POWER_LOW | 0x1048 | Auto
86 | Inverter Realtime Data | 0x1049 | 4169 | PV_TOTAL_INPUT_POWER_HIGH | U16 |  |  | RO | 1 | → | PV_TOTAL_INPUT_POWER_HIGH | 0x1049 | Auto
87 | Inverter Realtime Data | 0x104C | 4172 | Decimals of total energy | U16 |  |  | RO | 1 | → | TOTAL_ENERGY_DECIMALS | 0x104C | Auto
88 | Inverter Realtime Data | 0x1050 | 4176 | String1 input voltage | U16 |  |  | RO | 1 | → | STRING1_VOLTAGE | 0x1050 | Auto
89 | Inverter Realtime Data | 0x1051 | 4177 | String1 input current | U16 |  |  | RO | 1 | → | STRING1_CURRENT | 0x1051 | Auto
90 | Inverter Realtime Data | 0x1052 | 4178 | String2 input voltage | U16 |  |  | RO | 1 | → | STRING2_VOLTAGE | 0x1052 | Auto
91 | Inverter Realtime Data | 0x1053 | 4179 | String2 input current | U16 |  |  | RO | 1 | → | STRING2_CURRENT | 0x1053 | Auto
92 | Inverter Realtime Data | 0x1054 | 4180 | String3 input voltage | U16 |  |  | RO | 1 | → | STRING3_VOLTAGE | 0x1054 | Auto
93 | Inverter Realtime Data | 0x1055 | 4181 | String3 input current | U16 |  |  | RO | 1 | → | STRING3_CURRENT | 0x1055 | Auto
94 | Inverter Realtime Data | 0x1056 | 4182 | String4 input voltage | U16 |  |  | RO | 1 | → | STRING4_VOLTAGE | 0x1056 | Auto
95 | Inverter Realtime Data | 0x1057 | 4183 | String4 input current | U16 |  |  | RO | 1 | → | STRING4_CURRENT | 0x1057 | Auto
96 | Inverter Realtime Data | 0x1058 | 4184 | String5 input voltage | U16 |  |  | RO | 1 | → | STRING5_VOLTAGE | 0x1058 | Auto
97 | Inverter Realtime Data | 0x1059 | 4185 | String5 input current | U16 |  |  | RO | 1 | → | STRING5_CURRENT | 0x1059 | Auto
98 | Inverter Realtime Data | 0x105A | 4186 | String6 input voltage | U16 |  |  | RO | 1 | → | STRING6_VOLTAGE | 0x105A | Auto
99 | Inverter Realtime Data | 0x105B | 4187 | String6 input current | U16 |  |  | RO | 1 | → | STRING6_CURRENT | 0x105B | Auto
100 | Inverter Realtime Data | 0x105C | 4188 | String7 input voltage | U16 |  |  | RO | 1 | → | STRING7_VOLTAGE | 0x105C | Auto
101 | Inverter Realtime Data | 0x105D | 4189 | String7 input current | U16 |  |  | RO | 1 | → | STRING7_CURRENT | 0x105D | Auto
102 | Inverter Realtime Data | 0x105E | 4190 | String8 input voltage | U16 |  |  | RO | 1 | → | STRING8_VOLTAGE | 0x105E | Auto
103 | Inverter Realtime Data | 0x105F | 4191 | String8 input current | U16 |  |  | RO | 1 | → | STRING8_CURRENT | 0x105F | Auto
104 | Inverter Realtime Data | 0x1060 | 4192 | String9 input voltage | U16 |  |  | RO | 1 | → | STRING9_VOLTAGE | 0x1060 | Auto
105 | Inverter Realtime Data | 0x1061 | 4193 | String9 input current | U16 |  |  | RO | 1 | → | STRING9_CURRENT | 0x1061 | Auto
106 | Inverter Realtime Data | 0x1062 | 4194 | String10 input voltage | U16 |  |  | RO | 1 | → | STRING10_VOLTAGE | 0x1062 | Auto
107 | Inverter Realtime Data | 0x1063 | 4195 | String10 input current | U16 |  |  | RO | 1 | → | STRING10_CURRENT | 0x1063 | Auto
108 | Inverter Realtime Data | 0x1064 | 4196 | String11 input voltage | U16 |  |  | RO | 1 | → | STRING11_VOLTAGE | 0x1064 | Auto
109 | Inverter Realtime Data | 0x1065 | 4197 | String11 input current | U16 |  |  | RO | 1 | → | STRING11_CURRENT | 0x1065 | Auto
110 | Inverter Realtime Data | 0x1066 | 4198 | String12 input voltage | U16 |  |  | RO | 1 | → | STRING12_VOLTAGE | 0x1066 | Auto
111 | Inverter Realtime Data | 0x1067 | 4199 | String12 input current | U16 |  |  | RO | 1 | → | STRING12_CURRENT | 0x1067 | Auto
112 | Inverter Realtime Data | 0x1068 | 4200 | String13 input voltage | U16 |  |  | RO | 1 | → | STRING13_VOLTAGE | 0x1068 | Auto
113 | Inverter Realtime Data | 0x1069 | 4201 | String13 input current | U16 |  |  | RO | 1 | → | STRING13_CURRENT | 0x1069 | Auto
114 | Inverter Realtime Data | 0x106A | 4202 | String14 input voltage | U16 |  |  | RO | 1 | → | STRING14_VOLTAGE | 0x106A | Auto
115 | Inverter Realtime Data | 0x106B | 4203 | String14 input current | U16 |  |  | RO | 1 | → | STRING14_CURRENT | 0x106B | Auto
116 | Inverter Realtime Data | 0x106C | 4204 | String15 input voltage | U16 |  |  | RO | 1 | → | STRING15_VOLTAGE | 0x106C | Auto
117 | Inverter Realtime Data | 0x106D | 4205 | String15 input current | U16 |  |  | RO | 1 | → | STRING15_CURRENT | 0x106D | Auto
118 | Inverter Realtime Data | 0x106E | 4206 | String16 input voltage | U16 |  |  | RO | 1 | → | STRING16_VOLTAGE | 0x106E | Auto
119 | Inverter Realtime Data | 0x106F | 4207 | String16 input current | U16 |  |  | RO | 1 | → | STRING16_CURRENT | 0x106F | Auto
120 | Inverter Realtime Data | 0x1070 | 4208 | String17 input voltage | U16 |  |  | RO | 1 | → | STRING17_VOLTAGE | 0x1070 | Auto
121 | Inverter Realtime Data | 0x1071 | 4209 | String17 input current | U16 |  |  | RO | 1 | → | STRING17_CURRENT | 0x1071 | Auto
122 | Inverter Realtime Data | 0x1072 | 4210 | String18 input voltage | U16 |  |  | RO | 1 | → | STRING18_VOLTAGE | 0x1072 | Auto
123 | Inverter Realtime Data | 0x1073 | 4211 | String18 input current | U16 |  |  | RO | 1 | → | STRING18_CURRENT | 0x1073 | Auto
124 | Inverter Realtime Data | 0x1074 | 4212 | String19 input voltage | U16 |  |  | RO | 1 | → | STRING19_VOLTAGE | 0x1074 | Auto
125 | Inverter Realtime Data | 0x1075 | 4213 | String19 input current | U16 |  |  | RO | 1 | → | STRING19_CURRENT | 0x1075 | Auto
126 | Inverter Realtime Data | 0x1076 | 4214 | String20 input voltage | U16 |  |  | RO | 1 | → | STRING20_VOLTAGE | 0x1076 | Auto
127 | Inverter Realtime Data | 0x1077 | 4215 | String20 input current | U16 |  |  | RO | 1 | → | STRING20_CURRENT | 0x1077 | Auto
128 | Inverter Realtime Data | 0x1078 | 4216 | String21 input voltage | U16 |  |  | RO | 1 | → | STRING21_VOLTAGE | 0x1078 | Auto
129 | Inverter Realtime Data | 0x1079 | 4217 | String21 input current | U16 |  |  | RO | 1 | → | STRING21_CURRENT | 0x1079 | Auto
130 | Inverter Realtime Data | 0x107A | 4218 | String22 input voltage | U16 |  |  | RO | 1 | → | STRING22_VOLTAGE | 0x107A | Auto
131 | Inverter Realtime Data | 0x107B | 4219 | String22 input current | U16 |  |  | RO | 1 | → | STRING22_CURRENT | 0x107B | Auto
132 | Inverter Realtime Data | 0x107C | 4220 | String23 input voltage | U16 |  |  | RO | 1 | → | STRING23_VOLTAGE | 0x107C | Auto
133 | Inverter Realtime Data | 0x107D | 4221 | String23 input current | U16 |  |  | RO | 1 | → | STRING23_CURRENT | 0x107D | Auto
134 | Inverter Realtime Data | 0x107E | 4222 | String24 input voltage | U16 |  |  | RO | 1 | → | STRING24_VOLTAGE | 0x107E | Auto
135 | Inverter Realtime Data | 0x107F | 4223 | String24 input current | U16 |  |  | RO | 1 | → | STRING24_CURRENT | 0x107F | Auto
136 | Inverter Realtime Data | 0x1080 | 4224 | MPPT5 Voltage | U16 |  |  | RO | 1 | → | MPPT5_VOLTAGE | 0x1080 | Auto
137 | Inverter Realtime Data | 0x1081 | 4225 | MPPT5 Current | U16 |  |  | RO | 1 | → | MPPT5_CURRENT | 0x1081 | Auto
138 | Inverter Realtime Data | 0x1082 | 4226 | MPPT5 Power | U16 |  |  | RO | 1 | → | MPPT5_POWER_LOW | 0x1082 | Auto
139 | Inverter Realtime Data | 0x1084 | 4228 | MPPT6 Voltage | U16 |  |  | RO | 1 | → | MPPT6_VOLTAGE | 0x1084 | Auto
140 | Inverter Realtime Data | 0x1085 | 4229 | MPPT6 Current | U16 |  |  | RO | 1 | → | MPPT6_CURRENT | 0x1085 | Auto
141 | Inverter Realtime Data | 0x1086 | 4230 | MPPT6 Power | U16 |  |  | RO | 1 | → | MPPT6_POWER_LOW | 0x1086 | Auto
142 | Inverter Realtime Data | 0x1088 | 4232 | MPPT7 Voltage | U16 |  |  | RO | 1 | → | MPPT7_VOLTAGE | 0x1088 | Auto
143 | Inverter Realtime Data | 0x1089 | 4233 | MPPT7 Current | U16 |  |  | RO | 1 | → | MPPT7_CURRENT | 0x1089 | Auto
144 | Inverter Realtime Data | 0x108A | 4234 | MPPT7 Power | U16 |  |  | RO | 1 | → | MPPT7_POWER_LOW | 0x108A | Auto
145 | Inverter Realtime Data | 0x108C | 4236 | MPPT8 Voltage | U16 |  |  | RO | 1 | → | MPPT8_VOLTAGE | 0x108C | Auto
146 | Inverter Realtime Data | 0x108D | 4237 | MPPT8 Current | U16 |  |  | RO | 1 | → | MPPT8_CURRENT | 0x108D | Auto
147 | Inverter Realtime Data | 0x108E | 4238 | MPPT8 Power | U16 |  |  | RO | 1 | → | MPPT8_POWER_LOW | 0x108E | Auto
148 | Inverter Realtime Data | 0x1090 | 4240 | MPPT9 Voltage | U16 |  |  | RO | 1 | → | MPPT9_VOLTAGE | 0x1090 | Auto
149 | Inverter Realtime Data | 0x1091 | 4241 | MPPT9 Current | U16 |  |  | RO | 1 | → | MPPT9_CURRENT | 0x1091 | Auto
150 | Inverter Realtime Data | 0x1092 | 4242 | MPPT9 Power | U16 |  |  | RO | 1 | → | MPPT9_POWER_LOW | 0x1092 | Auto
151 | Inverter Realtime Data | 0x120C | 4620 | External fan speed duty | U16 |  |  | RO | 1 | → | FAN_SPEED_DUTY_PCT | 0x120C | Auto
152 | Inverter Realtime Data | 0x1210 | 4624 | DER_AVM_METER_STATUS | U16 |  |  | RO | 1 | → | DER_AVM_METER_STATUS | 0x1210 | Auto
--- Inverter Parameters ---
153 | Inverter Parameters | 0x1211 | 4625 | DER_AVM_MODE | U16 |  |  | RW | 1 | → | DER_AVM_MODE | 0x1211 | Auto
--- Inverter Realtime Data ---
154 | Inverter Realtime Data | 0x1226 | 4646 | Q (Reference Output reactive | U16 |  |  | RO | 1 | → |  |  | Unmapped
--- Inverter Parameters ---
155 | Inverter Parameters | 0x1240 | 4672 | RS485-2 Modbus address | U16 |  |  | RO | 1 | → |  |  | Unmapped
156 | Inverter Parameters | 0x1241 | 4673 | RS485-2 UART baud rate | U16 |  |  | RO | 1 | → |  |  | Unmapped
157 | Inverter Parameters | 0x1242 | 4674 | RS485-2 terminal resistance | U16 |  |  | RO | 1 | → |  |  | Unmapped
158 | Inverter Parameters | 0x1243 | 4675 | RS485-3 Modbus address | U16 |  |  | RO | 1 | → |  |  | Unmapped
159 | Inverter Parameters | 0x1244 | 4676 | RS485-3 UART baud rate | U16 |  |  | RO | 1 | → |  |  | Unmapped
160 | Inverter Parameters | 0x1245 | 4677 | RS485-3 terminal resistance | U16 |  |  | RO | 1 | → |  |  | Unmapped
--- Inverter Realtime Data ---
161 | Inverter Realtime Data | 0x1300 | 4864 | L1 watt of grid | U16 |  |  | RO | 1 | → |  |  | Unmapped
162 | Inverter Realtime Data | 0x1302 | 4866 | L2 watt of grid | U16 |  |  | RO | 1 | → |  |  | Unmapped
163 | Inverter Realtime Data | 0x1304 | 4868 | L3 watt of grid | U16 |  |  | RO | 1 | → |  |  | Unmapped
164 | Inverter Realtime Data | 0x1306 | 4870 | Accumulated energy of | U16 |  |  | RO | 1 | → | ACCUMULATED_ENERGY |  | Ref(92%)
165 | Inverter Realtime Data | 0x1308 | 4872 | Accumulated energy of | U16 |  |  | RO | 1 | → | ACCUMULATED_ENERGY |  | Ref(92%)
166 | Inverter Realtime Data | 0x130A | 4874 | L1 watt of load | U16 |  |  | RO | 1 | → |  |  | Unmapped
167 | Inverter Realtime Data | 0x130C | 4876 | L2 watt of load | U16 |  |  | RO | 1 | → |  |  | Unmapped
168 | Inverter Realtime Data | 0x130E | 4878 | L3 watt of load | U16 |  |  | RO | 1 | → |  |  | Unmapped
169 | Inverter Realtime Data | 0x1310 | 4880 | Accumulated energy of load | U16 |  |  | RO | 1 | → | ACCUMULATED_ENERGY |  | Ref(82%)
170 | Inverter Realtime Data | 0x131A | 4890 | L1-N phase voltage of grid | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(68%)
171 | Inverter Realtime Data | 0x131B | 4891 | L2-N phase voltage of grid | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(68%)
172 | Inverter Realtime Data | 0x131C | 4892 | L3-N phase voltage of grid | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(68%)
173 | Inverter Realtime Data | 0x131D | 4893 | L1 current of grid | U16 |  |  | RO | 1 | → | L1_CURRENT |  | Ref(71%)
174 | Inverter Realtime Data | 0x131F | 4895 | L2 current of grid | U16 |  |  | RO | 1 | → | L2_CURRENT |  | Ref(71%)
175 | Inverter Realtime Data | 0x1321 | 4897 | L3 current of grid | U16 |  |  | RO | 1 | → | L3_CURRENT |  | Ref(71%)
176 | Inverter Realtime Data | 0x1323 | 4899 | L1-N phase voltage of load | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(68%)
177 | Inverter Realtime Data | 0x1324 | 4900 | L2-N phase voltage of load | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(68%)
178 | Inverter Realtime Data | 0x1325 | 4901 | L3-N phase voltage of load | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(68%)
179 | Inverter Realtime Data | 0x1326 | 4902 | L1 current of load | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW |  | Ref(72%)
180 | Inverter Realtime Data | 0x1328 | 4904 | L2 current of load | U16 |  |  | RO | 1 | → | DEA_L2_CURRENT_LOW |  | Ref(72%)
181 | Inverter Realtime Data | 0x132A | 4906 | L3 current of load | U16 |  |  | RO | 1 | → | DEA_L3_CURRENT_LOW |  | Ref(72%)
182 | Inverter Realtime Data | 0x1332 | 4914 | Today import Energy | U16 |  |  | RO | 1 | → | TODAY_ENERGY |  | Ref(77%)
183 | Inverter Realtime Data | 0x1334 | 4916 | Today export Energy | U16 |  |  | RO | 1 | → | TODAY_ENERGY |  | Ref(77%)
184 | Inverter Realtime Data | 0x1336 | 4918 | Today load Energy | U16 |  |  | RO | 1 | → | TODAY_ENERGY |  | Ref(83%)
185 | Inverter Realtime Data | 0x1338 | 4920 | Frequency of grid | U16 |  |  | RO | 1 | → | FREQUENCY |  | Ref(69%)
--- Device Information ---
186 | Device Information | 0x1A00 | 6656 | Device Model name | U16 |  |  | RO | 1 | → | DEVICE_MODEL | 0x1A00 | Auto
187 | Device Information | 0x1A10 | 6672 | Device Serial number | U16 |  |  | RO | 1 | → | SERIAL_NUMBER | 0x1A10 | Auto
188 | Device Information | 0x1A1C | 6684 | Master firmware version | U16 | ASCII |  | RO | 3 | → | MASTER_FIRMWARE_VERSION | 0x1A1C | Auto
189 | Device Information | 0x1A26 | 6694 | Slave firmware version | U16 |  |  | RO | 1 | → | SLAVE_FIRMWARE_VERSION | 0x1A26 | Auto
190 | Device Information | 0x1A3B | 6715 | MPPT Number | U16 |  |  | RO | 1 | → | MPPT_COUNT | 0x1A3B | Auto
191 | Device Information | 0x1A44 | 6724 | Nominal Voltage | U16 |  |  | RO | 1 | → | NOMINAL_VOLTAGE | 0x1A44 | Auto
--- Inverter Parameters ---
192 | Inverter Parameters | 0x1A44 | 6724 | Nominal voltage | U16 |  |  | RO | 1 | → | NOMINAL_VOLTAGE | 0x1A44 | Auto
--- Device Information ---
193 | Device Information | 0x1A45 | 6725 | Nominal Frequency | U16 |  |  | RO | 1 | → | NOMINAL_FREQUENCY | 0x1A45 | Auto
194 | Device Information | 0x1A46 | 6726 | Nominal Active Power | U16 |  |  | RO | 1 | → | NOMINAL_POWER_LOW | 0x1A46 | Auto
195 | Device Information | 0x1A48 | 6728 | Grid Phase Number | U16 |  |  | RO | 1 | → | GRID_PHASE_NUMBER | 0x1A48 | Auto
196 | Device Information | 0x1A4E | 6734 | Nominal Active Power | U16 |  |  | RO | 1 | → | NOMINAL_POWER_HIGH | 0x1A4E | Auto
197 | Device Information | 0x1A60 | 6752 | EMS Firmware Version | U16 |  |  | RO | 1 | → | EMS_FIRMWARE_VERSION | 0x1A60 | Auto
198 | Device Information | 0x1A8E | 6798 | LCD firmware version | U16 |  |  | RO | 1 | → | LCD_FIRMWARE_VERSION | 0x1A8E | Auto
--- Inverter Parameters ---
199 | Inverter Parameters | 0x3000 | 12288 | Date：Year | U16 |  |  | RO | 1 | → |  |  | Unmapped
200 | Inverter Parameters | 0x3001 | 12289 | Date：Month + Day | U16 |  |  | RO | 1 | → |  |  | Unmapped
201 | Inverter Parameters | 0x3002 | 12290 | Date：Hour + Minute | U16 |  |  | RO | 1 | → | RADIATOR_TEMP |  | Ref(57%)
202 | Inverter Parameters | 0x3003 | 12291 | Date：Second + 0 | U16 |  |  | RO | 1 | → |  |  | Unmapped
203 | Inverter Parameters | 0x3005 | 12293 | Power derating percent by | U16 |  |  | RO | 1 | → | POWER_DERATING_PCT | 0x3005 | Auto
204 | Inverter Parameters | 0x303E | 12350 | RS485-1 Modbus Address | U16 |  |  | RO | 1 | → |  |  | Unmapped
205 | Inverter Parameters | 0x304C | 12364 | RS485-1 baud rate | U16 |  |  | RO | 1 | → |  |  | Unmapped
206 | Inverter Parameters | 0x3060 | 12384 | WIFI STA SSID | string | ASCII |  | RW | 16 | → |  |  | Unmapped
207 | Inverter Parameters | 0x3070 | 12400 | WIFI STA password | U16 |  |  | RO | 1 | → |  |  | Unmapped
208 | Inverter Parameters | 0x30B0 | 12464 | Digital meter Modbus address | U16 |  |  | RO | 1 | → |  |  | Unmapped
209 | Inverter Parameters | 0x30B1 | 12465 | Digital meter Type | U16 |  |  | RO | 1 | → | DEVICE_TYPE |  | Ref(55%)
210 | Inverter Parameters | 0x30B2 | 12466 | Power flow direction | U16 |  |  | RO | 1 | → | POWER_FACTOR |  | Ref(62%)
211 | Inverter Parameters | 0x30B3 | 12467 | Power limit function | U16 |  |  | RO | 1 | → | POWER_FACTOR |  | Ref(62%)
212 | Inverter Parameters | 0x30B4 | 12468 | Power limit CT ratio | U16 |  |  | RO | 1 | → | POWER_FACTOR |  | Ref(56%)
213 | Inverter Parameters | 0x30B5 | 12469 | Meter location | U16 |  |  | RO | 1 | → | DER_ACTION_MODE |  | Ref(55%)
214 | Inverter Parameters | 0x30B9 | 12473 | Maximum feed in grid power | U16 |  |  | RO | 1 | → |  |  | Unmapped
215 | Inverter Parameters | 0x5000 | 20480 | First connect start time | U16 |  |  | RO | 1 | → |  |  | Unmapped
216 | Inverter Parameters | 0x5001 | 20481 | Reconnect time | U16 |  |  | RO | 1 | → |  |  | Unmapped
217 | Inverter Parameters | 0x5002 | 20482 | Grid frequency high loss level | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(67%)
218 | Inverter Parameters | 0x5003 | 20483 | Grid frequency low loss level 1 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(62%)
219 | Inverter Parameters | 0x5004 | 20484 | Grid voltage high loss level 1 | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(57%)
220 | Inverter Parameters | 0x5005 | 20485 | Grid voltage low loss level 1 | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(56%)
221 | Inverter Parameters | 0x5006 | 20486 | Grid frequency high loss level | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(67%)
222 | Inverter Parameters | 0x5007 | 20487 | Grid frequency low loss level 1 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(62%)
223 | Inverter Parameters | 0x5008 | 20488 | Grid voltage high loss level 1 | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(57%)
224 | Inverter Parameters | 0x5009 | 20489 | Grid voltage low loss level 1 | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(56%)
225 | Inverter Parameters | 0x500A | 20490 | Grid frequency high loss level | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(67%)
226 | Inverter Parameters | 0x500B | 20491 | Grid frequency low loss level 2 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(62%)
227 | Inverter Parameters | 0x500C | 20492 | Grid voltage high loss level 2 | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(57%)
228 | Inverter Parameters | 0x500D | 20493 | Grid voltage low loss level 2 | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(56%)
229 | Inverter Parameters | 0x500E | 20494 | Grid frequency high loss level | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(67%)
230 | Inverter Parameters | 0x500F | 20495 | Grid frequency low loss level 2 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(62%)
231 | Inverter Parameters | 0x5010 | 20496 | Grid voltage high loss level 2 | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(57%)
232 | Inverter Parameters | 0x5011 | 20497 | Grid voltage low loss level 2 | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(56%)
233 | Inverter Parameters | 0x5012 | 20498 | Grid Frequency High Level 1 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(71%)
234 | Inverter Parameters | 0x5013 | 20499 | Grid Frequency Low Level 1 | U16 |  |  | RO | 1 | → | GRID_FREQUENCY |  | Ref(70%)
235 | Inverter Parameters | 0x5018 | 20504 | 10 min average sustained | U16 |  |  | RO | 1 | → |  |  | Unmapped
236 | Inverter Parameters | 0x5019 | 20505 | Reconnect soft output power | U16 |  |  | RO | 1 | → |  |  | Unmapped
237 | Inverter Parameters | 0x501A | 20506 | Over frequency power | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(76%)
238 | Inverter Parameters | 0x501B | 20507 | Insulation resistance active | U16 |  |  | RO | 1 | → |  |  | Unmapped
239 | Inverter Parameters | 0x501E | 20510 | Grid over voltage de-rating | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(68%)
240 | Inverter Parameters | 0x501E | 20510 | [0, 1] | U16 |  |  | RW | 1 | → |  |  | Unmapped
241 | Inverter Parameters | 0x501F | 20511 | Grid frequency high Level 1 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(71%)
242 | Inverter Parameters | 0x5020 | 20512 | Grid frequency low Level 1 trip | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(62%)
243 | Inverter Parameters | 0x5021 | 20513 | Grid over frequency de-rating | U16 |  |  | RO | 1 | → | GRID_T_FREQUENCY |  | Ref(67%)
244 | Inverter Parameters | 0x5022 | 20514 | Grid over frequency de-rating | U16 |  |  | RO | 1 | → | GRID_T_FREQUENCY |  | Ref(67%)
245 | Inverter Parameters | 0x5025 | 20517 | Grid Voltage High Level 1 trip | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(57%)
246 | Inverter Parameters | 0x5026 | 20518 | Grid Voltage Low Level 1 trip | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(56%)
247 | Inverter Parameters | 0x5027 | 20519 | Grid Voltage High Level 1 | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(64%)
248 | Inverter Parameters | 0x5028 | 20520 | Grid Voltage Low Level 1 back | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(56%)
249 | Inverter Parameters | 0x5029 | 20521 | First connect soft start output | U16 |  |  | RO | 1 | → |  |  | Unmapped
250 | Inverter Parameters | 0x5030 | 20528 | Output reactive power mode | U16 |  |  | RO | 1 | → | REACTIVE_POWER_SET |  | Ref(73%)
251 | Inverter Parameters | 0x5031 | 20529 | [0,9] | U16 |  |  | RW | 1 | → |  |  | Unmapped
252 | Inverter Parameters | 0x5031 | 20529 | Power factor setting | U16 |  |  | RO | 1 | → | POWER_FACTOR_SET |  | Ref(89%)
253 | Inverter Parameters | 0x5033 | 20531 | Reactive control response | U16 |  |  | RO | 1 | → | REACTIVE_POWER |  | Ref(62%)
254 | Inverter Parameters | 0x503C | 20540 | Q(U) curve node1 | U16 |  |  | RO | 1 | → | IV_CURVE_SCAN |  | Ref(59%)
255 | Inverter Parameters | 0x503D | 20541 | Q(U) curve node2 | U16 |  |  | RO | 1 | → | IV_CURVE_SCAN |  | Ref(59%)
256 | Inverter Parameters | 0x503E | 20542 | Q(U) curve node3 | U16 |  |  | RO | 1 | → | IV_CURVE_SCAN |  | Ref(59%)
257 | Inverter Parameters | 0x503F | 20543 | Q(U) curve node4 | U16 |  |  | RO | 1 | → | IV_CURVE_SCAN |  | Ref(59%)
258 | Inverter Parameters | 0x5040 | 20544 | Q(U) curve node1 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
259 | Inverter Parameters | 0x5041 | 20545 | Q(U) curve node2 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
260 | Inverter Parameters | 0x5042 | 20546 | Q(U) curve node3 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
261 | Inverter Parameters | 0x5043 | 20547 | Q(U) curve node4 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
262 | Inverter Parameters | 0x504B | 20555 | Volt-Watt node1 voltage for | U16 |  |  | RO | 1 | → | DEA_L1_VOLTAGE_LOW |  | Ref(58%)
263 | Inverter Parameters | 0x504C | 20556 | Volt-Watt node2 voltage for | U16 |  |  | RO | 1 | → | DEA_L2_VOLTAGE_LOW |  | Ref(58%)
264 | Inverter Parameters | 0x504F | 20559 | Volt-Watt node1 output | U16 |  |  | RO | 1 | → |  |  | Unmapped
265 | Inverter Parameters | 0x5050 | 20560 | Volt-Watt node2 output | U16 |  |  | RO | 1 | → |  |  | Unmapped
266 | Inverter Parameters | 0x505A | 20570 | Q(P) curve node 1 percentage | U16 |  |  | RO | 1 | → |  |  | Unmapped
267 | Inverter Parameters | 0x505B | 20571 | Q(P) curve node 2 percentage | U16 |  |  | RO | 1 | → |  |  | Unmapped
268 | Inverter Parameters | 0x505C | 20572 | Q(P) curve node 3 percentage | U16 |  |  | RO | 1 | → |  |  | Unmapped
269 | Inverter Parameters | 0x505D | 20573 | Q(P) curve node 4 percentage | U16 |  |  | RO | 1 | → |  |  | Unmapped
270 | Inverter Parameters | 0x505E | 20574 | Q(P) curve node 1 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
271 | Inverter Parameters | 0x505F | 20575 | Q(P) curve node 2 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
272 | Inverter Parameters | 0x5060 | 20576 | Q(P) curve node 3 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
273 | Inverter Parameters | 0x5061 | 20577 | Q(P) curve node 4 value | U16 |  |  | RO | 1 | → |  |  | Unmapped
274 | Inverter Parameters | 0x5063 | 20579 | LVRT Triggering voltage | U16 |  |  | RO | 1 | → | STRING1_VOLTAGE |  | Ref(68%)
275 | Inverter Parameters | 0x5064 | 20580 | HVRT Triggering voltage | U16 |  |  | RO | 1 | → | STRING1_VOLTAGE |  | Ref(68%)
276 | Inverter Parameters | 0x5065 | 20581 | FRT Mode | U16 |  |  | RO | 1 | → | INVERTER_MODE |  | Ref(67%)
277 | Inverter Parameters | 0x5066 | 20582 | FRT | U16 |  |  | RO | 1 | → |  |  | Unmapped
278 | Inverter Parameters | 0x5067 | 20583 | FRT | U16 |  |  | RO | 1 | → |  |  | Unmapped
279 | Inverter Parameters | 0x506C | 20588 | Grid frequency high Level 2 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(71%)
280 | Inverter Parameters | 0x506D | 20589 | Grid frequency low Level 2 trip | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(62%)
281 | Inverter Parameters | 0x5070 | 20592 | Grid frequency high level 3 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(71%)
282 | Inverter Parameters | 0x5071 | 20593 | Grid frequency low level 3 | U16 |  |  | RO | 1 | → | GRID_FREQUENCY |  | Ref(70%)
283 | Inverter Parameters | 0x5072 | 20594 | Grid voltage high level 3 limit | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(56%)
284 | Inverter Parameters | 0x5073 | 20595 | Grid voltage low level 3 limit | U16 |  |  | RO | 1 | → |  |  | Unmapped
285 | Inverter Parameters | 0x5074 | 20596 | Grid Frequency High Level 3 | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(71%)
286 | Inverter Parameters | 0x5075 | 20597 | Grid Frequency Low Level 3 | U16 |  |  | RO | 1 | → | GRID_FREQUENCY |  | Ref(70%)
287 | Inverter Parameters | 0x5076 | 20598 | Grid Voltage High Level 3 trip | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(57%)
288 | Inverter Parameters | 0x5077 | 20599 | Grid Voltage Low Level 3 trip | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(56%)
289 | Inverter Parameters | 0x507F | 20607 | Over frequency derating | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_HIGH |  | Ref(68%)
290 | Inverter Parameters | 0x5081 | 20609 | Grid under frequency rise | U16 |  |  | RO | 1 | → | GRID_T_FREQUENCY |  | Ref(73%)
291 | Inverter Parameters | 0x5082 | 20610 | Grid under frequency rise | U16 |  |  | RO | 1 | → | GRID_T_FREQUENCY |  | Ref(73%)
292 | Inverter Parameters | 0x5083 | 20611 | Under frequency rise power | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(70%)
293 | Inverter Parameters | 0x5084 | 20612 | Under frequency rise power | U16 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW |  | Ref(70%)
294 | Inverter Parameters | 0x5101 | 20737 | Regulation code | U16 |  |  | RO | 1 | → | ACTION_MODE |  | Ref(69%)
--- IV Scan ---
295 | IV Scan | 0x5101 | 20737 | [0, 65535] | S16 | 0.01% | 0.01 | RW | 1 | → |  |  | Unmapped
--- DER-AVM Parameters ---
296 | DER-AVM Parameters | 0x5101 | 20737 | Reserved | U16 |  |  | RO | 1 | → |  |  | Unmapped
--- Inverter Parameters ---
297 | Inverter Parameters | 0x5104 | 20740 | Derating Watt Percent | U16 |  |  | RO | 1 | → | DER_ACTIVE_POWER_PCT |  | Ref(59%)
298 | Inverter Parameters | 0x5106 | 20742 | Mppt shadow manage | U16 |  |  | RO | 1 | → | MPPT2_VOLTAGE |  | Ref(58%)
299 | Inverter Parameters | 0x5107 | 20743 | Mppt shadow manage interval | U16 |  |  | RO | 1 | → |  |  | Unmapped
300 | Inverter Parameters | 0x510E | 20750 | Islanding detection | U16 |  |  | RO | 1 | → |  |  | Unmapped
301 | Inverter Parameters | 0x5110 | 20752 | Ground current limit | U16 |  |  | RO | 1 | → | R_CURRENT |  | Ref(62%)
302 | Inverter Parameters | 0x5112 | 20754 | Low voltage through | U16 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_HIGH |  | Ref(68%)
303 | Inverter Parameters | 0x5114 | 20756 | Reactive Power Percent | U16 |  |  | RO | 1 | → | REACTIVE_POWER_PCT |  | Ref(90%)
304 | Inverter Parameters | 0x5115 | 20757 | RS485-1 terminal resistance | U16 |  |  | RO | 1 | → |  |  | Unmapped
305 | Inverter Parameters | 0x5117 | 20759 | Insulation Resistor Detection | U16 |  |  | RO | 1 | → |  |  | Unmapped
306 | Inverter Parameters | 0x5118 | 20760 | Ground Current Detection | U16 |  |  | RO | 1 | → |  |  | Unmapped
307 | Inverter Parameters | 0x511D | 20765 | Grid high voltage load | U16 |  |  | RO | 1 | → | GRID_R_VOLTAGE |  | Ref(72%)
308 | Inverter Parameters | 0x5121 | 20769 | Reactive Power Percent | U16 |  |  | RO | 1 | → | REACTIVE_POWER_PCT |  | Ref(90%)
309 | Inverter Parameters | 0x513D | 20797 | Fuse open Check Mask | U16 |  |  | RO | 1 | → | FUSE_OPEN_DATA_LOW |  | Ref(58%)
--- DER-AVM Parameters ---
310 | DER-AVM Parameters | 0x513D | 20797 | Indicate that read or write register value is out of limit or | U16 |  |  | RO | 1 | → |  |  | Unmapped
--- Inverter Parameters ---
311 | Inverter Parameters | 0x6001 | 24577 | Inverter control | U16 |  |  | RO | 1 | → | INVERTER_CONTROL | 0x6001 | Auto
312 | Inverter Parameters | 0x6006 | 24582 | EEPROM default | U16 |  |  | RO | 1 | → | EEPROM_DEFAULT | 0x6006 | Auto
313 | Inverter Parameters | 0x6009 | 24585 | Clear the EEPROM history | U16 |  |  | RO | 1 | → | CLEAR_ENERGY_RECORD | 0x6009 | Auto
314 | Inverter Parameters | 0x600D | 24589 | I-V curve scan | U16 |  |  | RO | 1 | → | IV_CURVE_SCAN | 0x600D | Auto
--- IV Scan ---
315 | IV Scan | 0x600F | 24591 | P.F (cosφ) | U16 |  |  | RO | 1 | → | POWER_FACTOR_DYNAMIC | 0x600F | Auto
316 | IV Scan | 0x6010 | 24592 | Reactive Power Percent | U16 |  |  | RO | 1 | → | REACTIVE_POWER_DYNAMIC | 0x6010 | Auto
--- Inverter Realtime Data ---
317 | Inverter Realtime Data | 0x8000 | 32768 | Tracker 1 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER1_VOLTAGE_BASE | 0x8000 | Auto
318 | Inverter Realtime Data | 0x8040 | 32832 | String 1-1 current | U16 |  |  | RO | 1 | → | IV_STRING1_1_CURRENT_BASE | 0x8040 | Auto
319 | Inverter Realtime Data | 0x8080 | 32896 | String 1-2 current | U16 |  |  | RO | 1 | → | IV_STRING1_2_CURRENT_BASE | 0x8080 | Auto
320 | Inverter Realtime Data | 0x80C0 | 32960 | String 1-3 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
321 | Inverter Realtime Data | 0x8100 | 33024 | String 1-4 current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(91%)
322 | Inverter Realtime Data | 0x8140 | 33088 | Tracker 2 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER2_VOLTAGE_BASE | 0x8140 | Auto
323 | Inverter Realtime Data | 0x8180 | 33152 | String 2-1 current | U16 |  |  | RO | 1 | → | IV_STRING2_1_CURRENT_BASE | 0x8180 | Auto
324 | Inverter Realtime Data | 0x81C0 | 33216 | String 2-2 current | U16 |  |  | RO | 1 | → | IV_STRING2_2_CURRENT_BASE | 0x81C0 | Auto
325 | Inverter Realtime Data | 0x8200 | 33280 | String 2-3 current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(91%)
326 | Inverter Realtime Data | 0x8240 | 33344 | String 2-4 current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(91%)
327 | Inverter Realtime Data | 0x8280 | 33408 | Tracker 3 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER3_VOLTAGE_BASE | 0x8280 | Auto
328 | Inverter Realtime Data | 0x82C0 | 33472 | String 3-1 current | U16 |  |  | RO | 1 | → | IV_STRING3_1_CURRENT_BASE | 0x82C0 | Auto
329 | Inverter Realtime Data | 0x8300 | 33536 | String 3-2 current | U16 |  |  | RO | 1 | → | IV_STRING3_2_CURRENT_BASE | 0x8300 | Auto
330 | Inverter Realtime Data | 0x8340 | 33600 | String 3-3 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
331 | Inverter Realtime Data | 0x8380 | 33664 | String 3-4 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
332 | Inverter Realtime Data | 0x83C0 | 33728 | Tracker 4 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER4_VOLTAGE_BASE | 0x83C0 | Auto
333 | Inverter Realtime Data | 0x8400 | 33792 | String 4-1 current | U16 |  |  | RO | 1 | → | IV_STRING4_1_CURRENT_BASE | 0x8400 | Auto
334 | Inverter Realtime Data | 0x8440 | 33856 | String 4-2 current | U16 |  |  | RO | 1 | → | IV_STRING4_2_CURRENT_BASE | 0x8440 | Auto
335 | Inverter Realtime Data | 0x8480 | 33920 | String 4-3 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
336 | Inverter Realtime Data | 0x84C0 | 33984 | String 4-4 current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(91%)
337 | Inverter Realtime Data | 0x8500 | 34048 | Tracker 5 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER3_VOLTAGE_BASE |  | Ref(73%)
338 | Inverter Realtime Data | 0x8540 | 34112 | String 5-1 current | U16 |  |  | RO | 1 | → | STRING5_CURRENT |  | Ref(91%)
339 | Inverter Realtime Data | 0x8580 | 34176 | String 5-2 current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(91%)
340 | Inverter Realtime Data | 0x85C0 | 34240 | String 5-3 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
341 | Inverter Realtime Data | 0x8600 | 34304 | String 5-4 current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(91%)
342 | Inverter Realtime Data | 0x8640 | 34368 | Tracker 6 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER3_VOLTAGE_BASE |  | Ref(73%)
343 | Inverter Realtime Data | 0x8680 | 34432 | String 6-1 current | U16 |  |  | RO | 1 | → | STRING1_CURRENT |  | Ref(91%)
344 | Inverter Realtime Data | 0x86C0 | 34496 | String 6-2 current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(91%)
345 | Inverter Realtime Data | 0x8700 | 34560 | String 6-3 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
346 | Inverter Realtime Data | 0x8740 | 34624 | String 6-4 current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(91%)
347 | Inverter Realtime Data | 0x8780 | 34688 | Tracker 7 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER3_VOLTAGE_BASE |  | Ref(73%)
348 | Inverter Realtime Data | 0x87C0 | 34752 | String 7-1 current | U16 |  |  | RO | 1 | → | STRING1_CURRENT |  | Ref(91%)
349 | Inverter Realtime Data | 0x8800 | 34816 | String 7-2 current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(91%)
350 | Inverter Realtime Data | 0x8840 | 34880 | String 7-3 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
351 | Inverter Realtime Data | 0x8880 | 34944 | String 7-4 current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(91%)
352 | Inverter Realtime Data | 0x88C0 | 35008 | Tracker 8 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER3_VOLTAGE_BASE |  | Ref(73%)
353 | Inverter Realtime Data | 0x8900 | 35072 | String 8-1 current | U16 |  |  | RO | 1 | → | STRING1_CURRENT |  | Ref(91%)
354 | Inverter Realtime Data | 0x8940 | 35136 | String 8-2 current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(91%)
355 | Inverter Realtime Data | 0x8980 | 35200 | String 8-3 current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(91%)
356 | Inverter Realtime Data | 0x89C0 | 35264 | String 8-4 current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(91%)
357 | Inverter Realtime Data | 0x8A00 | 35328 | Tracker 9 voltage | U16 |  |  | RO | 1 | → | IV_TRACKER3_VOLTAGE_BASE |  | Ref(73%)
358 | Inverter Realtime Data | 0x8A40 | 35392 | String 9-1 current | U16 |  |  | RO | 1 | → | STRING9_CURRENT |  | Ref(91%)
359 | Inverter Realtime Data | 0x8A80 | 35456 | String 9-2 current | U16 |  |  | RO | 1 | → | STRING9_CURRENT |  | Ref(91%)
360 | Inverter Realtime Data | 0x8AC0 | 35520 | String 9-3 current | U16 |  |  | RO | 1 | → | STRING9_CURRENT |  | Ref(91%)
361 | Inverter Realtime Data | 0x8B00 | 35584 | String 9-4 current | U16 |  |  | RO | 1 | → | STRING9_CURRENT |  | Ref(91%)
362 | Inverter Realtime Data | 0xB600 | 46592 | history log 0 | U16 |  |  | RO | 1 | → |  |  | Unmapped
363 | Inverter Realtime Data | 0xB600 | 46592 | Note: | S16 | 0.01A | 0.01 | RO | 1 | → |  |  | Unmapped
364 | Inverter Realtime Data | 0xB77D | 46973 | history log 127 | U16 |  |  | RO | 1 | → |  |  | Unmapped
--- DER-AVM Parameters ---
365 | DER-AVM Parameters | 0xFFFF | 65535 |  | U16 |  |  | RO | 1 | → |  |  | Unmapped
Mode: OFFLINE ¦ Match stats: Auto/Ref=306, Unmapped=59 ¦ Edit "Solarize_Name" for Unmapped rows (red = needs review).

## Status_Mapping
Raw_Code | Raw_Name | InverterMode_State | Solarize_Code | Notes
0 | Initial mode | INITIAL | 0
1 | Standby mode | STANDBY | 1
3 | On-Grid mode | ON_GRID | 3
4 | Off-Grid mode | ON_GRID | 3
5 | Fault mode | FAULT | 5
9 | Shutdown mode | SHUTDOWN | 9
NOTE: Edit "InverterMode_State" column: INITIAL/STANDBY/ON_GRID/FAULT/SHUTDOWN

## DER_AVM_Control
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x07D0 | 2000 | DER_POWER_FACTOR_SET | S16 | FC06 | 1 |  | 0.001 | RW | Power factor setpoint [-1000,-800],[800,1000]
0x07D1 | 2001 | DER_ACTION_MODE | U16 | FC06 | 1 |  | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
0x07D2 | 2002 | DER_REACTIVE_POWER_PCT | S16 | FC06 | 1 | % | 0.1 | RW | Reactive power % [-484,484]
0x07D3 | 2003 | DER_ACTIVE_POWER_PCT | U16 | FC06 | 1 | % | 0.1 | RW | Active power % [0,1100]
0x0834 | 2100 | INVERTER_ON_OFF | U16 | FC06 | 1 |  | 1 | RW | On/Off control: 0=ON, 1=OFF
0x0835 | 2101 | CLEAR_PV_INSULATION_WARNING | U16 | FC06 | 1 |  | 1 | WO | Clear PV insulation warning: 1=Clear
0x6001 | 24577 | INVERTER_CONTROL | U16 | FC06 | 1 |  | 1 | WO | Inverter control: 0=Power on, 1=Shut down
0x600D | 24589 | IV_CURVE_SCAN | U16 | FC06 | 1 |  | 1 | RW | IV curve scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
0x600F | 24591 | POWER_FACTOR_DYNAMIC | S16 | FC06 | 1 |  | 0.001 | RW | Dynamic power factor control
0x6010 | 24592 | REACTIVE_POWER_DYNAMIC | S16 | FC06 | 1 | % | 0.01 | RW | Dynamic reactive power control (%)
0x3005 | 12293 | POWER_DERATING_PCT | U16 | FC06 | 1 | % | 1 | RW | Active power derating [0-110]%
NOTE: DER-AVM control registers (always included). Do not modify addresses.

## DEA_AVM_Monitor
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x03E8 | 1000 | DEA_L1_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L1 current (low word)
0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 current (high word)
0x03EA | 1002 | DEA_L2_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L2 current (low word)
0x03EB | 1003 | DEA_L2_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 current (high word)
0x03EC | 1004 | DEA_L3_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L3 current (low word)
0x03ED | 1005 | DEA_L3_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 current (high word)
0x03EE | 1006 | DEA_L1_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L1 voltage (low word)
0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 voltage (high word)
0x03F0 | 1008 | DEA_L2_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L2 voltage (low word)
0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 voltage (high word)
0x03F2 | 1010 | DEA_L3_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L3 voltage (low word)
0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 voltage (high word)
0x03F4 | 1012 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | FC03 | 2 | kW | 0.1 | RO | DEA total active power (low word)
0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total active power (high word)
0x03F6 | 1014 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | FC03 | 2 | Var | 1 | RO | DEA total reactive power (low word)
0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total reactive power (high word)
0x03F8 | 1016 | DEA_POWER_FACTOR_LOW | S32 | FC03 | 2 |  | 0.001 | RO | DEA power factor (low word)
0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | S32 | FC03 | 1 |  |  | RO | DEA power factor (high word)
0x03FA | 1018 | DEA_FREQUENCY_LOW | S32 | FC03 | 2 | Hz | 0.1 | RO | DEA frequency (low word)
0x03FB | 1019 | DEA_FREQUENCY_HIGH | S32 | FC03 | 1 |  |  | RO | DEA frequency (high word)
0x03FC | 1020 | DEA_STATUS_FLAG_LOW | S32 | FC03 | 2 |  | 1 | RO | DEA status flag (low word)
0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | S32 | FC03 | 1 |  |  | RO | DEA status flag (high word)
NOTE: DEA-AVM monitoring registers (always included). Do not modify addresses.