## All Registers
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
1 | Mod el | RO | STR |  |  | 0x7530 | 30000 | 15 | Nameplate name of the machine, original "model name"
2 | SN | RO | STR |  |  | 0x753F | 30015 | 10 | Device SN, which is obtained from the electronic label of the entire system.
3 | PN | RO | STR |  |  | 0x7549 | 30025 | 10 | Product Code
4 | Firm ware Versi on | RO | STR |  |  | 0x7553 | 30035 | 15 | Character string reporting: initial version VX00R00X (default VR version) VX00R00XD01, VX00R00XD02... (D0X is provided by the test and certification personnel.) Different country codes may be displayed differently.
5 | Soft ware versi on | RO | STR |  |  | 0x7562 | 30050 | 15 | In V800R021C10SPCXXX, the offering name and software version are displayed on the display page.
6 | Prot ocol versi on [Mo dbus ] | RO | U32 |  |  | 0x7574 | 30068 | 2 | high-character: main version; Upgrade on Incompatible Changes low-letter: revision; Compatible upgrade The baseline version is D8.0. 0x00080000
7 | Mod el ID | RO | U16 |  |  | 0x7576 | 30070 | 1 | Model ID. For details, see the Inverter Model Definition.xlsm.
8 | Num ber of PV strin gs | RO | U16 |  | 1 | 0x7577 | 30071 | 1
9 | Num ber of MPP Ts | RO | U16 |  | 1 | 0x7578 | 30072 | 1
10 | Rate d pow er | RO | U32 | k W | 1000 | 0x7579 | 30073 | 2 | Pn
11 | Maxi mu m activ e pow er (Pm ax) | RO | U32 | k W | 1000 | 0x757B | 30075 | 2 | Read-only interface to 42027
12 | Maxi mu m appa rent (Sm ax) | RO | U32 | kV A | 1000 | 0x757D | 30077 | 2 | Read-only interface to 42025
13 | Real - time maxi mu m react ive pow er (Qm ax, fed to the pow er grid) | RO | I32 | kV ar | 1000 | 0x757F | 30079 | 2 | Reported to the monitoring, indicating the reactive power adjustment range. Feature data is updated when the power grid standard code and derating change except for model differences.
14 | Real - time maxi mu m react ive pow er (- Qma x, abso rbed from the pow er grid) | RO | I32 | kV ar | 1000 | 0x7581 | 30081 | 2 | Reported to the monitoring, indicating the reactive power adjustment range. Feature data is updated when the power grid standard code and derating change except for model differences.
15 | Maxi mu m activ e pow er (Pm ax_r eal) | RO | U32 | k W | 1000 | 0x7583 | 30083 | 2 | The default maximum active power capacity is fixed on the nameplate of the machine, and the maximum active power capacity will not change for one machine. as a set upper limit for the reference range (42027); The relationship is as follows: 0<Pmax≤Smax≤Pmax_real≤S max_real Or the 0<Pmax≤Pmax_real≤Smax≤S max_real
16 | Maxi mu m appa rent capa bility (Sm ax_r eal) | RO | U32 | kV A | 1000 | 0x7585 | 30085 | 2 | The default apparent maximum capacity value is fixed on the machine nameplate, and one machine will not change. as a set upper limit for the reference range (42025); The relationship is as follows: 0<Pmax≤Smax≤Pmax_real≤S max_real Or the 0<Pmax≤Pmax_real≤Smax≤S max_real
17 | Prod uct sales area | RO | STR |  |  | 0x7599 | 30105 | 2 | XX: Two uppercase letters, indicating the sales area or application area of the product, mainly related to the AC power system. CN: Chinese mainland; EU: Europe; JP: Japan; US: North America (US/ Canada/and regions with the same grid or certification requirements as the US); UK: United Kingdom; Default value: CN/EU: All areas where CE certification requirements are applicable. Huawei FusionSolar Smart PV Solution and Product Naming Specifications
18 | Prod uct soft ware ID | RO | U16 |  |  | 0x759B | 30107 | 1 | Unique ID of the software publishing entity. Used for processing the compatibility of the power grid standard code.
19 | Prod uct Soft ware Versi on Num ber | RO | U16 |  |  | 0x759C | 30108 | 1 | Software release entity specific release version sequence number Used to process the compatibility of the power grid standard code.
20 | Pow er Grid Stan dard Code Prot ocol Versi on | RO | U16 |  |  | 0x759D | 30109 | 1 | Protocol loading and verification is similar to CAN1.0 and CAN2.0.
21 | Uniq ue ID of the soft ware . | RO | U16 |  |  | 0x759E | 30110 | 1 | Unique ID of a software version. Upgrade packages with different IDs cannot be upgraded to each other. (Broadcast Upgrade Signature)
22 | Num ber of upgr ade pack ages | RO | U16 |  | 1 | 0x759F | 30111 | 1 | The number of upgrade packages must be sufficient because more and more devices need to be upgraded.
23 | Infor mati on abou t subp acka ge 1 | RO | U32 |  |  | 0x75A0 | 30112 | 2 | high-character: file type ID; Low character: device type ID.
24 | Subp acka ge 2 infor mati on | RO | U32 |  |  | 0x75A2 | 30114 | 2 | high-character: file type ID; Low character: device type ID.
25 | Infor mati on abou t subp acka ge 3 | RO | U32 |  |  | 0x75A4 | 30116 | 2 | high-character: file type ID; Low character: device type ID.
26 | Subp acka ge 4 infor mati on | RO | U32 |  |  | 0x75A6 | 30118 | 2 | high-character: file type ID; Low character: device type ID.
27 | Subp acka ge 5 infor mati on | RO | U32 |  |  | 0x75A8 | 30120 | 2 | high-character: file type ID; Low character: device type ID.
28 | Infor mati on abou t subp acka ge 6 | RO | U32 |  |  | 0x75AA | 30122 | 2 | high-character: file type ID; Low character: device type ID.
29 | Subp acka ge 7 infor mati on | RO | U32 |  |  | 0x75AC | 30124 | 2 | high-character: file type ID; Low character: device type ID.
30 | Subp acka ge 8 infor mati on | RO | U32 |  |  | 0x75AE | 30126 | 2 | high-character: file type ID; Low character: device type ID.
31 | Subp acka ge 9 infor mati on | RO | U32 |  |  | 0x75B0 | 30128 | 2 | high-character: file type ID; Low character: device type ID.
32 | Infor mati on abou t subp acka ge 10 | RO | U32 |  |  | 0x75B2 | 30130 | 2 | high-character: file type ID; Low character: device type ID.
33 | [Thir d- part y label ing] SN | RO | STR |  |  | 0x75EF | 30191 | 10 | Serial number of third-party OEM equipment, customized by third-party manufacturers
34 | [Thir d- part y label ] Man ufact urer mod el | RO | U16 |  |  | 0x75F9 | 30201 | 1 | Model of third-party OEM equipment manufacturer
35 | Subd evice Supp ort ID | RO | Bitfield32 |  |  | 0x75FF | 30207 | 2
36 | Subd evice pres ence flag. | RO | Bitfield32 |  |  | 0x7601 | 30209 | 2
37 | Num ber of uniq ue sout hbou nd soft ware IDs | RO | U16 |  | 1 | 0x7724 | 30500 | 1 | Total number of southbound components that have independent upgrade packages. Note: This flag corresponds to the EquipChrtCode in the upgrade package. For details, see the Inverter Key Signal Extended Description-Monitoring Model Mapping.
38 | Uniq ue ID 1 of the sout hbou nd soft ware . | RO | U16 |  |  | 0x7725 | 30501 | 1
39 | Uniq ue ID 2 of the sout hbou nd soft ware | RO | U16 |  |  | 0x7726 | 30502 | 1
40 | Num ber of upgr ade pack ages for sout hbou nd devic e 1 | RO | U16 |  | 1 | 0x772A | 30506 | 1
41 | Infor mati on abou t subp acka ge 1 of sout hbou nd devic e 1 | RO | U32 |  |  | 0x772B | 30507 | 2 | high-character: file type ID; Low character: device type ID.
42 | Infor mati on abou t subp acka ge 2 of sout hbou nd devic e 1 | RO | U32 |  |  | 0x772D | 30509 | 2 | high-character: file type ID; Low character: device type ID.
43 | Infor mati on abou t subp acka ge 3 of sout hbou nd devic e 1 | RO | U32 |  |  | 0x772F | 30511 | 2 | high-character: file type ID; Low character: device type ID.
44 | Num ber of upgr ade pack ages for sout hbou nd devic e 2 | RO | U16 |  | 1 | 0x7735 | 30517 | 1
45 | Infor mati on abou t subp acka ge 1 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x7736 | 30518 | 2 | high-character: file type ID; Low character: device type ID.
46 | Infor mati on abou t subp acka ge 2 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x7738 | 30520 | 2 | high-character: file type ID; Low character: device type ID.
47 | Infor mati on abou t subp acka ge 3 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x773A | 30522 | 2 | high-character: file type ID; Low character: device type ID.
48 | Infor mati on abou t subp acka ge 4 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x773C | 30524 | 2 | high-character: file type ID; Low character: device type ID.
49 | Offe ring nam e of sout hbou nd devic e 1 | RO | STR |  |  | 0x7761 | 30561 | 15 | Distributed inverter southbound device identification: Southbound device 1: optimizer
50 | Offe ring nam e of sout hbou nd devic e 2 | RO | STR |  |  | 0x7770 | 30576 | 15 | Distributed inverter southbound device identification: Southbound device 2: DC- MBUS
51 | Offe ring nam e of sout hbou nd devic e 3. | RO | STR |  |  | 0x777F | 30591 | 15 | Distributed inverter southbound device identification: Southbound device 3: LUNA2000 1.0
52 | Hard ware versi on | RO | STR |  | 1 | 0x7918 | 31000 | 15
53 | Mon itori ng Boar d SN | RO | STR |  |  | 0x7927 | 31015 | 10 | From the electronic label of the monitoring board
54 | Mon itori ng soft ware versi on | RO | STR |  |  | 0x7931 | 31025 | 15 | MCU1 version
55 | Main DSP versi on | RO | STR |  |  | 0x7940 | 31040 | 15 | MCU2 version
56 | CPL D versi on num ber | RO | STR |  |  | 0x795E | 31070 | 15 | MCU4 version
57 | AFCI versi on num ber | RO | STR |  |  | 0x796D | 31085 | 15 | MCU5 version
58 | DC- MBU S versi on num ber | RO | STR |  |  | 0x798B | 31115 | 15 | MCU7 version
59 | Regi strati on code | RO | STR |  | 1 | 0x79E0 | 31200 | 10
60 | [Re mot e com mun icati on] Singl e- node rem ote com mun icati on | RO | Bitfield16 |  |  | 0x7D00 | 32000 | 1 | Reported by IEC104, which indicates the merged PCS running status.
61 | [Re mot e sign al] Run ning statu s (mo nitor ing) | RO | Bitfield16 |  |  | 0x7D02 | 32002 | 1
62 | [Re mot e sign al] Run ning statu s (po wer proc essin g) | RO | Bitfield32 |  | 1 | 0x7D03 | 32003 | 2
63 | [Re mot e sign al] Alar m 1 | RO | Bitfield16 |  |  | 0x7D08 | 32008 | 1 | For details, see the Alarm Mapping sheet.
64 | [Re mot e sign al] Alar m 2 | RO | Bitfield16 |  |  | 0x7D09 | 32009 | 1 | For details, see the Alarm Mapping sheet.
65 | [Re mot e sign al] Alar m 3 | RO | Bitfield16 |  |  | 0x7D0A | 32010 | 1 | For details, see the Alarm Mapping sheet.
66 | [Re mot e sign al] Alar m 4 | RO | Bitfield16 |  |  | 0x7D0B | 32011 | 1 | For details, see the Alarm Mapping sheet.
67 | [Re mot e sign al] Alar m 5 | RO | Bitfield16 |  |  | 0x7D0C | 32012 | 1 | For details, see the Alarm Mapping sheet.
68 | [Re mot e sign al] Alar m 6 | RO | Bitfield16 |  |  | 0x7D0D | 32013 | 1 | For details, see the Alarm Mapping sheet.
69 | Devi ce SN feat ure code | RO | U16 |  |  | 0x7D0F | 32015 | 1 | Indicates the CRC16 value of the SN, which is the key data ID. Used to prevent incorrect energy yield from being modified due to incorrect energy yield reported by devices with the same address. The SN CRC is added to ensure that the energy yield source is correct.
70 | PV1 volta ge | RO | I16 | V | 10 | 0x7D10 | 32016 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV1 voltage. When bit 9 of the power parameter mask 14 is 1, the processing logic is as follows: When DC Input Display Mode 30205 is set to 0, the signal name is PV1 Voltage. When DC input 30205 is set to 1, the signal name is MPPT1 Voltage.
71 | PV1 curre nt | RO | I16 | A | 100 | 0x7D11 | 32017 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV1 current. When bit 9 of power parameter mask 14 is 1, the following logic is used: When DC input display mode 30205 is set to 0, the signal name is PV1 current. When DC Input Display Mode 30205 is set to 1, the signal name is MPPT1 Current.
72 | PV2 Volt age | RO | I16 | V | 10 | 0x7D12 | 32018 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV2 voltage. When bit 9 of the power parameter mask 14 is 1, the processing logic is as follows: When DC Input Display Mode 30205 is set to 0, the signal name is PV2 Voltage. When DC input 30205 is set to 1, the signal name is MPPT2 Voltage.
73 | PV2 curre nt | RO | I16 | A | 100 | 0x7D13 | 32019 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV2 current. When bit 9 of the power parameter mask 14 is 1, the following logic is used: When DC Input Display Mode 30205 is set to 0, the signal name is PV2 Current. When DC input display mode 30205 is set to 1, the signal name is MPPT2 current.
74 | PV3 Volt age | RO | I16 | V | 10 | 0x7D14 | 32020 | 1
75 | PV3 curre nt | RO | I16 | A | 100 | 0x7D15 | 32021 | 1
76 | PV4 Volt age | RO | I16 | V | 10 | 0x7D16 | 32022 | 1
77 | PV4 curre nt | RO | I16 | A | 100 | 0x7D17 | 32023 | 1
78 | PV5 volta ge | RO | I16 | V | 10 | 0x7D18 | 32024 | 1
79 | PV5 curre nt | RO | I16 | A | 100 | 0x7D19 | 32025 | 1
80 | PV6 volta ge | RO | I16 | V | 10 | 0x7D1A | 32026 | 1
81 | PV6 curre nt | RO | I16 | A | 100 | 0x7D1B | 32027 | 1
82 | PV7 Volt age | RO | I16 | V | 10 | 0x7D1C | 32028 | 1
83 | PV7 curre nt | RO | I16 | A | 100 | 0x7D1D | 32029 | 1
84 | PV8 Volt age | RO | I16 | V | 10 | 0x7D1E | 32030 | 1
85 | PV8 curre nt | RO | I16 | A | 100 | 0x7D1F | 32031 | 1
86 | DC pow er | RO | I32 | k W | 1000 | 0x7D40 | 32064 | 2
87 | Pow er grid line A and B volta ge | RO | U16 | V | 10 | 0x7D42 | 32066 | 1 | When the output mode is L/N, the signal name is Grid Voltage. When Output Mode is set to L1/L2/N or L1/L2, the signal name is UW Grid Voltage.
88 | Pow er grid B/C line volta ge | RO | U16 | V | 10 | 0x7D43 | 32067 | 1 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
89 | Pow er grid CA line volta ge | RO | U16 | V | 10 | 0x7D44 | 32068 | 1 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
90 | Pow er grid phas e A volta ge | RO | U16 | V | 10 | 0x7D45 | 32069 | 1 | This parameter is invalid when the output mode is L/N. When Output Mode is set to L1/L2/N or L1/L2, the signal name is UO Grid Voltage. Not displayed in off-grid mode
91 | Pow er grid phas e B volta ge | RO | U16 | V | 10 | 0x7D46 | 32070 | 1 | This parameter is invalid when the output mode is L/N. When Output Mode is set to L1/L2/N or L1/L2, the signal name is WO Grid Voltage. Not displayed in off-grid mode
92 | Pow er grid phas e C volta ge | RO | U16 | V | 10 | 0x7D47 | 32071 | 1 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
93 | Pow er grid phas e A curre nt | RO | I32 | A | 1000 | 0x7D48 | 32072 | 2 | When the output mode is L/N, L1/L2/N, or L1/L2, the signal name is Grid Current.
94 | Pow er grid phas e B curre nt | RO | I32 | A | 1000 | 0x7D4A | 32074 | 2 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
95 | Pow er grid phas e C curre nt | RO | I32 | A | 1000 | 0x7D4C | 32076 | 2 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
96 | Peak activ e pow er of the curre nt day | RO | I32 | k W | 1000 | 0x7D4E | 32078 | 2
97 | Activ e pow er | RO | I32 | k W | 1000 | 0x7D50 | 32080 | 2
98 | react ive pow er | RO | I32 | kV ar | 1000 | 0x7D52 | 32082 | 2
99 | Pow er facto r | RO | I16 |  | 1000 | 0x7D54 | 32084 | 1
100 | Grid freq uenc y | RO | U16 | Hz | 100 | 0x7D55 | 32085 | 1
101 | Inver ter effici ency | RO | U16 | % | 100 | 0x7D56 | 32086 | 1 | When PCS is used to generate power, it indicates the power generation efficiency. When PCS is used to absorb, it indicates the absorption efficiency.
102 | Inter nal tem pera ture | RO | I16 | °C | 10 | 0x7D57 | 32087 | 1
103 | Insul atio n impe danc e | RO | U16 | M Ω | 1000 | 0x7D58 | 32088 | 1
104 | Devi ce Stat us | RO | U16 |  |  | 0x7D59 | 32089 | 1 | 0x0000 Standby: initializing 0x0001 Standby: detecting insulation resistance 0x0002 Standby: detecting irradiation 0x0003 Standby: drid detecting 0x0100 Starting 0x0200 On-grid 0x0201 Grid connection: power limited 0x0202 Grid connection: self-derating 0x0300 Shutdown: fault 0x0301 Shutdown: command 0x0302 Shutdown: OVGR 0x0303 Shutdown: communication disconnected 0x0304 Shutdown: power limited 0x0305 Shutdown: manual startup required 0x0307 Shutdown: rapid cutoff 0x0401 Grid scheduling: cosφ-P curve 0x0402 Grid scheduling: Q- U curve 0x0403 Grid scheduling: PF- U curve 0x0404 Grid scheduling: dry contact 0x0405 Grid scheduling: Q-P curve 0x0500 Spot-check ready 0x0501 Spot-checking 0x0600 Inspecting 0X0700 AFCI self check 0X0800 I-V scanning 0xA000 Standby: no irradiation
105 | Fault Code | RO | U16 |  |  | 0x7D5A | 32090 | 1 | Fault code corresponding to the alarm with the highest priority. For details, see the Alarm Description sheet.
106 | Start -up time | RO | EpochSecond | s | 1 | 0x7D5B | 32091 | 2 | Monitoring Calculation
107 | Shut dow n time | RO | EpochSecond | s | 1 | 0x7D5D | 32093 | 2 | Monitoring Calculation
108 | Activ e pow er [fast ] | RO | I32 | k W | 1000 | 0x7D5F | 32095 | 2 | Fast reporting interface, which is not filtered and used for scheduling energy storage.
109 | Accu mula ted pow er gene ratio n | RO | U32 | k W h | 100 | 0x7D6A | 32106 | 2
110 | Total DC Inpu t Pow er | RO | U32 | k W h | 100 | 0x7D6C | 32108 | 2
111 | Stati stica l time of the curre nt ener gy yield . | RO | EpochSecond | s | 1 | 0x7D6E | 32110 | 2
112 | Curr ent Hour Elect ricity | RO | U32 | k W h | 100 | 0x7D70 | 32112 | 2
113 | Curr ent- day pow er gene ratio n | RO | U32 | k W h | 100 | 0x7D72 | 32114 | 2
114 | Elect ricity gene rate d in the curre nt mon th | RO | U32 | k W h | 100 | 0x7D74 | 32116 | 2
115 | Elect ricity gene rate d in the curre nt year | RO | U32 | k W h | 100 | 0x7D76 | 32118 | 2
116 | Num ber of critic al alar ms | RO | U16 |  | 1 | 0x7D97 | 32151 | 1
117 | Num ber of majo r alar ms | RO | U16 |  | 1 | 0x7D98 | 32152 | 1
118 | Num ber of Min or Alar ms | RO | U16 |  | 1 | 0x7D99 | 32153 | 1
119 | Num ber of War ning Alar ms | RO | U16 |  | 1 | 0x7D9A | 32154 | 1
120 | Alar m clear ance SN | RO | U16 |  |  | 0x7D9B | 32155 | 1 | After the alarm is cleared, the serial number increases by 1. After the alarm is reversed, the serial number starts from 1 and skips 0.
121 | Last Hour Pow er Stati stics Time | RO | EpochSecond | s | 1 | 0x7D9C | 32156 | 2 | include generate/absorbed power
122 | Elect ricity gene rate d in the previ ous hour | RO | U32 | k W h | 100 | 0x7D9E | 32158 | 2
123 | Elect ricity stati stics time of the previ ous day | RO | EpochSecond | s | 1 | 0x7DA0 | 32160 | 2 | include generate/absorbed power
124 | Elect ricity gene rate d in the previ ous day | RO | U32 | k W h | 100 | 0x7DA2 | 32162 | 2
125 | Stati stica l time of the previ ous mon th. | RO | EpochSecond | s | 1 | 0x7DA4 | 32164 | 2 | include generate/absorbed power
126 | Elect ricity gene rate d in the previ ous mon th | RO | U32 | k W h | 100 | 0x7DA6 | 32166 | 2
127 | Elect ricity stati stics time of the previ ous year | RO | EpochSecond | s | 1 | 0x7DA8 | 32168 | 2 | include generate/absorbed power
128 | Elect ricity gene rate d in the previ ous year | RO | U32 | k W h | 100 | 0x7DAA | 32170 | 2
129 | Seria l num ber of the lates t activ e alar m. | RO | U32 |  |  | 0x7DAC | 32172 | 2 | When a new active alarm is generated, the serial number increases by 1.
130 | Late st Hist orica l Alar m Seria l Num ber | RO | U32 |  |  | 0x7DAE | 32174 | 2 | When an active alarm is transferred to the historical alarm, the serial number of the historical alarm is the same as the serial number of the last active alarm transferred to the historical alarm.
131 | Total bus volta ge | RO | I16 | V | 10 | 0x7DB0 | 32176 | 1 | Data reported by PID, used in single-level scenarios
132 | Maxi mu m PV volta ge | RO | I16 | V | 10 | 0x7DB1 | 32177 | 1 | Data reported by PID, used in single-level scenarios
133 | Mini mu m PV volta ge | RO | I16 | V | 10 | 0x7DB2 | 32178 | 1 | Data reported by PID, used in single-level scenarios
134 | Aver age PV nega tive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DB3 | 32179 | 1 | Data reported by PID, used in single-level scenarios
135 | Maxi mu m PV posit ive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DB4 | 32180 | 1 | Data reported by PID, used in single-level scenarios
136 | Mini mu m PV nega tive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DB5 | 32181 | 1 | Data reported by PID, used in single-level scenarios
137 | Inver ter- to- PE with stan d volta ge | RO | U16 | V | 1 | 0x7DB6 | 32182 | 1 | Data reported by PID, used in single-level scenarios To be compatible with PID 2.0, the PCS reports 1502. 0:100 V or 1100 V inverter; 1500: HAV1 inverter; 1502: HAV2 inverter;
138 | ISO feat ure infor mati on | RO | Bitfield16 |  | 1 | 0x7DB7 | 32183 | 1 | Data reported by PID, used in single-level scenarios
139 | Built -in PID runn ing statu s | RO | E16 |  |  | 0x7DBE | 32190 | 1
140 | PV nega tive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DBF | 32191 | 1
141 | Dire ction of the built -in PID com pens atio n | RO | E16 |  |  | 0x7DC0 | 32192 | 1
142 | Total DC ener gy yield of MPP T1 | RO | U32 | k W h | 100 | 0x7DD4 | 32212 | 2 | TD Tech NMS GUI Display [5/4]
143 | Total DC ener gy yield of MPP T2 | RO | U32 | k W h | 100 | 0x7DD6 | 32214 | 2 | TD Tech NMS GUI Display [5/4]
144 | MPP T3 DC Total Ener gy Yield | RO | U32 | k W h | 100 | 0x7DD8 | 32216 | 2 | TD Tech NMS GUI Display [5/4]
145 | MPP T4 DC Accu mula ted Ener gy Yield | RO | U32 | k W h | 100 | 0x7DDA | 32218 | 2 | TD Tech NMS GUI Display [5/4]
146 | Mon itori ng alar m 1 | RO | Bitfield16 |  |  | 0x7DFC | 32252 | 1 | GroupID:0xFF00
147 | Mon itori ng alar m 2 | RO | Bitfield16 |  |  | 0x7DFD | 32253 | 1 | GroupID:0xFF01
148 | Mon itor alar m 3 | RO | Bitfield16 |  |  | 0x7DFE | 32254 | 1 | GroupID:0xFF02
149 | [Exte rnal] Pow er alar m 1 | RO | Bitfield16 |  |  | 0x7DFF | 32255 | 1 | GroupID:0x0000
150 | [Exte rnal] Pow er alar m 2 | RO | Bitfield16 |  |  | 0x7E00 | 32256 | 1 | GroupID:0x0001
151 | [Exte rnal] Pow er alar m 3 | RO | Bitfield16 |  |  | 0x7E01 | 32257 | 1 | GroupID:0x0002
152 | [Exte rnal] Pow er alar m 4 | RO | Bitfield16 |  |  | 0x7E02 | 32258 | 1 | GroupID:0x0003
153 | [Exte rnal] Pow er alar m 5 | RO | Bitfield16 |  |  | 0x7E03 | 32259 | 1 | GroupID:0x0004
154 | [Exte rnal] Pow er alar m 6 | RO | Bitfield16 |  |  | 0x7E04 | 32260 | 1 | GroupID:0x0005
155 | [Exte rnal] Pow er alar m 7 | RO | Bitfield16 |  |  | 0x7E05 | 32261 | 1 | GroupID:0x0006
156 | [Exte rnal] Pow er alar m 8 | RO | Bitfield16 |  |  | 0x7E06 | 32262 | 1 | GroupID:0x0007
157 | [Exte rnal] Pow er alar m 9 | RO | Bitfield16 |  |  | 0x7E07 | 32263 | 1 | GroupID:0x0008
158 | [Exte rnal] Pow er alar m 10 | RO | Bitfield16 |  |  | 0x7E08 | 32264 | 1 | GroupID:0x0009
159 | [Exte rnal] Pow er alar m 11 | RO | Bitfield16 |  |  | 0x7E09 | 32265 | 1 | GroupID:0x000A
160 | [Exte rnal] Pow er alar m 12 | RO | Bitfield16 |  |  | 0x7E0A | 32266 | 1 | GroupID:0x000B
161 | [Exte rnal] Pow er alar m 13 | RO | Bitfield16 |  |  | 0x7E0B | 32267 | 1 | GroupID:0x000C
162 | [Exte rnal] Pow er alar m 14 | RO | Bitfield16 |  |  | 0x7E0C | 32268 | 1 | GroupID:0x000D
163 | [Exte rnal] Pow er alar m 15 | RO | Bitfield16 |  |  | 0x7E0D | 32269 | 1 | GroupID:0x000E
164 | [Exte rnal] Pow er alar m 16 | RO | Bitfield16 |  |  | 0x7E0E | 32270 | 1 | GroupID:0x000F
165 | Mon itor alar m 4 | RO | Bitfield16 |  |  | 0x7E0F | 32271 | 1 | GroupID:0xFF03
166 | Mon itor alar m 5 | RO | Bitfield16 |  |  | 0x7E10 | 32272 | 1 | GroupID:0xFF04
167 | [Exte rnal] Pow er alar m 17 | RO | Bitfield16 |  |  | 0x7E11 | 32273 | 1 | GroupID:0x0010
168 | Strin g 1 acce ss statu s | RO | E16 |  |  | 0x7E2C | 32300 | 1
169 | Strin g 2 acce ss statu s | RO | E16 |  |  | 0x7E2D | 32301 | 1
170 | Strin g 3 acce ss statu s | RO | E16 |  |  | 0x7E2E | 32302 | 1
171 | Strin g 4 acce ss statu s | RO | E16 |  |  | 0x7E2F | 32303 | 1
172 | Strin g 5 acce ss statu s | RO | E16 |  |  | 0x7E30 | 32304 | 1
173 | Con necti on statu s of strin g 6 | RO | E16 |  |  | 0x7E31 | 32305 | 1
174 | Strin g 7 acce ss statu s | RO | E16 |  |  | 0x7E32 | 32306 | 1
175 | Strin g 8 acce ss statu s | RO | E16 |  |  | 0x7E33 | 32307 | 1
176 | Sten t Syst em Stat us | RO | Bitfield32 |  |  | 0x84D0 | 34000 | 2 | BIT0–BIT15: state of support system 1–16; BIT16–BIT31: reserved for future expansion.
177 | Tilt angl e 1 sam pling | RO | I16 | ° | 100 | 0x84D2 | 34002 | 1
178 | Azim uth 1 sam pling | RO | I16 | ° | 100 | 0x84D3 | 34003 | 1
179 | Tilt angl e 2 sam pling | RO | I16 | ° | 100 | 0x84D4 | 34004 | 1
180 | Azim uth 2 sam pling | RO | I16 | ° | 100 | 0x84D5 | 34005 | 1
181 | Tilt angl e 3 sam pling | RO | I16 | ° | 100 | 0x84D6 | 34006 | 1
182 | Azim uth 3 sam pling | RO | I16 | ° | 100 | 0x84D7 | 34007 | 1
183 | Tilt angl e 4 sam pling | RO | I16 | ° | 100 | 0x84D8 | 34008 | 1
184 | Azim uth 4 sam pling | RO | I16 | ° | 100 | 0x84D9 | 34009 | 1
185 | Tilt angl e 5 sam pling | RO | I16 | ° | 100 | 0x84DA | 34010 | 1
186 | Azim uth 5 sam pling | RO | I16 | ° | 100 | 0x84DB | 34011 | 1
187 | Tilt angl e 6 sam pling | RO | I16 | ° | 100 | 0x84DC | 34012 | 1
188 | Azim uth 6 sam pling | RO | I16 | ° | 100 | 0x84DD | 34013 | 1
189 | Tilt angl e 7 sam pling | RO | I16 | ° | 100 | 0x84DE | 34014 | 1
190 | Azim uth 7 sam pling | RO | I16 | ° | 100 | 0x84DF | 34015 | 1
191 | Tilt angl e 8 sam pling | RO | I16 | ° | 100 | 0x84E0 | 34016 | 1
192 | Azim uth 8 sam pling | RO | I16 | ° | 100 | 0x84E1 | 34017 | 1
193 | Tilt angl e 9 sam pling | RO | I16 | ° | 100 | 0x84E2 | 34018 | 1
194 | Azim uth 9 sam pling | RO | I16 | ° | 100 | 0x84E3 | 34019 | 1
195 | Tilt angl e 10 sam pling | RO | I16 | ° | 100 | 0x84E4 | 34020 | 1
196 | Azim uth 10 sam pling | RO | I16 | ° | 100 | 0x84E5 | 34021 | 1
197 | Tilt angl e 11 sam pling | RO | I16 | ° | 100 | 0x84E6 | 34022 | 1
198 | Azim uth 11 sam pling | RO | I16 | ° | 100 | 0x84E7 | 34023 | 1
199 | Tilt angl e 12 sam pling | RO | I16 | ° | 100 | 0x84E8 | 34024 | 1
200 | Azim uth 12 sam pling | RO | I16 | ° | 100 | 0x84E9 | 34025 | 1
201 | Tilt angl e 13 sam pling | RO | I16 | ° | 100 | 0x84EA | 34026 | 1
202 | Beari ng 13 sam pling | RO | I16 | ° | 100 | 0x84EB | 34027 | 1
203 | Tilt angl e 14 sam pling | RO | I16 | ° | 100 | 0x84EC | 34028 | 1
204 | Azim uth 14 sam pling | RO | I16 | ° | 100 | 0x84ED | 34029 | 1
205 | Tilt angl e 15 sam pling | RO | I16 | ° | 100 | 0x84EE | 34030 | 1
206 | Beari ng angl e 15 sam pling | RO | I16 | ° | 100 | 0x84EF | 34031 | 1
207 | Tilt angl e 16 sam pling | RO | I16 | ° | 100 | 0x84F0 | 34032 | 1
208 | Beari ng 16 sam pling | RO | I16 | ° | 100 | 0x84F1 | 34033 | 1
209 | Trac king syste m cont rolle r | RO | E16 |  |  | 0x84F2 | 34034 | 1
210 | Supp ort Syst em Type | RO | E16 |  |  | 0x84F3 | 34035 | 1 | If the vendor does not support a support type, the system returns the 03 error code.
211 | Oper atin g mod e | RO | E16 |  |  | 0x84F4 | 34036 | 1
212 | Total num ber of stent s | RO | U16 |  | 1 | 0x84F5 | 34037 | 1 | For dual-axis control, the maximum number of supports is 8.
213 | Supp ort acce ss statu s | RO | Bitfield32 |  | 1 | 0x84F6 | 34038 | 2 | BIT0–BIT15: access status of support system 1–16; BIT16–BIT31: reserved for future expansion.
214 | Wor king mod e mas k | RO | Bitfield32 |  | 1 | 0x84F8 | 34040 | 2 | Each bit indicates whether a working mode is supported.
215 | Supp ort 1 Gen eral Fault Stat us | RO | E16 |  |  | 0x851B | 34075 | 1 | Data reported by the SmartLogger to the management system
216 | Supp ort 1 user- defin ed fault statu s | RO | U16 |  | 1 | 0x851C | 34076 | 1 | For details about the controller scenario definition, see the corresponding document. Data reported by the SmartLogger to the management system
217 | Supp ort 2 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x851D | 34077 | 1
218 | Supp ort 2 Cust om Fault Stat us | RO | U16 |  | 1 | 0x851E | 34078 | 1
219 | Supp ort 3 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x851F | 34079 | 1
220 | Supp ort 3 user- defin ed fault statu s | RO | U16 |  | 1 | 0x8520 | 34080 | 1
221 | Supp ort 4 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8521 | 34081 | 1
222 | Supp ort 4 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8522 | 34082 | 1
223 | Supp ort 5 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8523 | 34083 | 1
224 | Supp ort 5 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8524 | 34084 | 1
225 | Supp ort 6 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8525 | 34085 | 1
226 | Supp ort 6 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8526 | 34086 | 1
227 | Supp ort 7 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8527 | 34087 | 1
228 | Supp ort 7 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8528 | 34088 | 1
229 | Supp ort 8 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8529 | 34089 | 1
230 | Supp ort 8 Cust om Fault Stat us | RO | U16 |  | 1 | 0x852A | 34090 | 1
231 | Supp ort 9 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x852B | 34091 | 1
232 | Supp ort 9 Cust om Fault Stat us | RO | U16 |  | 1 | 0x852C | 34092 | 1
233 | Supp ort 10 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x852D | 34093 | 1
234 | Supp ort 10 Cust om Fault Stat us | RO | U16 |  | 1 | 0x852E | 34094 | 1
235 | Supp ort 11 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x852F | 34095 | 1
236 | Supp ort 11 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8530 | 34096 | 1
237 | Supp ort 12 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8531 | 34097 | 1
238 | Supp ort 12 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8532 | 34098 | 1
239 | Supp ort 13 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8533 | 34099 | 1
240 | Supp ort 13 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8534 | 34100 | 1
241 | Supp ort 14 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8535 | 34101 | 1
242 | Supp ort 14 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8536 | 34102 | 1
243 | Supp ort 15 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8537 | 34103 | 1
244 | Supp ort 15 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8538 | 34104 | 1
245 | Supp ort 16 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8539 | 34105 | 1
246 | Supp ort 16 Cust om Fault Stat us | RO | U16 |  | 1 | 0x853A | 34106 | 1
247 | Run ning time of capa citor bank | RO | U32 | ho ur | 10 | 0x88B8 | 35000 | 2 | Used to inspect data.
248 | Inter nal fan 1 runn ing time | RO | U32 | ho ur | 10 | 0x88BA | 35002 | 2 | Used to inspect data.
249 | Inter nal alar m | RO | U16 | V | 1 | 0x88C2 | 35010 | 1 | Used for R&D data storage.
250 | Inter nal Tem pera ture 1 | RO | I16 | °C | 10 | 0x88CD | 35021 | 1 | Temperature of INV module A Used for R&D 5-minute data recording.
251 | Inter nal Tem pera ture 2 | RO | I16 | °C | 10 | 0x88CE | 35022 | 1 | Temperature of INV module B Used for R&D 5-minute data recording.
252 | Inter nal Tem pera ture 3 | RO | I16 | °C | 10 | 0x88CF | 35023 | 1 | INV module C temperature Used for R&D 5-minute data recording.
253 | Inter nal Tem pera ture 4 | RO | I16 | °C | 10 | 0x88D0 | 35024 | 1 | Temperature sampling of anti-reverse module 1 Used for R&D 5-minute data recording.
254 | Inter nal Tem pera ture 5 | RO | I16 | °C | 10 | 0x88D1 | 35025 | 1 | Output board relay, ambient temperature - maximum temperature Used for R&D 5-minute data recording.
255 | Inter nal Tem pera ture 6 | RO | I16 | °C | 10 | 0x88D2 | 35026 | 1 | Output board, power board input, and power board inverter temperature sampling - maximum temperature Used for R&D 5-minute data recording.
256 | Inter nal tem pera ture 7 | RO | I16 | °C | 10 | 0x88D3 | 35027 | 1 | Temperature sampling of anti-reverse module 2 Used for R&D 5-minute data recording.
257 | Inter nal tem pera ture 8 | RO | I16 | °C | 10 | 0x88D4 | 35028 | 1 | DC terminal temperature 1 / 2 - maximum temperature Used for R&D 5-minute data recording.
258 | Inter nal tem pera ture 9 | RO | I16 | °C | 10 | 0x88D5 | 35029 | 1 | AC Terminal Temperature 1 / 2 / 3 - Maximum Temperature Used for R&D 5-minute data recording.
259 | Inter nal tem pera ture 10 | RO | I16 | °C | 10 | 0x88D6 | 35030 | 1 | Used for R&D data storage.
260 | Inter nal tem pera ture 11 | RO | I16 | °C | 10 | 0x88D7 | 35031 | 1 | Used for R&D data storage.
261 | Inter nal tem pera ture 12 | RO | I16 | °C | 10 | 0x88D8 | 35032 | 1 | Used for R&D data storage.
262 | Phas e A DC com pone nt DCI | RO | I16 | A | 1000 | 0x88DE | 35038 | 1 | Used for R&D 5-minute data recording.
263 | Phas e B DC com pone nt DCI | RO | I16 | A | 1000 | 0x88DF | 35039 | 1 | Used for R&D 5-minute data recording.
264 | Phas e C DC com pone nt DCI | RO | I16 | A | 1000 | 0x88E0 | 35040 | 1 | Used for R&D 5-minute data recording.
265 | Leak age curre nt RCD | RO | I16 | m A | 1 | 0x88E1 | 35041 | 1 | Used for R&D 5-minute data recording.
266 | Posit ive bus volta ge | RO | I16 | V | 10 | 0x88E2 | 35042 | 1 | Used for R&D 5-minute data recording.
267 | Neg ative bus volta ge | RO | I16 | V | 10 | 0x88E3 | 35043 | 1 | Used for R&D 5-minute data recording.
268 | BUS nega tive volta ge to grou nd | RO | I16 | V | 10 | 0x88E4 | 35044 | 1 | Used for R&D 5-minute data recording.
269 | I-V scan statu s | RO | E16 |  |  | 0x8916 | 35094 | 1
270 | I-V scan ning capa bility | RO | E16 |  |  | 0x8917 | 35095 | 1
271 | [Ma nage men t Syst em] NMS IP addr ess | RO | U32 |  | 1 | 0x891E | 35102 | 2 | Indicates whether the NMS is successfully connected. After the NMS is connected, fill in the NMS IP address. If there is no access, the value is 0XFFFFFFFF. The customer interface is called NA.
272 | [STA ] Wire less Rout ing Acce ss Sign al Stre ngth | RO | E16 |  |  | 0x8920 | 35104 | 1 | The FE status enumeration is used by the mobile app to effectively identify the current network conditions, switch icons, and provide effective prompts.
273 | [STA ] WLA N list scan ning statu s | RO | E16 |  |  | 0x8921 | 35105 | 1
274 | Wifi- Mac | RO | MLD |  | 1 | 0x8922 | 35106 | 3
275 | [NTP ] Last NTP sync hron izati on statu s. | RO | U16 |  | 1 | 0x8928 | 35112 | 1 | 0: normal 1: abnormal
276 | [NTP ] NTP Last Sync hron izati on Time | RO | U32 |  | 1 | 0x8929 | 35113 | 2 | Epoch Second
277 | Defe rred activ atio n state | RO | E16 |  |  | 0x892B | 35115 | 1
278 | [4G] Mon thly used traffi c | RO | U32 | M B | 100 | 0x892C | 35116 | 2
279 | [4G] Mon thly Rem ainin g Traff ic | RO | U32 | M B | 100 | 0x892E | 35118 | 2
280 | [4G] Aver age daily traffi c usag e | RO | U32 | M B | 100 | 0x8930 | 35120 | 2
281 | [4G] Traff ic statu s | RO | E16 |  |  | 0x8932 | 35122 | 1
282 | [STA ] Rout er conn ectio n time | RO | U16 | s | 1 | 0x8934 | 35124 | 1 | This parameter indicates the performance indicators for connecting the inverter or dongle to the router, and the duration for connecting the inverter or dongle to the router after the SSID and password are configured on the user interface. The maximum value given here.
283 | [STA ] Rout er conn ectio n statu s | RO | E16 |  |  | 0x8935 | 35125 | 1 | Note: 3: Connection failure indicates that the route can be discovered normally and the password is correct but the result fails. 0: Not connected indicates that the required information about the SSID and password is not configured.
284 | [FE] Con necti on statu s | RO | U16 |  | 1 | 0x8936 | 35126 | 1 | 0: not connected 1: being connected 2: successful connection 3: connection failure
285 | [Sm art I- V-V- Diag nosis ] Auth oriza tion Func tion | RO | Bitfield32 |  | 1 | 0x8940 | 35136 | 2 | 2019-02-19 SEG of the Monitoring Development Dept: The original LicC does not support the scenario where different features have different expiration dates. The license features are not supported by different models. Added the mechanism support. The original API is degenerated to support only the IV feature. For subsequent features, two interfaces (status and expiration time) are extended for each additional feature.
286 | Sma rt I- V-V- Diag nosis (Lice nse) Stat us | RO | E16 |  |  | 0x8942 | 35138 | 1
287 | [Sm art I- V-V- Diag nosis ] Lice nse expir atio n date | RO | EpochSecond | s | 1 | 0x8943 | 35139 | 2 | Epoch second 0XF2A52380 (2099-1-1) is reported, indicating that the setting takes effect permanently. If there is no license, 0 or 0XFFFFFFFF is reported and NA is displayed on the GUI.
288 | Lice nse loadi ng time | RO | EpochSecond | s | 1 | 0x8945 | 35141 | 2 | Epoch Second
289 | Lice nse Dere gistr atio n Time | RO | EpochSecond | s | 1 | 0x8947 | 35143 | 2 | Epoch second 0XFFFFFFFF is reported when the status is not deregistered.
290 | Lice nse SN | RO | STR |  | 1 | 0x8949 | 35145 | 10
291 | Inval idati on code . | RO | STR |  | 1 | 0x8953 | 35155 | 64
292 | Auth oriza tion Feat ure Sign atur e | RO | E16 |  |  | 0x8993 | 35219 | 2 | 1. If bit is set to 1, the function is licensed. 2. If the bit is cleared, the function does not need to be licensed on the current model. Used to support differentiated management and control policies for models.
293 | [Stri ng moni torin g] Lice nse statu s | RO | E16 |  |  | 0x8995 | 35221 | 1 | 0: no license; 1: normal; 2: grace period; 3: deregistered; 4: The SN does not match. 5: expired;
294 | [Stri ng Mon itori ng] Lice nse Expir atio n Time | RO | EpochSecond | s | 1 | 0x8996 | 35222 | 2 | Epoch Second If the feature status is normal, 0XF2A52380(2099-1-1) is reported, indicating that the feature takes effect permanently. If the feature status is abnormal, 0 or 0XFFFFFFFF is reported, and NA is displayed on the GUI.
295 | [4G] Mod ule statu s | RO | E16 |  |  | 0x89B1 | 35249 | 1
296 | [4G] IP addr ess | RO | U32 |  | 1 | 0x89B2 | 35250 | 2
297 | [4G] Subn et Mas k | RO | U32 |  | 1 | 0x89B4 | 35252 | 2
298 | [4G] IMEI | RO | STR |  | 1 | 0x89B6 | 35254 | 10
299 | [4G] sign al stren gth | RO | U16 |  | 1 | 0x89C0 | 35264 | 1 | 0 = No signal
300 | [4G] PIN num ber inpu t time s | RO | U16 |  | 1 | 0x89C1 | 35265 | 1
301 | [4G] PIN chec k statu s | RO | E16 |  |  | 0x89C2 | 35266 | 1
302 | Activ e pow er adju stme nt statu s | RO | MLD |  |  | 0x89E4 | 35300 | 4
303 | Reac tive pow er adju stme nt statu s | RO | MLD |  |  | 0x89E8 | 35304 | 4
304 | Upgr ade statu s ID. | RO | E16 |  |  | 0x8CC1 | 36033 | 1 | The flag is cleared each time the system is powered on. After the upgrade is successful, the flag is set to 1, indicating that the upgrade is successful and no abnormal restart occurs.
305 | [Mo dule 1] Run ning statu s of the batt ery | RO | E16 |  |  | 0x9088 | 37000 | 1
306 | Met er Stat us | RO | E16 |  |  | 0x90EC | 37100 | 1
307 | Grid volta ge (pha se A volta ge) | RO | I32 | V | 10 | 0x90ED | 37101 | 2
308 | Phas e B volta ge | RO | I32 | V | 10 | 0x90EF | 37103 | 2
309 | Phas e C volta ge | RO | I32 | V | 10 | 0x90F1 | 37105 | 2
310 | Grid curre nt (pha se A curre nt) | RO | I32 | A | 100 | 0x90F3 | 37107 | 2
311 | Phas e B curre nt | RO | I32 | A | 100 | 0x90F5 | 37109 | 2
312 | Phas e C curre nt | RO | I32 | A | 100 | 0x90F7 | 37111 | 2
313 | Activ e pow er | RO | I32 | W | 1 | 0x90F9 | 37113 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
314 | react ive pow er | RO | I32 | Va r | 1 | 0x90FB | 37115 | 2
315 | Pow er facto r | RO | I16 |  | 1000 | 0x90FD | 37117 | 1
316 | Grid freq uenc y | RO | I16 | Hz | 100 | 0x90FE | 37118 | 1
317 | Posit ive activ e pow er | RO | I32 | k W h | 100 | 0x90FF | 37119 | 2 | Inverter power fed to the grid
318 | Reve rse activ e pow er | RO | I32 | k W h | 100 | 0x9101 | 37121 | 2 | Electricity absorbed by the distributed system from the grid
319 | Accu mula ted react ive pow er | RO | I32 | kV ar h | 100 | 0x9103 | 37123 | 2
320 | Met er Type | RO | E16 |  |  | 0x9105 | 37125 | 1
321 | A-B line volta ge | RO | I32 | V | 10 | 0x9106 | 37126 | 2
322 | BC line volta ge | RO | I32 | V | 10 | 0x9108 | 37128 | 2
323 | CA line volta ge | RO | I32 | V | 10 | 0x910A | 37130 | 2
324 | Phas e A activ e pow er | RO | I32 | W | 1 | 0x910C | 37132 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
325 | Phas e B activ e pow er | RO | I32 | W | 1 | 0x910E | 37134 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
326 | Phas e C activ e pow er | RO | I32 | W | 1 | 0x9110 | 37136 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
327 | Met er Mod el Chec k Resu lt | RO | E16 |  |  | 0x9112 | 37138 | 1
328 | Total num ber of opti mize rs | RO | U16 |  | 1 | 0x9150 | 37200 | 1
329 | Num ber of onlin e opti mize rs | RO | U16 |  | 1 | 0x9151 | 37201 | 1
330 | Feat ure data sequ ence num ber | RO | U16 |  | 1 | 0x9152 | 37202 | 1
331 | Phys ical Loca tion Loca ting Prog ress | RO | E16 |  |  | 0x9153 | 37203 | 1
332 | Log expo rt prog ress | RO | E16 |  |  | 0x9154 | 37204 | 1
333 | Real - time data quer y prog ress | RO | E16 |  |  | 0x9155 | 37205 | 1
334 | Curr ent statu s of the phys ical locat ion | RO | E16 |  |  | 0x9156 | 37206 | 1
335 | Num ber of Sear ched Opti mize rs | RO | U16 |  | 1 | 0x9157 | 37207 | 1
336 | Rela tive Posit ionin g Stat us | RO | E16 |  |  | 0x9158 | 37208 | 1 | The previous result needs to be solidified and retained after a power failure.
337 | Layo ut File Stor age Prog ress | RO | U16 | % | 1 | 0x9159 | 37209 | 1 | 0xffff: indicates that saving the data fails.
338 | Layo ut File Cha nge SN | RO | U16 |  | 1 | 0x915A | 37210 | 1
339 | Disc onne ction dete ction prog ress | RO | U16 | % | 1 | 0x915B | 37211 | 1 | Other values are error codes. Error code definitions are as follows: 0xfe02: Off-grid running, operation forbidden 0xfe03: The equipment test is being performed and the operation is forbidden. 0xfe04: The optimizer is searching. Please try again later. 0xfe05: The optimizer is identifying a long PV string. Try again later. 0xfe07: Exporting optimizer logs is in progress. Please try again later. 0xfe08: The fast shutdown is triggered and the operation is disabled. 0xfe09: No illumination at night or all optimizers are offline. 0xfff0: No optimizer is configured or the optimizer is configured. The operation is disabled. 0xfff1: The illumination is weak. If the illumination is normal, perform the disconnection detection function again. 0xfff2: The output voltage of the optimizer is abnormal. Perform the disconnection locating function again.
340 | Disc onne cted statu s | RO | E16 |  |  | 0x915C | 37212 | 1
341 | [DC- MBU S] Net work ing statu s | RO | E16 |  |  | 0x9182 | 37250 | 1
342 | Num ber of Net work ed Net work s | RO | U16 |  |  | 0x9183 | 37251 | 1
343 | Num ber of neig hbor ing netw orks | RO | U16 |  |  | 0x9184 | 37252 | 1
344 | Fast Shut dow n Self Test Stat us | RO | E16 |  |  | 0x9185 | 37253 | 1 | 0: not executed, indicating that the system life cycle has never been executed. The previous result needs to be solidified and retained after a power failure.
345 | Run ning statu s | RO | E16 |  |  | 0x9186 | 37254 | 1
346 | SN | RO | STR |  |  | 0x9187 | 37255 | 10
347 | SN | RO | STR |  | 1 | 0x9218 | 37400 | 10
348 | Type | RO | E16 |  |  | 0x9222 | 37410 | 1
349 | Maxi mu m num ber of conn ecte d devic es | RO | U16 |  | 1 | 0x9235 | 37429 | 1
350 | RAT | RO | STR |  | 1 | 0x9236 | 37430 | 10
351 | Carri ers | RO | STR |  | 1 | 0x9240 | 37440 | 15 | The default value is reported when no query is found.
352 | Total rate d capa city of grid- tied inver ters | RO | U32 | k W | 1000 | 0x925E | 37470 | 2 | Difference from plant capacity: refers only to the total capacity of online grid- tied inverters.
353 | Conv ersio n facto r | RO | U32 |  | 1000 | 0x9260 | 37472 | 2 | Percentage of current control/percentage of control delivered by the electric power company
354 | Curr ent Perc enta ge | RO | U16 | % | 10 | 0x9262 | 37474 | 1
355 | [Sch edul e serv er] Com mun icati on statu s | RO | E16 |  |  | 0x9263 | 37475 | 1 | Dongle and Japan Electric Power Huawei server communication status (only for third-party NMSs in Japan): Dispatching server: intelligence distribution, intelligence distribution, intelligence distribution, and information distribution
356 | [Sch edul e serv er] Late st conn ectio n statu s | RO | E16 |  |  | 0x9264 | 37476 | 1
357 | [Sch edul e serv er] Late st conn ectio n time | RO | U32 |  |  | 0x9265 | 37477 | 2
358 | Soft ware versi on | RO | STR |  |  | 0x9267 | 37479 | 15 | Dongle firmware version
359 | Num ber of conn ecte d devic es | RO | U16 |  |  | 0x9276 | 37494 | 1
360 | Silen ce flag | RO | E16 |  |  | 0x9278 | 37496 | 1 | Note: This API is used only to synchronize dongle silence between the mobile app and inverter. Wait for the dongle to exit bus control in silence. Only the mobile phone app can initiate a request to the slave UPS in parallel mode.
361 | Upgr ade Stat us | RO | E16 |  |  | 0x9279 | 37497 | 1
362 | Inver ter com preh ensiv e statu s | RO | Bitfield16 |  |  | 0x928E | 37518 | 1
363 | Inver ter integ rate d statu s supp ort flag | RO | U16 |  | 1 | 0x928F | 37519 | 1
364 | Syst em time (loca l time ) | RW | EpochSecond | s | 1 | 0x9C40 | 40000 | 2 | The data is in the epoch second format, that is, the local time.
365 | Q-U char acter istic curv e mod e | RW | E16 |  |  | 0x9C65 | 40037 | 1
366 | Q-U Sche dulin g Trigg er Pow er Perc enta ge | RW | I16 | % | 1 | 0x9C66 | 40038 | 1
367 | Activ e pow er is dera ted by a fixed valu e. | RW | U16 | k W | 10 | 0x9CB8 | 40120 | 1
368 | Pow er facto r | RW | I16 |  | 1000 | 0x9CBA | 40122 | 1
369 | Reac tive pow er com pens atio n (Q/S ) [low preci sion] | RW | I16 |  | 1000 | 0x9CBB | 40123 | 1 | The equipment end converts the value into a fixed Q value for reactive power control. S is Smax.
370 | Reac tive pow er adju stme nt time | RW | U16 | s | 1 | 0x9CBC | 40124 | 1 | Change requirement: The "Reactive power adjustment time" broadcast interface is added to the Q-P characteristic curve and cosphi-P characteristic curve delivery interface, which is the same as the Q-U characteristic curve 20190918.
371 | Activ e pow er perc enta ge dera ting (low preci sion) | RW | I16 | % | 10 | 0x9CBD | 40125 | 1 | Active power fine adjustment interface
372 | Activ e pow er is dera ted by a fixed valu e. | RW | U32 | W | 1 | 0x9CBE | 40126 | 2 | Value range: [0, Pmax]
373 | Nigh t react ive pow er com pens atio n (Q/S ) | RW | I16 |  | 1000 | 0x9CC0 | 40128 | 1 | The equipment end converts the value into a fixed Q value for reactive power control. S is Smax.
374 | Fixe d valu e of react ive pow er at nigh t | RW | I32 | kV ar | 1000 | 0x9CC1 | 40129 | 2
375 | Cos? - P/Pn char acter istic curv e | RW | MLD |  |  | 0x9CC5 | 40133 | 21
376 | Q-U char acter istic curv e | RW | MLD |  |  | 0x9CDA | 40154 | 21
377 | PF-U char acter istic curv e | RW | MLD |  |  | 0x9CEF | 40175 | 21
378 | [Cha racte ristic curv e] Reac tive pow er adju stme nt time | RW | U16 | s | 1 | 0x9D04 | 40196 | 1 | Change requirement: The "Reactive power adjustment time" broadcast interface is added to the Q-P characteristic curve and cosphi-P characteristic curve delivery interface, which is the same as the Q-U characteristic curve 20190918.
379 | Q-U Sche dulin g Exit Pow er Perc enta ge | RW | I16 | % | 1 | 0x9D06 | 40198 | 1
380 | Activ e pow er perc enta ge cont rol [low preci sion] | RW | I16 | % | 10 | 0x9D07 | 40199 | 1 | This interface is used in distributed mode. It is used to control the active power percentage. It is issued to the power software in the anti-backflow control, and controls the upper limit of the output active power when the power is increased due to underfrequency.
381 | Start the syste m. | WO | E16 |  |  | 0x9D08 | 40200 | 1
382 | Shut dow n. | WO | E16 |  |  | 0x9D09 | 40201 | 1
383 | Quic k pow er- on and pow er- off | WO | E16 |  |  | 0x9D0A | 40202 | 1 | Not affected by shutdown gradient
384 | reset | WO | E16 |  |  | 0x9D0D | 40205 | 1 | After receiving the command, the DSP responds immediately and then resets. After receiving the command, the inverter monitoring module sends the command to the DSP. After receiving a normal response, the inverter monitoring module sends the command to the northbound port. After 3s, the system is reset. Otherwise, the system does not restart.
385 | Insul atio n impe danc e diag nosis | WO | U16 |  | 1 | 0x9D0E | 40206 | 1 | [0, 1], 1 action After receiving the instruction, the inverter restarts and performs insulation impedance detection.
386 | Dry Cont act Sche dulin g Setti ngs | RW | MLD |  | 1 | 0x9D6C | 40300 | 33
387 | Q-P char acter istic curv e | RW | MLD |  |  | 0x9DA2 | 40354 | 21
388 | Q-U char acter istic curv e mini mu m PF limit | RW | U16 |  | 1000 | 0x9DB7 | 40375 | 1 | This MPI is used to limit the reactive power output by the QU curve by limiting the current PF value. The country code that is not required by this function is set to 0 by default, indicating that the reactive power output is not limited. The country code in EN50549 can be set to 0 to 1, and the default value is 0.9.
389 | Q-U char acter istic curv e valid ity dela y time | RW | U16 | s | 1 | 0x9DB8 | 40376 | 1 | After the QU curve reaches the trigger voltage, the reactive power starts to change after a period of time is delayed. Italy CEI0-16/21 requires that the default value be 3s, indicating that the QU curve takes effect after the triggering delay is 3s, which can be set on the GUI. For other countries, the default value is 0.
390 | Syst em Time (UTC ) | WO | EpochSecond | s | 1 | 0x9E34 | 40500 | 2 | The data is in the UTC time format.
391 | Pow er grid stan dard code | RW | U16 |  | 1 | 0xA410 | 42000 | 1 | CHINA_MV800 For details about the scope, see the Power Grid Standard Code.
392 | Outp ut mod e | RW | E16 |  |  | 0xA411 | 42001 | 1 | On the customer interface, only read signals can be displayed. Currently, only three-phase three-wire signals are supported. No configuration is required. In the future, the interface changes will be used to notify each interface.
393 | Volt age level | RW | U16 | V | 1 | 0xA412 | 42002 | 1 | Vn
394 | Freq uenc y Class | RW | U16 | Hz | 1 | 0xA413 | 42003 | 1 | Fn
395 | Repl ace the targ et mod el. | RW | U16 |  | 1 | 0xA41C | 42012 | 1 | Enumerated ID of the inverter model. For details, see the Inverter Model Definition. The default value is 65535 (0xFFFF). If the ID is invalid, the replacement requirement is not set.
396 | Rem ote pow er sche dulin g | RW | E16 |  |  | 0xA41E | 42014 | 1 | 0：Disable 1：Enable If this parameter is disabled, the inverter will be locked.
397 | react ive pow er gradi ent | RW | U32 | %/ s | 1000 | 0xA41F | 42015 | 2
398 | Activ e pow er chan ge gradi ent | RW | U32 | %/ s | 1000 | 0xA421 | 42017 | 2 | Limits the speed at which the power changes caused by the power scheduling command
399 | Sche dule d instr uctio n hold time | RW | U32 | s | 1 | 0xA423 | 42019 | 2 | Permanently valid when the value is 0.
400 | Maxi mu m appa rent pow er | RW | U32 | kV A | 1000 | 0xA425 | 42021 | 2 | ["Maximum active power",Smax]
401 | Maxi mu m activ e pow er | RW | U32 | k W | 1000 | 0xA427 | 42023 | 2 | [0.1,Pmax]
402 | appa rent pow er refer ence | RW | U32 | kV ar | 1000 | 0xA429 | 42025 | 2 | Sn: upper limit of the maximum active power (PMax), which is used as the reference for reactive power scheduling (Q/S).
403 | Activ e pow er refer ence | RW | U32 | k W | 1000 | 0xA42B | 42027 | 2 | Set the lower limit of the maximum apparent value (SMax), which is also used as the reference for active power scheduling (percentage).
404 | Plan t activ e pow er gradi ent | RW | U16 | mi n/ 10 0% | 1 | 0xA42D | 42029 | 1 | China standards require that the active power change caused by light fluctuation must meet the speed requirements during normal operation of the equipment.
405 | Plan t activ e aver age filter ing time | RW | U32 | ms | 1 | 0xA42E | 42030 | 2
406 | Filter ing time for PF-U volta ge dete ction | RW | U16 | s | 10 | 0xA430 | 42032 | 1
407 | Dry cont act sche dulin g | RW | E16 |  |  | 0xA431 | 42033 | 1
408 | Audi ble and visua l alar m | RW | E16 |  |  | 0xA432 | 42034 | 1
409 | Freq uenc y Activ e Pow er Dera ting Reco very Dela y Time | RW | U16 | s | 1 | 0xA438 | 42040 | 1
410 | Freq uenc y Activ e Pow er Dera ting Effec tive Dela y Time | RW | U16 | ms | 1 | 0xA439 | 42041 | 1
411 | Freq uenc y activ e pow er dera ting hyst eresi s | RW | E16 |  |  | 0xA43A | 42042 | 1
412 | Freq uenc y mod ulati on cont rol resp onse dead band | RW | U16 | Hz | 1000 | 0xA43B | 42043 | 1
413 | Off- grid switc hove r mod e | RW | E16 |  |  | 0xA43C | 42044 | 1
414 | Off- grid mod e | RW | E16 |  |  | 0xA43D | 42045 | 1
415 | PQ mod e | RW | E16 |  |  | 0xA43E | 42046 | 1
416 | PV Pane l Type | RW | E16 |  |  | 0xA43F | 42047 | 1
417 | PID com pens atio n direc tion | RW | E16 |  |  | 0xA440 | 42048 | 1
418 | Strin g conn ectio n mod e | RW | E16 |  |  | 0xA441 | 42049 | 1
419 | Isola tion Setti ngs | RW | E16 |  |  | 0xA442 | 42050 | 1 | On the customer interface, only read signals can be displayed. Currently, only the input is not grounded and transformer is supported. Interface changes will be used to notify each interface during setting.
420 | Freq uenc y mod ulati on cont rol pow er chan ge gradi ent | RW | U16 | %/ mi n | 1 | 0xA443 | 42051 | 1
421 | Freq uenc y mod ulati on cont rol pow er chan ge limiti ng ampl itude | RW | U16 | % | 10 | 0xA444 | 42052 | 1
422 | FM cont rol dela y resp onse time | RW | U16 | ms | 1 | 0xA445 | 42053 | 1 | Polish national requirements, open and configurable Initial delay in the frequency sensitive mode
423 | MPP T mult imod al scan ning | RW | E16 |  |  | 0xA446 | 42054 | 1
424 | MPP T scan ning inter val | RW | U16 | mi n | 1 | 0xA447 | 42055 | 1
425 | Predi cted MPP T pow er | RO | U32 | k W | 1000 | 0xA448 | 42056 | 2
426 | Pow er grid fault reco very auto mati c start up | RW | E16 |  |  | 0xA44D | 42061 | 1
427 | Pow er limit 0% shut dow n | RW | E16 |  |  | 0xA44E | 42062 | 1
428 | Auto mati c pow er- off whe n com mun icati on is disco nnec ted | RW | E16 |  |  | 0xA44F | 42063 | 1 | In a parallel system, the system automatically shuts down when the communication link is interrupted by default. The communication interruption duration is 1 minute. The PCS power system determines the priority of the default power policy and the parameter setting. The affected parameters include all parameters under "Communication Disconnection Protection".
429 | Auto mati c pow er- on after com mun icati on reco very | RW | E16 |  |  | 0xA450 | 42064 | 1
430 | Pow er Qual ity Opti miza tion Mod e | RW | E16 |  |  | 0xA451 | 42065 | 1
431 | RCD Enha nce men t | RW | E16 |  |  | 0xA452 | 42066 | 1
432 | Nigh t react ive pow er | RW | E16 |  |  | 0xA453 | 42067 | 1
433 | Abn orm al grou ndin g shut dow n | RW | E16 |  |  | 0xA454 | 42068 | 1
434 | Nigh t PID prot ectio n | RW | E16 |  |  | 0xA455 | 42069 | 1
435 | Nigh t react ive pow er para mete rs take effec t | RW | E16 |  |  | 0xA456 | 42070 | 1
436 | Com mun icati on Disc onne ction Dete ction Time | RW | U16 | s | 1 | 0xA458 | 42072 | 1 | This parameter is displayed when the protection against communication disconnection is enabled.
437 | AFCI | RW | E16 |  |  | 0xA459 | 42073 | 1
438 | AFCI dete ction adap tatio n mod e | RW | E16 |  |  | 0xA45A | 42074 | 1
439 | Com mun icati on link failu re prot ectio n | RW | E16 |  |  | 0xA45B | 42075 | 1 | Used to initiate the security protection function after the communication between the device and the northbound interface is interrupted.
440 | Failu re prot ectio n activ e pow er mod e | RW | E16 |  |  | 0xA45C | 42076 | 1 | This parameter is displayed when the protection against communication disconnection is enabled.
441 | Activ e Pow er Limit for Failu re Prot ectio n [kW] [Low Preci sion] | RW | U32 | k W | 10 | 0xA45D | 42077 | 2 | This parameter is displayed only when the communication link failure protection is set to Enable and the active power mode is set to a fixed value.
442 | Failu re prot ectio n react ive pow er mod e | RW | E16 |  |  | 0xA45F | 42079 | 1 | This parameter is displayed when the protection against communication disconnection is enabled.
443 | Freq uenc y rate prot ectio n | RW | E16 |  |  | 0xA460 | 42080 | 1
444 | Freq uenc y chan ge rate prot ectio n poin t | RW | U16 | Hz /s | 10 | 0xA461 | 42081 | 1
445 | Freq uenc y chan ge rate prot ectio n time | RW | U16 | s | 10 | 0xA462 | 42082 | 1
446 | Reac tive pow er limit for failu re prot ectio n [Q/S ] [low preci sion] | RW | I16 |  | 1000 | 0xA463 | 42083 | 1 | (Deliver Q/S value) This parameter is displayed only when Communication Disconnection Failure Protection is set to Enable and Reactive Power Mode is set to Q/S.
447 | Pow er- on volta ge uppe r limit for grid conn ectio n | RW | U16 | V | 10 | 0xA464 | 42084 | 1 | Parameters for normal reconnection
448 | Pow er- on volta ge lowe r limit for grid conn ectio n | RW | U16 | V | 10 | 0xA465 | 42085 | 1 | Parameters for normal reconnection
449 | Pow er- on freq uenc y uppe r limit for grid conn ectio n | RW | U16 | Hz | 100 | 0xA466 | 42086 | 1 | Parameters for normal reconnection
450 | Pow er- on freq uenc y lowe r limit for grid conn ectio n | RW | U16 | Hz | 100 | 0xA467 | 42087 | 1 | Parameters for normal reconnection
451 | Pow er grid reco nnec tion volta ge uppe r limit | RW | U16 | V | 10 | 0xA468 | 42088 | 1 | Parameters for reconnection after a fault
452 | Pow er Grid Reco nnec tion Volt age Low er Thre shol d | RW | U16 | V | 10 | 0xA469 | 42089 | 1 | Parameters for reconnection after a fault
453 | Pow er grid reco nnec tion freq uenc y uppe r limit | RW | U16 | Hz | 100 | 0xA46A | 42090 | 1 | Parameters for reconnection after a fault
454 | Pow er grid reco nnec tion freq uenc y lowe r limit | RW | U16 | Hz | 100 | 0xA46B | 42091 | 1 | Parameters for reconnection after a fault
455 | Auto mati c Pow er Grid Reco nnec tion Time | RW | U16 | s | 1 | 0xA46C | 42092 | 1
456 | Insul atio n impe danc e prot ectio n poin t | RW | U16 | M Ω | 1000 | 0xA471 | 42097 | 1 | Value range: [0.02, 1.5] Actual protection is implemented by the inverter based on the DC voltage. 600 V DC inverter: [0.02, 1.5] 1000 V DC inverter: [0.033, 1.5] 1500 V DC inverter: [0.05, 1.5]
457 | Volt age unba lanc e prot ectio n thres hold | RW | U16 | % | 10 | 0xA472 | 42098 | 1
458 | Phas e prot ectio n poin t | RW | U16 | ° | 10 | 0xA473 | 42099 | 1
459 | Pow er- on soft start time due to pow er grid fault s | RW | U16 | s | 1 | 0xA474 | 42100 | 1 | Power rise gradient during equipment startup after a power grid fault
460 | Cos? - P/Pn trigg er volta ge | RW | U16 | % | 1 | 0xA475 | 42101 | 1
461 | Cos? - P/Pn exit volta ge | RW | U16 | % | 1 | 0xA476 | 42102 | 1
462 | Start up soft start time | RW | U16 | s | 1 | 0xA477 | 42103 | 1
463 | Pow er grid fault reco very time | RW | U16 | s | 1 | 0xA478 | 42104 | 1
464 | Time for dete rmin ing short - term pow er grid inter rupti on | RW | U32 | ms | 1 | 0xA479 | 42105 | 2 | Quick Start After Power Grid Fault is enabled and can be set.
465 | Shut dow n gradi ent | RW | U32 | %/ s | 1000 | 0xA47B | 42107 | 2
466 | Line loss com pens atio n | RW | U16 | % | 10 | 0xA47D | 42109 | 1
467 | Grid fault zero curre nt mod e | RW | E16 |  |  | 0xA47E | 42110 | 1
468 | Grid volta ge jump trigg er thres hold | RW | U16 | % | 10 | 0xA47F | 42111 | 1 | This parameter can be set only for the VDE4120.
469 | HVR T | RW | E16 |  |  | 0xA480 | 42112 | 1
470 | HVR T Trigg er Thre shol d | RW | U16 | V | 10 | 0xA481 | 42113 | 1
471 | HVR T posit ive sequ ence react ive pow er com pens atio n facto r | RW | U16 |  | 10 | 0xA482 | 42114 | 1
472 | V phas e to grou nd | RW | E16 |  |  | 0xA483 | 42115 | 1 | For the medium-three- phase 20KTL-M3 model in Japan, the phase wire on the side where the transformer is connected to the inverter must be grounded. The phase wire on the side where the transformer is connected to the inverter can be connected in delta or star topology.
473 | Shor t- term pow er grid inter rupti on and quic k start up | RW | E16 |  |  | 0xA484 | 42116 | 1 | Indicates whether to enable the fast startup function after the power grid recovers from a short-term interruption. If this parameter is set to 0, the power grid is connected according to the normal startup process after a short-term interruption. If this parameter is set to 1, the power grid is enabled. After a short-term interruption occurs on the power grid, the quick startup process is used. Some detection items are skipped and the power grid is quickly connected to the power grid. Whether a short-term interruption occurs on the power grid depends on whether the power grid can be recovered within the "short-term interruption time".
474 | LVRT activ e curre nt main tena nce coeff icien t | RW | U16 |  | 100 | 0xA486 | 42118 | 1
475 | LVRT | RW | E16 |  |  | 0xA487 | 42119 | 1 | By default, this function is enabled in the BDEW standard. In other standards, this function is disabled by default.
476 | LVRT Trigg er Thre shol d | RW | U16 | V | 10 | 0xA488 | 42120 | 1 | Sets the threshold for triggering low voltage ride- through. The threshold must comply with the local power grid standards.
477 | Pow er grid volta ge prot ectio n shiel d duri ng VRT | RW | E16 |  |  | 0xA489 | 42121 | 1 | It is used to set whether the voltage protection function needs to be shielded during the voltage ride-through.
478 | LVRT posit ive sequ ence react ive pow er com pens atio n facto r | RW | U16 |  | 10 | 0xA48A | 42122 | 1 | During the low voltage ride through (LVRT), the device needs to generate positive- sequence reactive power to support the power grid. This parameter is used to set the positive-sequence reactive power emitted by the device. For example, if the LVRT positive-sequence reactive power compensation factor is set to 2, the positive- sequence reactive current generated by the device increases by 20% of the rated current every time the AC voltage decreases by 10% during the low-voltage ride-through process.
479 | VRT exit hyst eresi s thres hold | RW | U16 | V | 10 | 0xA48B | 42123 | 1 | Sets the LVRT/HVRT recovery threshold. LVRT recovery threshold = LVRT trigger threshold + VRT exit hysteresis threshold HVRT recovery threshold = HVRT trigger threshold – VRT exit hysteresis threshold
480 | VRT activ e curre nt limiti ng perc enta ge | RW | U16 | % | 1 | 0xA48C | 42124 | 1
481 | VRT activ e pow er reco very gradi ent | RW | U16 | %/ s | 1 | 0xA48D | 42125 | 1
482 | HVR T nega tive sequ ence react ive com pens atio n facto r | RW | U16 |  | 10 | 0xA48E | 42126 | 1
483 | LVRT nega tive sequ ence react ive pow er com pens atio n facto r | RW | U16 |  | 10 | 0xA48F | 42127 | 1 | During low voltage ride through (LVRT), the device needs to generate negative- sequence reactive power to support the power grid. This parameter is used to set the negative-sequence reactive power emitted by the device. For example, if the LVRT negative sequence reactive power compensation factor is set to 2, the negative sequence reactive current generated by the device increases by 20% of the rated current every time the AC voltage decreases by 10% during the low voltage ride-through process.
484 | phas e angl e devi atio n prot ectio n | RW | E16 |  |  | 0xA490 | 42128 | 1
485 | Activ e Islan ding Prot ectio n | RW | E16 |  |  | 0xA491 | 42129 | 1
486 | Passi ve Islan ding Prot ectio n | RW | E16 |  |  | 0xA492 | 42130 | 1
487 | OVG R Asso ciate d Shut dow n | RW | E16 |  |  | 0xA493 | 42131 | 1
488 | Dry cont act func tion | RW | E16 |  |  | 0xA494 | 42132 | 1
489 | LVRT react ive curre nt limiti ng perc enta ge | RW | U16 | % | 1 | 0xA495 | 42133 | 1 | During low voltage ride- through, the equipment needs to limit the reactive current emitted by the equipment. For example, if LVRT Reactive Current Limit Percentage is set to 50, the upper limit of the reactive current of the device is 50% of the rated current during low voltage ride-through.
490 | LVRT zero curre nt mod e thres hold | RW | U16 | V | 10 | 0xA496 | 42134 | 1 | If the zero current mode is enabled and the voltage of the grid is less than the zero current mode threshold during LVRT, the zero current mode is used. Otherwise, the zero current mode is used.
491 | LVRT mod e | RW | E16 |  |  | 0xA497 | 42135 | 1
492 | RCD curre nt limit | RW | U16 | m A | 10 | 0xA498 | 42136 | 1
493 | Volt age rise supp ressi on | RW | E16 |  |  | 0xA49A | 42138 | 1
494 | Volt age rise supp ressi on react ive pow er adju stme nt poin t | RW | U16 | % | 10 | 0xA49B | 42139 | 1 | The value of "Voltage Rise Reject Active Derating Point" must be greater than the value of "Voltage Rise Reject Reactive Adjust Point".
495 | Volt age rise supp ressi on activ e dera ting thres hold | RW | U16 | % | 10 | 0xA49C | 42140 | 1 | The value of "Voltage Rise Reject Active Derating Point" must be greater than the value of "Voltage Rise Reject Reactive Adjust Point".
496 | freq uenc y mod ulati on cont rol | RW | E16 |  |  | 0xA49D | 42141 | 1 | According to the standards of some countries or regions, the power grid frequency changes around the rated value. If the device needs to fine-tune the active power output based on the frequency modulation control adjustment rate to help stabilize the power grid frequency, set this parameter to Enable. Frequency sensitive mode (FSM), which is required by the G99 standard.
497 | freq uenc y mod ulati on cont rol diffe renti al mod ulati on rate | RW | U16 | % | 1 | 0xA49E | 42142 | 1 | Frequency sensitive mode (FSM) Droop, which is required by the G99 standard.
498 | Over freq uenc y dera ting | RW | E16 |  |  | 0xA49F | 42143 | 1 | If this parameter is set to Enable, the device derates the active power based on a certain gradient when the power grid frequency exceeds the triggering frequency of overfrequency derating.
499 | Over freq uenc y dera ting cutof f freq uenc y | RW | U16 | Hz | 100 | 0xA4A0 | 42144 | 1 | Specifies the cutoff frequency for overfrequency derating.
500 | Over freq uenc y dera ting cut- off pow er | RW | U16 | % | 1 | 0xA4A1 | 42145 | 1 | Indicates the cutoff power point for overfrequency derating.
501 | Trigg ering freq uenc y of overf requ ency dera ting | RW | U16 | Hz | 100 | 0xA4A2 | 42146 | 1 | According to the standards in some countries or regions, the active power output by the device must be derated when the power grid frequency exceeds a specified value.
502 | Over freq uenc y dera ting exit freq uenc y | RW | U16 | Hz | 100 | 0xA4A3 | 42147 | 1 | Specifies the exit frequency of overfrequency derating.
503 | Over freq uenc y dera ting pow er reco very gradi ent | RW | U16 | %/ mi n | 1 | 0xA4A4 | 42148 | 1 | Indicates the speed at which the overfrequency derating power recovers.
504 | Und erfre quen cy Pow er Incre ase | RW | E16 |  |  | 0xA4A7 | 42151 | 1 | According to the standards in some countries or regions, the power grid frequency is lower than the triggering frequency of underfrequency power increase. In this case, the active power output needs to be increased to help increase the power grid frequency. In this case, set this parameter to Enable.
505 | Und erfre quen cy Pow er Incre ase Reco very Grad ient | RW | U16 | %/ mi n | 1 | 0xA4A8 | 42152 | 1 | Indicates the speed for recovering the underfrequency power increase.
506 | LVRT char acter istic curv e | RW | MLD |  |  | 0xA4AB | 42155 | 21 | Set the low-voltage ride- through capability of the equipment. For details, see the Key Information Description Table. The SmartLogger and NMS support batch settings and provide a separate GUI for users to edit.
507 | Cutof f freq uenc y of unde rfreq uenc y pow er incre ase | RW | U16 | Hz | 100 | 0xA4C0 | 42176 | 1 | Indicates the cutoff frequency for underfrequency power increase.
508 | Cut- off pow er for unde rfreq uenc y pow er incre ase | RW | U16 | % | 1 | 0xA4C1 | 42177 | 1 | Indicates the cutoff power point for underfrequency power increase.
509 | Und erfre quen cy Pow er Incre ase Trigg ering Freq uenc y | RW | U16 | Hz | 100 | 0xA4C2 | 42178 | 1 | Set the triggering frequency for underfrequency power increase.
510 | Und erfre quen cy Pow er Incre ase Exit Freq uenc y | RW | U16 | Hz | 100 | 0xA4C3 | 42179 | 1 | Specifies the exit frequency for underfrequency power increase.
511 | Built -in PID mod e | RW | E16 |  |  | 0xA4C4 | 42180 | 1
512 | PID outp ut volta ge | RW | I16 | V | 10 | 0xA4C5 | 42181 | 1 | Fixed output. This interface is reserved. The GUI is closed.
513 | PID | RW | E16 |  |  | 0xA4C6 | 42182 | 1 | Currently reserved only for equipment
514 | Nigh t off- grid repai r | RW | E16 |  |  | 0xA4C7 | 42183 | 1
515 | Activ e pow er chan ge gradi ent | RW | U32 | %/ s | 1000 | 0xA4D0 | 42192 | 2 | Dedicated broadcast interface for the SmartLogger, which does not support incremental reporting and is used in the remote output scenario in Japan.
516 | Q-U curv e | RW | MLD |  |  | 0xA4D8 | 42200 | 21
517 | P-U curv e | RW | MLD |  |  | 0xA4ED | 42221 | 21
518 | P-U curv e adju stme nt time | RW | U16 | s | 100 | 0xA502 | 42242 | 1
519 | Und ervol tage prot ectio n thres hold for 10 min utes | RW | U16 | V | 10 | 0xA52F | 42287 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
520 | Ten- min ute unde rvolt age prot ectio n time | RW | U32 | ms | 1 | 0xA530 | 42288 | 2
521 | Ten- min ute over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA532 | 42290 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
522 | Ten- min ute over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA533 | 42291 | 2
523 | Leve l-1 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA535 | 42293 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
524 | Leve l-1 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA536 | 42294 | 2
525 | Leve l-2 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA538 | 42296 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
526 | Leve l 2 Over volta ge Prot ectio n Time | RW | U32 | ms | 1 | 0xA539 | 42297 | 2
527 | Leve l-3 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA53B | 42299 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
528 | Leve l-3 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA53C | 42300 | 2
529 | Leve l-4 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA53E | 42302 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
530 | Leve l-4 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA53F | 42303 | 2
531 | Leve l-5 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA541 | 42305 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
532 | Leve l-5 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA542 | 42306 | 2
533 | Leve l-6 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA544 | 42308 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
534 | Leve l-6 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA545 | 42309 | 2
535 | Leve l-1 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA547 | 42311 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
536 | Leve l-1 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA548 | 42312 | 2
537 | Leve l-2 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA54A | 42314 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
538 | Leve l 2 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA54B | 42315 | 2
539 | Leve l-3 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA54D | 42317 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
540 | Leve l-3 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA54E | 42318 | 2
541 | Leve l-4 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA550 | 42320 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
542 | Leve l-4 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA551 | 42321 | 2
543 | Leve l-5 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA553 | 42323 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
544 | Leve l-5 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA554 | 42324 | 2
545 | Leve l-6 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA556 | 42326 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
546 | Leve l-6 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA557 | 42327 | 2
547 | Leve l-1 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA559 | 42329 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
548 | Leve l-1 Over freq uenc y Prot ectio n Time | RW | U32 | ms | 1 | 0xA55A | 42330 | 2
549 | Leve l-2 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA55C | 42332 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
550 | Leve l-2 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA55D | 42333 | 2
551 | Leve l-3 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA55F | 42335 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
552 | Leve l-3 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA560 | 42336 | 2
553 | Leve l-4 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA562 | 42338 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
554 | Leve l-4 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA563 | 42339 | 2
555 | Leve l-5 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA565 | 42341 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
556 | Leve l-5 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA566 | 42342 | 2
557 | Leve l-6 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA568 | 42344 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
558 | Six- level overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA569 | 42345 | 2
559 | Leve l-1 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA56B | 42347 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
560 | Leve l-1 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA56C | 42348 | 2
561 | Leve l-2 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA56E | 42350 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
562 | Leve l-2 unde rfreq uenc y prot ectio n time | RW | U32 | ms | 1 | 0xA56F | 42351 | 2
563 | Leve l-3 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA571 | 42353 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
564 | Leve l-3 unde rfreq uenc y prot ectio n time | RW | U32 | ms | 1 | 0xA572 | 42354 | 2
565 | Leve l-4 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA574 | 42356 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
566 | Leve l-4 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA575 | 42357 | 2
567 | Leve l-5 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA577 | 42359 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
568 | Leve l-5 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA578 | 42360 | 2
569 | Leve l-6 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA57A | 42362 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
570 | Leve l-6 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA57B | 42363 | 2
571 | Eme rgen cy stop switc h DI | RW | E16 |  |  | 0xA5A0 | 42400 | 1
572 | Outp ut impe danc e enha nce men t | RW | E16 |  |  | 0xA5A3 | 42403 | 1 | After the output impedance enhancement function is enabled, you can set the output impedance enhancement frequency to increase the output impedance at the frequency.
573 | Outp ut impe danc e enha nce men t freq uenc y poin t | RW | U16 | Hz | 10 | 0xA5A4 | 42404 | 1 | The default values are 1025.0 Hz for Switzerland, 175.0 Hz for France, and 210.0 Hz for Germany.
574 | Micr ogri d adap tabili ty | RW | E16 |  |  | 0xA5A7 | 42407 | 1 | The microgrid adaptability interface is added to the inverter (including the PCS current source grid-tied). When the microgrid adaptability function is enabled, the inverter (including the PCS current source grid-tied) supports a higher optical storage ratio based on the original country code feature.
575 | Oper atin g mod e | RW | E16 |  |  | 0xA5A9 | 42409 | 1 | The default value is PQ. You need to set the working mode during site deployment. Set the working mode to VSG in the churn scenario and PQ in the grid-tied scenario. Note: After this parameter is set, the device is powered off.
576 | Und erfre quen cy Pow er Incre ase Effec tive Dela y Time | RW | U16 | ms | 1 | 0xA5BD | 42429 | 1 | Setting the Underfrequency Power Increase Effective Delay Time
577 | Strin g-to- grou nd short circu it prot ectio n auto mati c reco very | RW | E16 |  |  | 0xA5C0 | 42432 | 1 | Enabled: The string short circuit to ground alarm is automatically cleared when the alarm conditions are not met. Disabled: The string short circuit to ground alarm cannot be automatically cleared. You need to manually clear the alarm.
578 | Dela yed upgr ade | RW | E16 |  |  | 0xA65E | 42590 | 1
579 | Intell igent strin g moni torin g | RW | E16 |  |  | 0xA662 | 42594 | 1
580 | Strin g dete ction refer ence asy mm etry coeff icien t | RW | U16 |  | 100 | 0xA663 | 42595 | 1
581 | Strin g dete ction start pow er perc enta ge | RW | U16 | % | 1 | 0xA664 | 42596 | 1
582 | Com mun icati on Inter rupti on Time | RW | I16 | mi n | 1 | 0xA665 | 42597 | 1
583 | Com mun icati ons | RW | E16 |  |  | 0xA666 | 42598 | 1
584 | [RS4 85-2 ] Com mun icati on | RW | E16 |  |  | 0xA667 | 42599 | 1
585 | PMI | WO | E16 |  |  | 0xA6EA | 42730 | 1 | Broadcast command interface Note: The instruction range extension design is made here. The higher eight bits are used to mask specified inspection actions in the inspection function. This feature improves the inspection efficiency for specific purposes. Shen Yanbai 20190702
586 | IV Curv e Scan ning | WO | E16 |  |  | 0xA71B | 42779 | 1 | Broadcast command interface
587 | Dayli ght Savi ng Time | RW | E16 |  |  | 0xA794 | 42900 | 1
588 | [DST ] Offs et time | RW | I16 | mi n | 1 | 0xA795 | 42901 | 1
589 | [DST ] Start Mon th | RW | U16 |  | 1 | 0xA796 | 42902 | 1
590 | [DST ] Start date | RW | U16 |  | 1 | 0xA797 | 42903 | 1 | The number of the day in a week is expressed by the number of weeks. The value 1 indicates Monday and the value 7 indicates Sunday. - shenyanbai 20190527
591 | [DST ] Start time | RW | U16 |  | 1 | 0xA798 | 42904 | 1
592 | [DST ] Start min ute | RW | U16 |  | 1 | 0xA799 | 42905 | 1
593 | [DST ] Start seco nd | RW | U16 |  | 1 | 0xA79A | 42906 | 1
594 | [DST ] End mon th | RW | U16 |  | 1 | 0xA79B | 42907 | 1
595 | [DST ] End date | RW | U16 |  | 1 | 0xA79C | 42908 | 1 | The number of the day in a week is expressed by the number of weeks. The value 1 indicates Monday and the value 7 indicates Sunday. - shenyanbai 20190527
596 | [Day light Savi ng Time ] Ends | RW | U16 |  | 1 | 0xA79D | 42909 | 1
597 | [DST ] End min ute | RW | U16 |  | 1 | 0xA79E | 42910 | 1
598 | [DST ] End seco nd | RW | U16 |  | 1 | 0xA79F | 42911 | 1
599 | [Syst em Time ] Year | WO | U16 |  | 1 | 0xA7F8 | 43000 | 1
600 | [Syst em Time ] Mon th | WO | U16 |  | 1 | 0xA7F9 | 43001 | 1
601 | [Syst em time ] day | WO | U16 |  | 1 | 0xA7FA | 43002 | 1
602 | [Syst em time ] hour | WO | U16 |  | 1 | 0xA7FB | 43003 | 1
603 | [Syst em Time ] Min. | WO | U16 |  | 1 | 0xA7FC | 43004 | 1
604 | [Syst em Time ] Seco nd | WO | U16 |  | 1 | 0xA7FD | 43005 | 1
605 | Time zone | RW | I16 | mi n | 1 | 0xA7FE | 43006 | 1
606 | Cloc k sour ce | RW | E16 |  |  | 0xA7FF | 43007 | 1
607 | City code | RW | U32 |  |  | 0xA800 | 43008 | 2 | (UTC+08:00) Beijing
608 | Inver ter Insta llatio n Posit ion Long itude | RW | I32 | ° | 10000000 | 0xA806 | 43014 | 2 | Set this parameter only on the app. The NMS can read the data.
609 | Inver ter Insta llatio n Posit ion Latit ude | RW | I32 | ° | 10000000 | 0xA808 | 43016 | 2 | Set this parameter only on the app. The NMS can read the data.
610 | [RS4 85-1 ] Prot ocol Type | RW | E16 |  |  | 0xA80A | 43018 | 1
611 | [RS4 85-1 ] Com mun icati on addr ess | RW | U16 |  | 1 | 0xA80B | 43019 | 1 | 0: broadcast address; 1–247: device address; 248–255: reserved
612 | [RS4 85-1 ] Baud Rate | RW | E16 |  |  | 0xA80C | 43020 | 1 | 115200 baud rate, corresponding to bit 26 of feature code 3.
613 | [RS4 85-1 ] Verif icati on mod e | RW | E16 |  |  | 0xA80D | 43021 | 1
614 | [RS4 85-1 ] Port mod e | RW | E16 |  |  | 0xA80E | 43022 | 1
615 | [RS4 85-1 ] Mod bus Prot ocol Mod el Versi on | RW | E16 |  |  | 0xA80F | 43023 | 1 | This parameter is used only when the northbound port is used in the old model replacement scenario.
616 | [RS4 85-2 ] Prot ocol Type | RW | E16 |  |  | 0xA819 | 43033 | 1
617 | [RS4 85-2 ] Com mun icati on addr ess | RW | U16 |  | 1 | 0xA81A | 43034 | 1 | 0: broadcast address 1–247: device address 248–255: reserved
618 | [RS4 85-2 ] Baud Rate | RW | E16 |  |  | 0xA81B | 43035 | 1 | 115200 baud rate, corresponding to bit 27 of feature code 3.
619 | [RS4 85-2 ] Verif icati on Mod e | RW | E16 |  |  | 0xA81C | 43036 | 1
620 | [RS4 85-2 ] Port mod e | RW | E16 |  |  | 0xA81D | 43037 | 1
621 | Prot ocol Type | RW | E16 |  |  | 0xA827 | 43047 | 1
622 | Box- type trans form er num ber | RW | U16 |  | 1 | 0xA828 | 43048 | 1 | Only the 06 function code is supported. Local application
623 | Win ding No. | RW | U16 |  | 1 | 0xA829 | 43049 | 1 | Only the 06 function code is supported. Local application
624 | Mac Offs et | RW | U16 |  | 1 | 0xA82A | 43050 | 1 | Only the 06 function code is supported. Local application
625 | Pow er setti ngs | RW | U16 | dB | 1 | 0xA82C | 43052 | 1 | Note: This parameter x 2 corresponds to the dB value.
626 | [Ma nage men t Syst em] TCP Fra me Leng th | RW | U16 |  | 1 | 0xA837 | 43063 | 1 | [320, 1500]
627 | [Ma nage men t Syst em] Appl icati on- Laye r Hear tbea t Inter val | RW | U16 | mi n | 1 | 0xA838 | 43064 | 1 | Default value: 30 minutes
628 | [Ma nage men t Syst em] TCP Hear tbea t Inter val | RW | U16 | s | 1 | 0xA839 | 43065 | 1 | 0XFFFF indicates that there is no heartbeat. If this parameter is set to 0, the default heartbeat period is 3 minutes.
629 | [Ma nage men t Syst em] Prot ocol Type | RW | E16 |  |  | 0xA83A | 43066 | 1
630 | [Ma nage men t Syst em] Serv er | RW | STR |  | 1 | 0xA83B | 43067 | 30 | Domain name address or IP address
631 | [Ma nage men t syste m] Port 1 | RW | U16 |  | 1 | 0xA859 | 43097 | 1
632 | [Ma nage men t Syst em] TLS Encr yptio n | RW | E16 |  |  | 0xA85A | 43098 | 1
633 | [Ma nage men t Syst em] Port mod e | RW | E16 |  |  | 0xA85C | 43100 | 1
634 | [FE] Key pass word | WO | MLD |  |  | 0xA85E | 43102 | 32 | Interface for delivering the key password when the app certificate is replaced
635 | [STA ] Acce ssing a Wire less Rout er | RW | E16 |  |  | 0xA88B | 43147 | 1
636 | [STA ] Wire less Rout ing Net work Nam e | RW | STR |  | 1 | 0xA88C | 43148 | 16
637 | [STA ] Wire less Rout ing Encr yptio n Mod e | RW | E16 |  |  | 0xA89C | 43164 | 1
638 | [STA ] Wire less Rout er Logi n Pass word | RW | STR |  | 1 | 0xA89D | 43165 | 32 | This parameter is not displayed in non-encryption mode.
639 | [FE] DHC P | RW | E16 |  |  | 0xA8BD | 43197 | 1
640 | [FE] IP addr ess | RW | IPv4 |  |  | 0xA8BE | 43198 | 2 | If the IP address, subnet mask, and gateway address are modified, the other two parameters must be delivered in the same frame.
641 | [FE] Subn et Mas k | RW | IPv4 |  |  | 0xA8C0 | 43200 | 2
642 | [FE] Gate way addr ess | RW | IPv4 |  |  | 0xA8C2 | 43202 | 2
643 | [STA ] Prefe rred DNS Serv er | RW | U32 |  | 1 | 0xA8C4 | 43204 | 2
644 | [STA ] Stan dby DNS serv er | RW | U32 |  | 1 | 0xA8C6 | 43206 | 2
645 | [FE] DHC P | RW | E16 |  |  | 0xA8C8 | 43208 | 1 | Decoupling mode: Feature code 2:18
646 | [FE] IP addr ess | RW | U32 |  | 1 | 0xA8C9 | 43209 | 2 | If the IP address, subnet mask, and gateway address are modified, the other two parameters must be delivered in the same frame.
647 | [FE] Subn et Mas k | RW | U32 |  | 1 | 0xA8CB | 43211 | 2
648 | [FE] Gate way addr ess | RW | U32 |  | 1 | 0xA8CD | 43213 | 2
649 | [FE] Prefe rred DNS serv er | RW | U32 |  | 1 | 0xA8CF | 43215 | 2 | Decoupling mode: Feature code 2:18
650 | [FE] Seco ndar y DNS serv er | RW | U32 |  | 1 | 0xA8D1 | 43217 | 2 | Decoupling mode: Feature code 2:18
651 | WLA N O& M Polic y | RW | E16 |  |  | 0xA8E4 | 43236 | 1 | Configures O&M policies for WLAN ports. For the SACU, policies 0, 1, and 2 can be configured. For the APP, policies 0 and 1. Permanently enabled: The WLAN port function is always available. Idle: Disable the WLAN O&M function after the idle time is 4 hours. Permanently disabled: The WLAN function is unavailable. If the power can be disabled, the power is disabled. If the power cannot be disabled, the O&M capability is disabled. Supported by SDongle and distributed inverters
652 | [AP] SSID broa dcas t | RW | U16 |  | 1 | 0xA8E5 | 43237 | 1 | 0: enabled 1: disabled Default value: 0
653 | [AP] WLA N nam e | RW | STR |  | 1 | 0xA8E6 | 43238 | 16 | Wifi-AP mode
654 | [AP] WLA N Logi n Pass word | RW | STR |  | 1 | 0xA8F6 | 43254 | 32 | The password must contain at least eight characters.
655 | [AP] Gate way IP addr ess | RW | U32 |  | 1 | 0xA917 | 43287 | 2
656 | [AP] subn et mas k | RW | U32 |  | 1 | 0xA919 | 43289 | 2
657 | [NTP ] NTP time sync hron izati on | RW | U16 |  | 1 | 0xA92F | 43311 | 1
658 | [NTP ] NTP serv er addr ess | RW | STR |  | 1 | 0xA930 | 43312 | 30
659 | [NTP ] NTP serv er port | RW | U16 |  | 1 | 0xA94E | 43342 | 1
660 | [NTP ] NTP Servi ce Time Inter val | RW | U16 | mi n | 1 | 0xA94F | 43343 | 1
661 | Devi ce nam e | RW | STR |  |  | 0xA955 | 43349 | 10 | This parameter is left blank by default. It is used by the customer to modify the device name.
662 | [App ] Initia l pow er- on flag | RW | E16 |  |  | 0xA95F | 43359 | 1 | After the SmartLogger is deployed, the power-on flag needs to be cleared.
663 | Paral lel com mun icati on mod e | RW | E16 |  |  | 0xA961 | 43361 | 1 | This interface is used to set the communication mode between the host machine and the parallel slave server in the Sdongle network access scenario. After the setting, the host machine bridges the Dongle or USB expansion module to the interface. Note: This interface is used to replace the cascade channel 43360 interface. The inverter must be compatible with this interface. When the interface has been set, the parameters must be migrated. When the high byte is 0, the SUN2000 automatically determines the parallel control entry based on the request entry.
664 | [4G] 4G mod ule | RW | E16 |  |  | 0xA96A | 43370 | 1
665 | [4G] Card No. | RW | MLD |  | 1 | 0xA97A | 43386 | 10
666 | [4G] Net work mod e | RW | E16 |  |  | 0xA9A6 | 43430 | 1
667 | [4G] APN mod e | RW | E16 |  |  | 0xA9A7 | 43431 | 1
668 | [4G] [Def ault] Iden tity auth entic atio n type | RW | E16 |  |  | 0xA9A9 | 43433 | 1
669 | [4G] [Def ault] APN | RW | STR |  | 1 | 0xA9AA | 43434 | 16
670 | [4G] [Def ault] APN user nam e | RW | STR |  | 1 | 0xA9CA | 43466 | 16
671 | [4G] [Def ault] APN user pass word | RW | STR |  | 1 | 0xA9DA | 43482 | 16
672 | [4G] Iden tity auth entic atio n type | RW | E16 |  |  | 0xA9EB | 43499 | 1
673 | [4G] APN | RW | STR |  | 1 | 0xA9EC | 43500 | 16 | APN name
674 | [4G] APN dial- up num ber | RW | STR |  | 1 | 0xA9FC | 43516 | 16 | Dial Number
675 | [4G] APN User Nam e | RW | STR |  | 1 | 0xAA0C | 43532 | 16 | APN User Name
676 | [4G] APN user pass word | RW | STR |  | 1 | 0xAA1C | 43548 | 16 | APN Password
677 | [4G] Traff ic pack age | RW | U32 | M B | 100 | 0xAA2C | 43564 | 2
678 | [4G] Mon thly used traffi c | RW | U32 | M B | 100 | 0xAA2E | 43566 | 2 | Used for traffic correction.
679 | [4G] PIN | WO | MLD |  | 1 | 0xAA30 | 43568 | 4
680 | Strin g acce ss dete ction | RW | U16 |  | 1 | 0xAA70 | 43632 | 1 | 0: disabled (default) 1: enabled
681 | Start -up curre nt | RW | U16 | A | 100 | 0xAA71 | 43633 | 1 | [3.0, 10.0] Default value: 5.0
682 | Two- in- one dete ction start ing curre nt | RW | U16 | A | 100 | 0xAA72 | 43634 | 1 | [10.0, 20.0] Default value: 15.0
683 | Strin g 1 acce ss type | RW | E16 |  |  | 0xAA73 | 43635 | 1
684 | Strin g 2 Acce ss Type | RW | E16 |  |  | 0xAA74 | 43636 | 1
685 | Strin g 3 Acce ss Type | RW | E16 |  |  | 0xAA75 | 43637 | 1
686 | Strin g 4 Acce ss Type | RW | E16 |  |  | 0xAA76 | 43638 | 1
687 | Strin g 5 Acce ss Type | RW | E16 |  |  | 0xAA77 | 43639 | 1
688 | Strin g 6 Acce ss Type | RW | E16 |  |  | 0xAA78 | 43640 | 1
689 | Strin g 7 Acce ss Type | RW | E16 |  |  | 0xAA79 | 43641 | 1
690 | Strin g 8 Acce ss Type | RW | E16 |  |  | 0xAA7A | 43642 | 1
691 | Supp ort Syst em Type | RW | E16 |  |  | 0xABE0 | 44000 | 1 | If the device vendor does not support one of the modes, the system returns the 03 error code.
692 | Oper atin g mod e | RW | E16 |  |  | 0xABE1 | 44001 | 1
693 | Cont rol perio d | RW | U16 | mi n | 1 | 0xABE2 | 44002 | 1
694 | Start time of rever se traci ng in the mor ning (hou r) | RW | U16 | ho ur | 1 | 0xABE3 | 44003 | 1
695 | Start time of rever se traci ng in the mor ning (min utes) | RW | U16 | mi n | 1 | 0xABE4 | 44004 | 1
696 | Mor ning Back track ing Dura tion Min ute | RW | U16 | mi n | 1 | 0xABE5 | 44005 | 1
697 | Tilt angl e cont rol | RW | MLD |  | 1 | 0xABE6 | 44006 | 2 | HW: ID of the support system, ranging from 0 to 16. The value 0 indicates full control. LW: tilt angle. The gain is 100. The value range is [0-90]. The control angle range also meets the requirements of the upper and lower limits of tilt angle control.
698 | Beari ng cont rol | RW | MLD |  | 1 | 0xABE8 | 44008 | 2 | HW: ID of the support system, ranging from 0 to 16. 0 indicates full control. LW: azimuth preset value, gain 100, range [-90 to 90] The control angle range must meet the requirements of the upper and lower limits of azimuth control.
699 | Num ber of mot ors cont rolle d simu ltane ousl y | RW | U16 |  | 1 | 0xABEA | 44010 | 1 | If the actual number of motors is less than 16, the setting may fail.
700 | Start time of the rever se traci ng in the even ing (hou r) | RW | U16 | ho ur | 1 | 0xABEB | 44011 | 1
701 | Start time of the rever se traci ng in the even ing (min ute) | RW | U16 | mi n | 1 | 0xABEC | 44012 | 1
702 | Even ing Back track ing Dura tion Min ute | RW | U16 | mi n | 1 | 0xABED | 44013 | 1
703 | Sens or insta llatio n direc tion | RW | E16 |  |  | 0xABEE | 44014 | 1
704 | Cont rolle r time sync hron izati on | RW | E16 |  |  | 0xABEF | 44015 | 1
705 | Num ber of cont rol boxe s | RW | U16 |  | 1 | 0xABF0 | 44016 | 1
706 | Total num ber of stent s | RW | U16 |  | 1 | 0xAC12 | 44050 | 1 | When dual-axis control is used, the maximum number of support systems is 8.
707 | Insta llatio n Long itude | RW | I16 | ° | 100 | 0xAC13 | 44051 | 1 | The east longitude is positive and the west longitude is negative.
708 | Insta llatio n Dim ensi on | RW | I16 | ° | 100 | 0xAC14 | 44052 | 1 | The north latitude is positive and the south latitude is negative.
709 | Cont rol addr ess 1 | RW | U16 |  | 1 | 0xAC15 | 44053 | 1
710 | Cont rol addr ess 2 | RW | U16 |  | 1 | 0xAC16 | 44054 | 1
711 | Sout hbou nd RS48 5 Chec k Mod e | RW | E16 |  |  | 0xAC17 | 44055 | 1
712 | Sout hbou nd RS48 5 baud rate | RW | E16 |  |  | 0xAC18 | 44056 | 1
713 | Tilt angl e cont rol uppe r limit | RW | I16 | ° | 100 | 0xAC19 | 44057 | 1 | Tilt angle control upper limit must be greater than lower limit
714 | Tilt angl e cont rol lowe r limit | RW | I16 | ° | 100 | 0xAC1A | 44058 | 1 | Tilt angle control upper limit must be greater than lower limit
715 | Upp er limit of azim uth cont rol | RW | I16 | ° | 100 | 0xAC1B | 44059 | 1 | The upper limit of azimuth control must be greater than the lower limit.
716 | Low er limit for azim uth cont rol | RW | I16 | ° | 100 | 0xAC1C | 44060 | 1 | The upper limit of azimuth control must be greater than the lower limit.
717 | Sens or 1 addr ess | RW | U16 |  | 1 | 0xAC1D | 44061 | 1
718 | Sens or 2 Addr ess | RW | U16 |  | 1 | 0xAC1E | 44062 | 1
719 | Sens or 3 Addr ess | RW | U16 |  | 1 | 0xAC1F | 44063 | 1
720 | Sens or 4 Addr ess | RW | U16 |  | 1 | 0xAC20 | 44064 | 1
721 | Sens or 5 Addr ess | RW | U16 |  | 1 | 0xAC21 | 44065 | 1
722 | Sens or 6 Addr ess | RW | U16 |  | 1 | 0xAC22 | 44066 | 1
723 | Sens or 7 addr ess | RW | U16 |  | 1 | 0xAC23 | 44067 | 1
724 | Sens or 8 Addr ess | RW | U16 |  | 1 | 0xAC24 | 44068 | 1
725 | Sens or 9 Addr ess | RW | U16 |  | 1 | 0xAC25 | 44069 | 1
726 | Sens or 10 Addr ess | RW | U16 |  | 1 | 0xAC26 | 44070 | 1
727 | Sens or 11 addr ess | RW | U16 |  | 1 | 0xAC27 | 44071 | 1
728 | Sens or 12 Addr ess | RW | U16 |  | 1 | 0xAC28 | 44072 | 1
729 | Sens or 13 addr ess | RW | U16 |  | 1 | 0xAC29 | 44073 | 1
730 | Sens or 14 Addr ess | RW | U16 |  | 1 | 0xAC2A | 44074 | 1
731 | Sens or 15 Addr ess | RW | U16 |  | 1 | 0xAC2B | 44075 | 1
732 | Sens or 16 Addr ess | RW | U16 |  | 1 | 0xAC2C | 44076 | 1
733 | Trac king syste m cont rolle r | RW | E16 |  |  | 0xAC2D | 44077 | 1
734 | Cont rol addr ess 3 | RW | U16 |  | 1 | 0xAC2F | 44079 | 1
735 | Cont rol addr ess 4 | RW | U16 |  | 1 | 0xAC30 | 44080 | 1
736 | Sout hbou nd RS48 5 stop bit | RW | E16 |  |  | 0xAC31 | 44081 | 1
737 | Supp ort Fault Clea ranc e | WO | U16 |  | 1 | 0xAC32 | 44082 | 1 | 0: Clear all support faults. 1-16: Clear the fault of the specified support.
738 | GPS time (loca l time ): year | RW | U16 |  | 1 | 0xAC33 | 44083 | 1
739 | wind spee d | RW | U16 | m/ s | 1 | 0xAC39 | 44089 | 1
740 | Time zone | RW | I16 | mi n | 1 | 0xAC3A | 44090 | 1
741 | Cont rol addr ess 5 | RW | U16 |  | 1 | 0xAC3B | 44091 | 1
742 | Cont rol addr ess 6 | RW | U16 |  | 1 | 0xAC3C | 44092 | 1
743 | Cont rol addr ess 7 | RW | U16 |  | 1 | 0xAC3D | 44093 | 1
744 | Cont rol addr ess 8 | RW | U16 |  | 1 | 0xAC3E | 44094 | 1
745 | Cont rol addr ess 9 | RW | U16 |  | 1 | 0xAC3F | 44095 | 1
746 | Cont rol addr ess 10 | RW | U16 |  | 1 | 0xAC40 | 44096 | 1
747 | Cont rol addr ess 11 | RW | U16 |  | 1 | 0xAC41 | 44097 | 1
748 | Cont rol addr ess 12 | RW | U16 |  | 1 | 0xAC42 | 44098 | 1
749 | Cont rol addr ess 13 | RW | U16 |  | 1 | 0xAC43 | 44099 | 1
750 | Cont rol addr ess 14 | RW | U16 |  | 1 | 0xAC44 | 44100 | 1
751 | Cont rol addr ess 15 | RW | U16 |  | 1 | 0xAC45 | 44101 | 1
752 | Cont rol addr ess 16 | RW | U16 |  | 1 | 0xAC46 | 44102 | 1
753 | Scie nce and Tech nolo gy Jingk e Prot ocol Versi on | RW | E16 |  |  | 0xAC47 | 44103 | 1
754 | Sens or Rang e | RW | U16 | ° | 1 | 0xAC48 | 44104 | 1
755 | Cont rol preci sion | RW | U16 | ° | 100 | 0xAC49 | 44105 | 1
756 | KP | RW | I16 |  | 100 | 0xACA8 | 44200 | 1 | Debugging interface
757 | KI | RW | I16 |  | 100 | 0xACA9 | 44201 | 1 | Debugging interface
758 | KD | RW | I16 |  | 100 | 0xACAA | 44202 | 1 | Debugging interface
759 | wind spee d | WO | U16 | m/ s | 1 | 0xAD0C | 44300 | 1
760 | Win d direc tion | WO | U16 | ° | 1 | 0xAD0D | 44301 | 1
761 | Start up cont rol | WO | E16 |  |  | 0xAD0E | 44302 | 2 | BIT0–BIT15: Start command of bracket 1–bracket system 16; BIT16–BIT31: reserved for future expansion.
762 | Supp ort Fault Clea ranc e | WO | E16 |  |  | 0xAD10 | 44304 | 2 | BIT0–BIT15: Clear the faults of support 1–16 in sequence. Bits 16–32: reserved for future expansion.
763 | Stop cont rol | WO | E16 |  |  | 0xAD12 | 44306 | 2 | BIT0~BIT15: stop command of rack 1~rack system 16; BIT16–BIT31: reserved for future expansion.
764 | Tem pera ture 1 | WO | I16 | °C | 10 | 0xAD78 | 44408 | 1
765 | Hum idity 1 | WO | U16 | % RH | 10 | 0xAD7A | 44410 | 1
766 | Rest ore facto ry setti ngs. | WO | E16 |  |  | 0xAFC8 | 45000 | 1
767 | Clea ring activ e alar ms | WO | MLD |  |  | 0xAFC9 | 45001 | 2
768 | Alar m setti ng | WO | MLD |  |  | 0xAFCB | 45003 | 2
769 | Alar m clear ance | WO | E16 |  |  | 0xAFCD | 45005 | 1
770 | Alar m mas king | WO | E16 |  |  | 0xAFCE | 45006 | 1
771 | AFCI self- chec k start | WO | U16 |  | 1 | 0xAFCF | 45007 | 1 | Set the field to 0. Associate the AFCI controller in the in-position ID of the subdevice.
772 | Accu mula ted ener gy yield corre ction | WO | U32 | k W h | 100 | 0xAFD0 | 45008 | 2
773 | Clea r histo rical batt ery level. | WO | E16 |  |  | 0xAFD2 | 45010 | 1 | Including the accumulated power generation capacity and accumulated charging capacity on the power side
774 | Clea r the runn ing time infor mati on. | WO | E16 |  |  | 0xAFD3 | 45011 | 1 | Clears the accumulated running time, fault duration, and grid-tied running time.
775 | Spot Chec k | WO | E16 |  |  | 0xAFD4 | 45012 | 1
776 | Clea r the flash me mor y. | WO | U16 |  | 1 | 0xAFD6 | 45014 | 1
777 | ESN valid atio n com man d | WO | U16 |  | 1 | 0xAFD7 | 45015 | 1
778 | Rest ore the defa ult pass word . | WO | MLD |  | 1 | 0xAFD8 | 45016 | 10 | Enter the equipment ESN in the Data field.
779 | [STA ] Start scan ning the avail able WLA N list. | WO | U16 |  | 1 | 0xAFE2 | 45026 | 1 | 0
780 | [Lice nse Inter face] Lice nse Dere gistr atio n | WO | MLD |  | 1 | 0xAFE3 | 45027 | 10 | Fill the LSN in the data field.
781 | Alar m port self- chec k start | WO | U16 |  | 1 | 0xAFED | 45037 | 1 | The data field is set to 0.
782 | Audi ble and visua l alar m confi rmat ion | WO | U16 |  | 1 | 0xAFF0 | 45040 | 1 | This parameter is added to disable the audible and visual alarm function. After the alarm condition is cleared, the audible and visual alarm function is enabled again.
783 | Box- type trans form er num ber | RW | U16 |  | 1 | 0xB799 | 47001 | 1 | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
784 | Win ding No. | RW | U16 |  | 1 | 0xB79A | 47002 | 1 | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
785 | Mac Offs et | RW | U16 |  | 1 | 0xB79B | 47003 | 1 | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
786 | Oper atin g mod e | RW | E16 |  |  | 0xB79C | 47004 | 1
787 | Pow er limit for grid- tied sites | RW | I32 | W | 1 | 0xB7E7 | 47079 | 2
788 | Opti mize r | RW | E16 |  |  | 0xB810 | 47120 | 1 | Used to add the safety box. After the safety box is added, the DC-PLC status is set. Shenyanbai: This flag is forcibly set to 1 in the single-phase inverter implementation of the US version.
789 | Singl e Opti mize r Data Quer y | RW | U16 |  | 1 | 0xB816 | 47126 | 1 | Optimizer Logical Address
790 | Alias Setti ngs | WO | MLD |  | 1 | 0xB819 | 47129 | 11 | W0: optimizer address; (small end) W1–10: alias character string
791 | Phys ical locat ion | WO | E16 |  |  | 0xB824 | 47140 | 1 | Anti-crosstalk is disabled.
792 | Imp ortin g Logs | WO | E16 |  |  | 0xB825 | 47141 | 1
793 | Brok en line dete ction | WO | E16 |  |  | 0xB827 | 47143 | 1
794 | Expo rt com plete logs. | WO | E16 |  |  | 0xB828 | 47144 | 1
795 | Setti ng the Accu mula ted Ener gy Yield | WO | MULTIDATA | 1 |  | 0xB829 | 47145 | 3 | Gain: 1000 Unit: kWh
796 | Baud Rate | RW | E16 |  |  | 0xB82E | 47150 | 1 | The MBUS register is 43113.
797 | Anti- cross talk | RW | E16 |  |  | 0xB82F | 47151 | 1 | The MBUS register is 47022.
798 | Net work freq uenc y band | RW | E16 |  |  | 0xB830 | 47152 | 1 | The MBUS register is 43116.
799 | Net work ing | RW | E16 |  |  | 0xB831 | 47153 | 1 | The MBUS register is 47010.
800 | Pack et loss rate test | RW | E16 |  |  | 0xB832 | 47154 | 1
801 | Secu rity mod e | RW | E16 |  |  | 0xB834 | 47156 | 1 | When the PLC enters and exits the unlock mode, the CCO is reset.
802 | Fast pow er- dow n enab le | RW | E16 |  |  | 0xB835 | 47157 | 1
803 | Fast Shut dow n Self- Test | WO | U16 |  |  | 0xB836 | 47158 | 1
804 | Forw ard pow er | RW | E16 |  |  | 0xB8C4 | 47300 | 1
805 | Cabl e conn ectio n posit ion | RW | E16 |  |  | 0xB8C5 | 47301 | 1
806 | CT rate d curre nt | RW | U16 | A | 1 | 0xB8C6 | 47302 | 1
807 | Met er mod el | RW | E16 |  |  | 0xB8C7 | 47303 | 1 | Note: 47002 conflicts with the winding number of the [Remote Setting]. The winding number is reassigned. This interface will be used in later versions. Naming format: manufacturer-model
808 | Met er addr ess | RW | U16 |  | 1 | 0xB8C8 | 47304 | 1 | Note: 47003 conflicts with [Remote Settings] MAC Offset. This interface will be used in later versions.
809 | Met er nam e | RW | MLD |  | 1 | 0xB8C9 | 47305 | 15 | Used to store the name of the meter during model loading.
810 | Enab le auto mati c addr ess alloc atio n. | RW | E16 |  |  | 0xB928 | 47400 | 1
811 | Start addr ess for auto mati c addr ess assig nme nt | RW | U16 |  | 1 | 0xB929 | 47401 | 1
812 | Com mun icati on mod ule addr ess | RW | U16 |  | 1 | 0xB936 | 47414 | 1
813 | Activ e pow er cont rol mod e | RW | E16 |  |  | 0xB937 | 47415 | 1
814 | Maxi mu m pow er fed to the grid (kW) | RW | I32 | k W | 1000 | 0xB938 | 47416 | 2
815 | Maxi mu m Feed Grid Pow er (%) | RW | I16 | % | 10 | 0xB93A | 47418 | 1
816 | Restr ictio n mod e | RW | E16 |  |  | 0xB93B | 47419 | 1
817 | Pow er decr ease adju stme nt perio d | RW | U16 | s | 10 | 0xB93C | 47420 | 1
818 | Maxi mu m prot ectio n time | RW | U16 | s | 10 | 0xB93D | 47421 | 1
819 | Pow er Incre ase Thre shol d | RW | U32 | k W | 1000 | 0xB93E | 47422 | 2
820 | Activ e pow er limit for fail prot ectio n [%] [low preci sion] | RW | I16 | % | 10 | 0xB940 | 47424 | 1 | Not displayed on the GUI. The gains of the old interface are different. This function is used only to support the batch settings of the SmartLogger.
821 | react ive pow er cont rol mod e | RW | E16 |  |  | 0xB941 | 47425 | 1
822 | Reac tive fixed valu e | RW | I32 | kV ar | 1000 | 0xB942 | 47426 | 2
823 | targ et pow er facto r | RW | I16 |  | 1000 | 0xB944 | 47428 | 1
824 | Reac tive pow er adju stme nt perio d | RW | U16 | s | 10 | 0xB945 | 47429 | 1
825 | Adju sting Dea d Zone | RW | U16 |  | 1000 | 0xB946 | 47430 | 1
826 | Com pens atin g dela y | RW | U16 | s | 10 | 0xB947 | 47431 | 1
827 | Failu re prot ectio n react ive pow er limit [PF] | RW | I16 |  | 1000 | 0xB948 | 47432 | 1 | This parameter is displayed only when Communication Disconnection Failure Protection is set to Enabled and Reactive Power Mode is set to Power Factor.
828 | Plan t capa city | RW | U32 | k W | 1000 | 0xB949 | 47433 | 2
829 | Pow er plan t DC capa city | RW | U32 | k W | 1000 | 0xB94B | 47435 | 2
830 | [Re mot e Outp ut] Certif icate | RW | E16 |  |  | 0xB94D | 47437 | 1 | Note: "Output Control" is a direct reference in Japanese name, which essentially expresses the active output control under server scheduling. Currently, this function is required only by Japan. Update the name when the general function requires it. 20190223 Shen Yanbai
831 | [Re mot e outp ut] PV plan t ID | RW | MLD |  |  | 0xB94E | 47438 | 13 | Only 26 digits are supported.
832 | [Re mot e outp ut] Rem ote outp ut cont rol serv er | RW | STR |  |  | 0xB95B | 47451 | 30 | Other server addresses can be manually entered.
833 | [Re mot e Outp ut] Rem ote Outp ut Cont rol Time | RW | U16 | mi n | 1 | 0xB979 | 47481 | 1 | It refers to the time that the output of the plant is controlled from 0% to 100%.
834 | [Re mot e outp ut] Con necti ng to the disp atch serv er | WO | U16 |  | 1 | 0xB97A | 47482 | 1
835 | close d loop cont rolle r | RW | E16 |  |  | 0xB97B | 47483 | 1 | Note: The external controller uses the exponential data source or Dongle. In this case, the inverter does not perform the closed-loop control algorithm.
836 | [Loc al Acce ss] Link Enab led | RW | E16 |  |  | 0xB9EA | 47594 | 1
837 | [Loc al acce ss] Clien t 1 IP addr ess | RW | IPv4 |  | 1 | 0xB9EB | 47595 | 2
838 | Sche dule Task | RW | E16 |  |  | 0xBA3A | 47674 | 1 | South Australia Dynamic Feeder Requirements
839 | Maxi mu m Feed Grid Pow er Defa ult | RW | I32 | k W | 1000 | 0xBA3B | 47675 | 2 | Power limit on the grid-tied point when the default task is executed for the dynamic feeder network in South Australia.
840 | Defa ult activ e pow er chan ge gradi ent | RW | U32 | %/ s | 1000 | 0xBA3D | 47677 | 2 | Power change rate during switchover between the default task and the planned task in South Australia dynamic feeder network requirements
841 | Feed ing pow er over- thres hold prot ectio n shut dow n | RW | U16 | 1 |  | 0xBB4E | 47950 | 1
842 | Feed thres hold - cross ing prot ectio n shut dow n thres hold | RW | I32 | 10 00 |  | 0xBB4F | 47951 | 2
843 | Feed thres hold - cross ing prot ectio n shut dow n time | RW | U16 | 1 |  | 0xBB51 | 47953 | 1
844 | [Ma nage men t Syst em - 1] Man age men t Syst em Acce ss | RW | U16 | N/ A |  | 0xBB95 | 48021 | 1
845 | [Ma nage men t Syst em- 1] Prot ocol Type | RW | E16 |  |  | 0xBBD7 | 48087 | 1 | Automatically adapt to the "1" protocol for the SkyTeam OEM model.
846 | Grou nd short circu it prot ectio n | RW | E16 |  |  | 0xBBDA | 48090 | 1

## Summary
Section | Sheet Name | Register Count | Address Range
01. Device Info (Nameplate) | 01_DeviceInfo | 33 | 30000~30191 (0x7530~0x75EF)
02. Device Info (Extended) | 02_DeviceInfo_Ext | 18 | 30201~30591 (0x75F9~0x777F)
03. Subdevice / Components | 03_Subdevice | 8 | 31000~31200 (0x7918~0x79E0)
04. Status & Alarms | 04_Status_Alarms | 116 | 32000~32307 (0x7D00~0x7E33)
05. Real-time Measurements | 05_Realtime | 60 | 36033~37519 (0x8CC1~0x928F)
06. PV String Data | 06_PV_String | 128 | 34000~35304 (0x84D0~0x89E8)
07. Grid Parameters | 07_Grid_Params | 27 | 40000~40500 (0x9C40~0x9E34)
08. Power Grid Scheduling | 08_Grid_Scheduling | 208 | 42000~42911 (0xA410~0xA79F)
09. Communications & Network | 09_Comms_Network | 92 | 43000~43642 (0xA7F8~0xAA7A)
10. Tracker / Feature Params | 10_Tracker_Feature | 92 | 44000~45040 (0xABE0~0xAFF0)
11. Energy Storage / Battery | 11_EnergyStorage | 64 | 47001~48090 (0xB799~0xBBDA)
TOTAL |  | 846
▼ Appendix Definition Tables
알람 정보 (Table 5-1) | A1_Alarm_Info | 41
cosφ-P/Pn 특성 곡선 (Table 5-2) | A2_cosφ_P_Curve | 34
Q-U 특성 곡선 (Table 5-3) | A3_Q_U_Curve | 21
PF-U 특성 곡선 (Table 5-4) | A4_PF_U_Curve | 21
계통 코드 목록 (Table 5-5) | A5_Grid_Codes | 273
에너지저장 TOU 전기요금 (Table 5-6) | A6_ES_TOU_Periods | 11
에너지저장 고정충방전 (Table 5-7) | A7_ES_Fixed_Periods | 11
옵티마이저 시스템 정보 (4.1) | A8_Optimizer_SysInfo | 4
옵티마이저 실시간 데이터 (4.2) | A9_Optimizer_Realtime | 33

## 01_DeviceInfo
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
1 | Mod el | RO | STR |  |  | 0x7530 | 30000 | 15 | Nameplate name of the machine, original "model name"
2 | SN | RO | STR |  |  | 0x753F | 30015 | 10 | Device SN, which is obtained from the electronic label of the entire system.
3 | PN | RO | STR |  |  | 0x7549 | 30025 | 10 | Product Code
4 | Firm ware Versi on | RO | STR |  |  | 0x7553 | 30035 | 15 | Character string reporting: initial version VX00R00X (default VR version) VX00R00XD01, VX00R00XD02... (D0X is provided by the test and certification personnel.) Different country codes may be displayed differently.
5 | Soft ware versi on | RO | STR |  |  | 0x7562 | 30050 | 15 | In V800R021C10SPCXXX, the offering name and software version are displayed on the display page.
6 | Prot ocol versi on [Mo dbus ] | RO | U32 |  |  | 0x7574 | 30068 | 2 | high-character: main version; Upgrade on Incompatible Changes low-letter: revision; Compatible upgrade The baseline version is D8.0. 0x00080000
7 | Mod el ID | RO | U16 |  |  | 0x7576 | 30070 | 1 | Model ID. For details, see the Inverter Model Definition.xlsm.
8 | Num ber of PV strin gs | RO | U16 |  | 1 | 0x7577 | 30071 | 1
9 | Num ber of MPP Ts | RO | U16 |  | 1 | 0x7578 | 30072 | 1
10 | Rate d pow er | RO | U32 | k W | 1000 | 0x7579 | 30073 | 2 | Pn
11 | Maxi mu m activ e pow er (Pm ax) | RO | U32 | k W | 1000 | 0x757B | 30075 | 2 | Read-only interface to 42027
12 | Maxi mu m appa rent (Sm ax) | RO | U32 | kV A | 1000 | 0x757D | 30077 | 2 | Read-only interface to 42025
13 | Real - time maxi mu m react ive pow er (Qm ax, fed to the pow er grid) | RO | I32 | kV ar | 1000 | 0x757F | 30079 | 2 | Reported to the monitoring, indicating the reactive power adjustment range. Feature data is updated when the power grid standard code and derating change except for model differences.
14 | Real - time maxi mu m react ive pow er (- Qma x, abso rbed from the pow er grid) | RO | I32 | kV ar | 1000 | 0x7581 | 30081 | 2 | Reported to the monitoring, indicating the reactive power adjustment range. Feature data is updated when the power grid standard code and derating change except for model differences.
15 | Maxi mu m activ e pow er (Pm ax_r eal) | RO | U32 | k W | 1000 | 0x7583 | 30083 | 2 | The default maximum active power capacity is fixed on the nameplate of the machine, and the maximum active power capacity will not change for one machine. as a set upper limit for the reference range (42027); The relationship is as follows: 0<Pmax≤Smax≤Pmax_real≤S max_real Or the 0<Pmax≤Pmax_real≤Smax≤S max_real
16 | Maxi mu m appa rent capa bility (Sm ax_r eal) | RO | U32 | kV A | 1000 | 0x7585 | 30085 | 2 | The default apparent maximum capacity value is fixed on the machine nameplate, and one machine will not change. as a set upper limit for the reference range (42025); The relationship is as follows: 0<Pmax≤Smax≤Pmax_real≤S max_real Or the 0<Pmax≤Pmax_real≤Smax≤S max_real
17 | Prod uct sales area | RO | STR |  |  | 0x7599 | 30105 | 2 | XX: Two uppercase letters, indicating the sales area or application area of the product, mainly related to the AC power system. CN: Chinese mainland; EU: Europe; JP: Japan; US: North America (US/ Canada/and regions with the same grid or certification requirements as the US); UK: United Kingdom; Default value: CN/EU: All areas where CE certification requirements are applicable. Huawei FusionSolar Smart PV Solution and Product Naming Specifications
18 | Prod uct soft ware ID | RO | U16 |  |  | 0x759B | 30107 | 1 | Unique ID of the software publishing entity. Used for processing the compatibility of the power grid standard code.
19 | Prod uct Soft ware Versi on Num ber | RO | U16 |  |  | 0x759C | 30108 | 1 | Software release entity specific release version sequence number Used to process the compatibility of the power grid standard code.
20 | Pow er Grid Stan dard Code Prot ocol Versi on | RO | U16 |  |  | 0x759D | 30109 | 1 | Protocol loading and verification is similar to CAN1.0 and CAN2.0.
21 | Uniq ue ID of the soft ware . | RO | U16 |  |  | 0x759E | 30110 | 1 | Unique ID of a software version. Upgrade packages with different IDs cannot be upgraded to each other. (Broadcast Upgrade Signature)
22 | Num ber of upgr ade pack ages | RO | U16 |  | 1 | 0x759F | 30111 | 1 | The number of upgrade packages must be sufficient because more and more devices need to be upgraded.
23 | Infor mati on abou t subp acka ge 1 | RO | U32 |  |  | 0x75A0 | 30112 | 2 | high-character: file type ID; Low character: device type ID.
24 | Subp acka ge 2 infor mati on | RO | U32 |  |  | 0x75A2 | 30114 | 2 | high-character: file type ID; Low character: device type ID.
25 | Infor mati on abou t subp acka ge 3 | RO | U32 |  |  | 0x75A4 | 30116 | 2 | high-character: file type ID; Low character: device type ID.
26 | Subp acka ge 4 infor mati on | RO | U32 |  |  | 0x75A6 | 30118 | 2 | high-character: file type ID; Low character: device type ID.
27 | Subp acka ge 5 infor mati on | RO | U32 |  |  | 0x75A8 | 30120 | 2 | high-character: file type ID; Low character: device type ID.
28 | Infor mati on abou t subp acka ge 6 | RO | U32 |  |  | 0x75AA | 30122 | 2 | high-character: file type ID; Low character: device type ID.
29 | Subp acka ge 7 infor mati on | RO | U32 |  |  | 0x75AC | 30124 | 2 | high-character: file type ID; Low character: device type ID.
30 | Subp acka ge 8 infor mati on | RO | U32 |  |  | 0x75AE | 30126 | 2 | high-character: file type ID; Low character: device type ID.
31 | Subp acka ge 9 infor mati on | RO | U32 |  |  | 0x75B0 | 30128 | 2 | high-character: file type ID; Low character: device type ID.
32 | Infor mati on abou t subp acka ge 10 | RO | U32 |  |  | 0x75B2 | 30130 | 2 | high-character: file type ID; Low character: device type ID.
33 | [Thir d- part y label ing] SN | RO | STR |  |  | 0x75EF | 30191 | 10 | Serial number of third-party OEM equipment, customized by third-party manufacturers

## 02_DeviceInfo_Ext
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
34 | [Thir d- part y label ] Man ufact urer mod el | RO | U16 |  |  | 0x75F9 | 30201 | 1 | Model of third-party OEM equipment manufacturer
35 | Subd evice Supp ort ID | RO | Bitfield32 |  |  | 0x75FF | 30207 | 2
36 | Subd evice pres ence flag. | RO | Bitfield32 |  |  | 0x7601 | 30209 | 2
37 | Num ber of uniq ue sout hbou nd soft ware IDs | RO | U16 |  | 1 | 0x7724 | 30500 | 1 | Total number of southbound components that have independent upgrade packages. Note: This flag corresponds to the EquipChrtCode in the upgrade package. For details, see the Inverter Key Signal Extended Description-Monitoring Model Mapping.
38 | Uniq ue ID 1 of the sout hbou nd soft ware . | RO | U16 |  |  | 0x7725 | 30501 | 1
39 | Uniq ue ID 2 of the sout hbou nd soft ware | RO | U16 |  |  | 0x7726 | 30502 | 1
40 | Num ber of upgr ade pack ages for sout hbou nd devic e 1 | RO | U16 |  | 1 | 0x772A | 30506 | 1
41 | Infor mati on abou t subp acka ge 1 of sout hbou nd devic e 1 | RO | U32 |  |  | 0x772B | 30507 | 2 | high-character: file type ID; Low character: device type ID.
42 | Infor mati on abou t subp acka ge 2 of sout hbou nd devic e 1 | RO | U32 |  |  | 0x772D | 30509 | 2 | high-character: file type ID; Low character: device type ID.
43 | Infor mati on abou t subp acka ge 3 of sout hbou nd devic e 1 | RO | U32 |  |  | 0x772F | 30511 | 2 | high-character: file type ID; Low character: device type ID.
44 | Num ber of upgr ade pack ages for sout hbou nd devic e 2 | RO | U16 |  | 1 | 0x7735 | 30517 | 1
45 | Infor mati on abou t subp acka ge 1 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x7736 | 30518 | 2 | high-character: file type ID; Low character: device type ID.
46 | Infor mati on abou t subp acka ge 2 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x7738 | 30520 | 2 | high-character: file type ID; Low character: device type ID.
47 | Infor mati on abou t subp acka ge 3 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x773A | 30522 | 2 | high-character: file type ID; Low character: device type ID.
48 | Infor mati on abou t subp acka ge 4 of sout hbou nd devic e 2 | RO | U32 |  |  | 0x773C | 30524 | 2 | high-character: file type ID; Low character: device type ID.
49 | Offe ring nam e of sout hbou nd devic e 1 | RO | STR |  |  | 0x7761 | 30561 | 15 | Distributed inverter southbound device identification: Southbound device 1: optimizer
50 | Offe ring nam e of sout hbou nd devic e 2 | RO | STR |  |  | 0x7770 | 30576 | 15 | Distributed inverter southbound device identification: Southbound device 2: DC- MBUS
51 | Offe ring nam e of sout hbou nd devic e 3. | RO | STR |  |  | 0x777F | 30591 | 15 | Distributed inverter southbound device identification: Southbound device 3: LUNA2000 1.0

## 03_Subdevice
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
52 | Hard ware versi on | RO | STR |  | 1 | 0x7918 | 31000 | 15
53 | Mon itori ng Boar d SN | RO | STR |  |  | 0x7927 | 31015 | 10 | From the electronic label of the monitoring board
54 | Mon itori ng soft ware versi on | RO | STR |  |  | 0x7931 | 31025 | 15 | MCU1 version
55 | Main DSP versi on | RO | STR |  |  | 0x7940 | 31040 | 15 | MCU2 version
56 | CPL D versi on num ber | RO | STR |  |  | 0x795E | 31070 | 15 | MCU4 version
57 | AFCI versi on num ber | RO | STR |  |  | 0x796D | 31085 | 15 | MCU5 version
58 | DC- MBU S versi on num ber | RO | STR |  |  | 0x798B | 31115 | 15 | MCU7 version
59 | Regi strati on code | RO | STR |  | 1 | 0x79E0 | 31200 | 10

## 04_Status_Alarms
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
60 | [Re mot e com mun icati on] Singl e- node rem ote com mun icati on | RO | Bitfield16 |  |  | 0x7D00 | 32000 | 1 | Reported by IEC104, which indicates the merged PCS running status.
61 | [Re mot e sign al] Run ning statu s (mo nitor ing) | RO | Bitfield16 |  |  | 0x7D02 | 32002 | 1
62 | [Re mot e sign al] Run ning statu s (po wer proc essin g) | RO | Bitfield32 |  | 1 | 0x7D03 | 32003 | 2
63 | [Re mot e sign al] Alar m 1 | RO | Bitfield16 |  |  | 0x7D08 | 32008 | 1 | For details, see the Alarm Mapping sheet.
64 | [Re mot e sign al] Alar m 2 | RO | Bitfield16 |  |  | 0x7D09 | 32009 | 1 | For details, see the Alarm Mapping sheet.
65 | [Re mot e sign al] Alar m 3 | RO | Bitfield16 |  |  | 0x7D0A | 32010 | 1 | For details, see the Alarm Mapping sheet.
66 | [Re mot e sign al] Alar m 4 | RO | Bitfield16 |  |  | 0x7D0B | 32011 | 1 | For details, see the Alarm Mapping sheet.
67 | [Re mot e sign al] Alar m 5 | RO | Bitfield16 |  |  | 0x7D0C | 32012 | 1 | For details, see the Alarm Mapping sheet.
68 | [Re mot e sign al] Alar m 6 | RO | Bitfield16 |  |  | 0x7D0D | 32013 | 1 | For details, see the Alarm Mapping sheet.
69 | Devi ce SN feat ure code | RO | U16 |  |  | 0x7D0F | 32015 | 1 | Indicates the CRC16 value of the SN, which is the key data ID. Used to prevent incorrect energy yield from being modified due to incorrect energy yield reported by devices with the same address. The SN CRC is added to ensure that the energy yield source is correct.
70 | PV1 volta ge | RO | I16 | V | 10 | 0x7D10 | 32016 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV1 voltage. When bit 9 of the power parameter mask 14 is 1, the processing logic is as follows: When DC Input Display Mode 30205 is set to 0, the signal name is PV1 Voltage. When DC input 30205 is set to 1, the signal name is MPPT1 Voltage.
71 | PV1 curre nt | RO | I16 | A | 100 | 0x7D11 | 32017 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV1 current. When bit 9 of power parameter mask 14 is 1, the following logic is used: When DC input display mode 30205 is set to 0, the signal name is PV1 current. When DC Input Display Mode 30205 is set to 1, the signal name is MPPT1 Current.
72 | PV2 Volt age | RO | I16 | V | 10 | 0x7D12 | 32018 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV2 voltage. When bit 9 of the power parameter mask 14 is 1, the processing logic is as follows: When DC Input Display Mode 30205 is set to 0, the signal name is PV2 Voltage. When DC input 30205 is set to 1, the signal name is MPPT2 Voltage.
73 | PV2 curre nt | RO | I16 | A | 100 | 0x7D13 | 32019 | 1 | When bit 9 of power parameter mask 14 is 0, the signal name is PV2 current. When bit 9 of the power parameter mask 14 is 1, the following logic is used: When DC Input Display Mode 30205 is set to 0, the signal name is PV2 Current. When DC input display mode 30205 is set to 1, the signal name is MPPT2 current.
74 | PV3 Volt age | RO | I16 | V | 10 | 0x7D14 | 32020 | 1
75 | PV3 curre nt | RO | I16 | A | 100 | 0x7D15 | 32021 | 1
76 | PV4 Volt age | RO | I16 | V | 10 | 0x7D16 | 32022 | 1
77 | PV4 curre nt | RO | I16 | A | 100 | 0x7D17 | 32023 | 1
78 | PV5 volta ge | RO | I16 | V | 10 | 0x7D18 | 32024 | 1
79 | PV5 curre nt | RO | I16 | A | 100 | 0x7D19 | 32025 | 1
80 | PV6 volta ge | RO | I16 | V | 10 | 0x7D1A | 32026 | 1
81 | PV6 curre nt | RO | I16 | A | 100 | 0x7D1B | 32027 | 1
82 | PV7 Volt age | RO | I16 | V | 10 | 0x7D1C | 32028 | 1
83 | PV7 curre nt | RO | I16 | A | 100 | 0x7D1D | 32029 | 1
84 | PV8 Volt age | RO | I16 | V | 10 | 0x7D1E | 32030 | 1
85 | PV8 curre nt | RO | I16 | A | 100 | 0x7D1F | 32031 | 1
86 | DC pow er | RO | I32 | k W | 1000 | 0x7D40 | 32064 | 2
87 | Pow er grid line A and B volta ge | RO | U16 | V | 10 | 0x7D42 | 32066 | 1 | When the output mode is L/N, the signal name is Grid Voltage. When Output Mode is set to L1/L2/N or L1/L2, the signal name is UW Grid Voltage.
88 | Pow er grid B/C line volta ge | RO | U16 | V | 10 | 0x7D43 | 32067 | 1 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
89 | Pow er grid CA line volta ge | RO | U16 | V | 10 | 0x7D44 | 32068 | 1 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
90 | Pow er grid phas e A volta ge | RO | U16 | V | 10 | 0x7D45 | 32069 | 1 | This parameter is invalid when the output mode is L/N. When Output Mode is set to L1/L2/N or L1/L2, the signal name is UO Grid Voltage. Not displayed in off-grid mode
91 | Pow er grid phas e B volta ge | RO | U16 | V | 10 | 0x7D46 | 32070 | 1 | This parameter is invalid when the output mode is L/N. When Output Mode is set to L1/L2/N or L1/L2, the signal name is WO Grid Voltage. Not displayed in off-grid mode
92 | Pow er grid phas e C volta ge | RO | U16 | V | 10 | 0x7D47 | 32071 | 1 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
93 | Pow er grid phas e A curre nt | RO | I32 | A | 1000 | 0x7D48 | 32072 | 2 | When the output mode is L/N, L1/L2/N, or L1/L2, the signal name is Grid Current.
94 | Pow er grid phas e B curre nt | RO | I32 | A | 1000 | 0x7D4A | 32074 | 2 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
95 | Pow er grid phas e C curre nt | RO | I32 | A | 1000 | 0x7D4C | 32076 | 2 | This parameter is invalid when the output mode is L/N, L1/L2/N, or L1/L2.
96 | Peak activ e pow er of the curre nt day | RO | I32 | k W | 1000 | 0x7D4E | 32078 | 2
97 | Activ e pow er | RO | I32 | k W | 1000 | 0x7D50 | 32080 | 2
98 | react ive pow er | RO | I32 | kV ar | 1000 | 0x7D52 | 32082 | 2
99 | Pow er facto r | RO | I16 |  | 1000 | 0x7D54 | 32084 | 1
100 | Grid freq uenc y | RO | U16 | Hz | 100 | 0x7D55 | 32085 | 1
101 | Inver ter effici ency | RO | U16 | % | 100 | 0x7D56 | 32086 | 1 | When PCS is used to generate power, it indicates the power generation efficiency. When PCS is used to absorb, it indicates the absorption efficiency.
102 | Inter nal tem pera ture | RO | I16 | °C | 10 | 0x7D57 | 32087 | 1
103 | Insul atio n impe danc e | RO | U16 | M Ω | 1000 | 0x7D58 | 32088 | 1
104 | Devi ce Stat us | RO | U16 |  |  | 0x7D59 | 32089 | 1 | 0x0000 Standby: initializing 0x0001 Standby: detecting insulation resistance 0x0002 Standby: detecting irradiation 0x0003 Standby: drid detecting 0x0100 Starting 0x0200 On-grid 0x0201 Grid connection: power limited 0x0202 Grid connection: self-derating 0x0300 Shutdown: fault 0x0301 Shutdown: command 0x0302 Shutdown: OVGR 0x0303 Shutdown: communication disconnected 0x0304 Shutdown: power limited 0x0305 Shutdown: manual startup required 0x0307 Shutdown: rapid cutoff 0x0401 Grid scheduling: cosφ-P curve 0x0402 Grid scheduling: Q- U curve 0x0403 Grid scheduling: PF- U curve 0x0404 Grid scheduling: dry contact 0x0405 Grid scheduling: Q-P curve 0x0500 Spot-check ready 0x0501 Spot-checking 0x0600 Inspecting 0X0700 AFCI self check 0X0800 I-V scanning 0xA000 Standby: no irradiation
105 | Fault Code | RO | U16 |  |  | 0x7D5A | 32090 | 1 | Fault code corresponding to the alarm with the highest priority. For details, see the Alarm Description sheet.
106 | Start -up time | RO | EpochSecond | s | 1 | 0x7D5B | 32091 | 2 | Monitoring Calculation
107 | Shut dow n time | RO | EpochSecond | s | 1 | 0x7D5D | 32093 | 2 | Monitoring Calculation
108 | Activ e pow er [fast ] | RO | I32 | k W | 1000 | 0x7D5F | 32095 | 2 | Fast reporting interface, which is not filtered and used for scheduling energy storage.
109 | Accu mula ted pow er gene ratio n | RO | U32 | k W h | 100 | 0x7D6A | 32106 | 2
110 | Total DC Inpu t Pow er | RO | U32 | k W h | 100 | 0x7D6C | 32108 | 2
111 | Stati stica l time of the curre nt ener gy yield . | RO | EpochSecond | s | 1 | 0x7D6E | 32110 | 2
112 | Curr ent Hour Elect ricity | RO | U32 | k W h | 100 | 0x7D70 | 32112 | 2
113 | Curr ent- day pow er gene ratio n | RO | U32 | k W h | 100 | 0x7D72 | 32114 | 2
114 | Elect ricity gene rate d in the curre nt mon th | RO | U32 | k W h | 100 | 0x7D74 | 32116 | 2
115 | Elect ricity gene rate d in the curre nt year | RO | U32 | k W h | 100 | 0x7D76 | 32118 | 2
116 | Num ber of critic al alar ms | RO | U16 |  | 1 | 0x7D97 | 32151 | 1
117 | Num ber of majo r alar ms | RO | U16 |  | 1 | 0x7D98 | 32152 | 1
118 | Num ber of Min or Alar ms | RO | U16 |  | 1 | 0x7D99 | 32153 | 1
119 | Num ber of War ning Alar ms | RO | U16 |  | 1 | 0x7D9A | 32154 | 1
120 | Alar m clear ance SN | RO | U16 |  |  | 0x7D9B | 32155 | 1 | After the alarm is cleared, the serial number increases by 1. After the alarm is reversed, the serial number starts from 1 and skips 0.
121 | Last Hour Pow er Stati stics Time | RO | EpochSecond | s | 1 | 0x7D9C | 32156 | 2 | include generate/absorbed power
122 | Elect ricity gene rate d in the previ ous hour | RO | U32 | k W h | 100 | 0x7D9E | 32158 | 2
123 | Elect ricity stati stics time of the previ ous day | RO | EpochSecond | s | 1 | 0x7DA0 | 32160 | 2 | include generate/absorbed power
124 | Elect ricity gene rate d in the previ ous day | RO | U32 | k W h | 100 | 0x7DA2 | 32162 | 2
125 | Stati stica l time of the previ ous mon th. | RO | EpochSecond | s | 1 | 0x7DA4 | 32164 | 2 | include generate/absorbed power
126 | Elect ricity gene rate d in the previ ous mon th | RO | U32 | k W h | 100 | 0x7DA6 | 32166 | 2
127 | Elect ricity stati stics time of the previ ous year | RO | EpochSecond | s | 1 | 0x7DA8 | 32168 | 2 | include generate/absorbed power
128 | Elect ricity gene rate d in the previ ous year | RO | U32 | k W h | 100 | 0x7DAA | 32170 | 2
129 | Seria l num ber of the lates t activ e alar m. | RO | U32 |  |  | 0x7DAC | 32172 | 2 | When a new active alarm is generated, the serial number increases by 1.
130 | Late st Hist orica l Alar m Seria l Num ber | RO | U32 |  |  | 0x7DAE | 32174 | 2 | When an active alarm is transferred to the historical alarm, the serial number of the historical alarm is the same as the serial number of the last active alarm transferred to the historical alarm.
131 | Total bus volta ge | RO | I16 | V | 10 | 0x7DB0 | 32176 | 1 | Data reported by PID, used in single-level scenarios
132 | Maxi mu m PV volta ge | RO | I16 | V | 10 | 0x7DB1 | 32177 | 1 | Data reported by PID, used in single-level scenarios
133 | Mini mu m PV volta ge | RO | I16 | V | 10 | 0x7DB2 | 32178 | 1 | Data reported by PID, used in single-level scenarios
134 | Aver age PV nega tive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DB3 | 32179 | 1 | Data reported by PID, used in single-level scenarios
135 | Maxi mu m PV posit ive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DB4 | 32180 | 1 | Data reported by PID, used in single-level scenarios
136 | Mini mu m PV nega tive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DB5 | 32181 | 1 | Data reported by PID, used in single-level scenarios
137 | Inver ter- to- PE with stan d volta ge | RO | U16 | V | 1 | 0x7DB6 | 32182 | 1 | Data reported by PID, used in single-level scenarios To be compatible with PID 2.0, the PCS reports 1502. 0:100 V or 1100 V inverter; 1500: HAV1 inverter; 1502: HAV2 inverter;
138 | ISO feat ure infor mati on | RO | Bitfield16 |  | 1 | 0x7DB7 | 32183 | 1 | Data reported by PID, used in single-level scenarios
139 | Built -in PID runn ing statu s | RO | E16 |  |  | 0x7DBE | 32190 | 1
140 | PV nega tive- to- grou nd volta ge | RO | I16 | V | 10 | 0x7DBF | 32191 | 1
141 | Dire ction of the built -in PID com pens atio n | RO | E16 |  |  | 0x7DC0 | 32192 | 1
142 | Total DC ener gy yield of MPP T1 | RO | U32 | k W h | 100 | 0x7DD4 | 32212 | 2 | TD Tech NMS GUI Display [5/4]
143 | Total DC ener gy yield of MPP T2 | RO | U32 | k W h | 100 | 0x7DD6 | 32214 | 2 | TD Tech NMS GUI Display [5/4]
144 | MPP T3 DC Total Ener gy Yield | RO | U32 | k W h | 100 | 0x7DD8 | 32216 | 2 | TD Tech NMS GUI Display [5/4]
145 | MPP T4 DC Accu mula ted Ener gy Yield | RO | U32 | k W h | 100 | 0x7DDA | 32218 | 2 | TD Tech NMS GUI Display [5/4]
146 | Mon itori ng alar m 1 | RO | Bitfield16 |  |  | 0x7DFC | 32252 | 1 | GroupID:0xFF00
147 | Mon itori ng alar m 2 | RO | Bitfield16 |  |  | 0x7DFD | 32253 | 1 | GroupID:0xFF01
148 | Mon itor alar m 3 | RO | Bitfield16 |  |  | 0x7DFE | 32254 | 1 | GroupID:0xFF02
149 | [Exte rnal] Pow er alar m 1 | RO | Bitfield16 |  |  | 0x7DFF | 32255 | 1 | GroupID:0x0000
150 | [Exte rnal] Pow er alar m 2 | RO | Bitfield16 |  |  | 0x7E00 | 32256 | 1 | GroupID:0x0001
151 | [Exte rnal] Pow er alar m 3 | RO | Bitfield16 |  |  | 0x7E01 | 32257 | 1 | GroupID:0x0002
152 | [Exte rnal] Pow er alar m 4 | RO | Bitfield16 |  |  | 0x7E02 | 32258 | 1 | GroupID:0x0003
153 | [Exte rnal] Pow er alar m 5 | RO | Bitfield16 |  |  | 0x7E03 | 32259 | 1 | GroupID:0x0004
154 | [Exte rnal] Pow er alar m 6 | RO | Bitfield16 |  |  | 0x7E04 | 32260 | 1 | GroupID:0x0005
155 | [Exte rnal] Pow er alar m 7 | RO | Bitfield16 |  |  | 0x7E05 | 32261 | 1 | GroupID:0x0006
156 | [Exte rnal] Pow er alar m 8 | RO | Bitfield16 |  |  | 0x7E06 | 32262 | 1 | GroupID:0x0007
157 | [Exte rnal] Pow er alar m 9 | RO | Bitfield16 |  |  | 0x7E07 | 32263 | 1 | GroupID:0x0008
158 | [Exte rnal] Pow er alar m 10 | RO | Bitfield16 |  |  | 0x7E08 | 32264 | 1 | GroupID:0x0009
159 | [Exte rnal] Pow er alar m 11 | RO | Bitfield16 |  |  | 0x7E09 | 32265 | 1 | GroupID:0x000A
160 | [Exte rnal] Pow er alar m 12 | RO | Bitfield16 |  |  | 0x7E0A | 32266 | 1 | GroupID:0x000B
161 | [Exte rnal] Pow er alar m 13 | RO | Bitfield16 |  |  | 0x7E0B | 32267 | 1 | GroupID:0x000C
162 | [Exte rnal] Pow er alar m 14 | RO | Bitfield16 |  |  | 0x7E0C | 32268 | 1 | GroupID:0x000D
163 | [Exte rnal] Pow er alar m 15 | RO | Bitfield16 |  |  | 0x7E0D | 32269 | 1 | GroupID:0x000E
164 | [Exte rnal] Pow er alar m 16 | RO | Bitfield16 |  |  | 0x7E0E | 32270 | 1 | GroupID:0x000F
165 | Mon itor alar m 4 | RO | Bitfield16 |  |  | 0x7E0F | 32271 | 1 | GroupID:0xFF03
166 | Mon itor alar m 5 | RO | Bitfield16 |  |  | 0x7E10 | 32272 | 1 | GroupID:0xFF04
167 | [Exte rnal] Pow er alar m 17 | RO | Bitfield16 |  |  | 0x7E11 | 32273 | 1 | GroupID:0x0010
168 | Strin g 1 acce ss statu s | RO | E16 |  |  | 0x7E2C | 32300 | 1
169 | Strin g 2 acce ss statu s | RO | E16 |  |  | 0x7E2D | 32301 | 1
170 | Strin g 3 acce ss statu s | RO | E16 |  |  | 0x7E2E | 32302 | 1
171 | Strin g 4 acce ss statu s | RO | E16 |  |  | 0x7E2F | 32303 | 1
172 | Strin g 5 acce ss statu s | RO | E16 |  |  | 0x7E30 | 32304 | 1
173 | Con necti on statu s of strin g 6 | RO | E16 |  |  | 0x7E31 | 32305 | 1
174 | Strin g 7 acce ss statu s | RO | E16 |  |  | 0x7E32 | 32306 | 1
175 | Strin g 8 acce ss statu s | RO | E16 |  |  | 0x7E33 | 32307 | 1

## 05_Realtime
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
304 | Upgr ade statu s ID. | RO | E16 |  |  | 0x8CC1 | 36033 | 1 | The flag is cleared each time the system is powered on. After the upgrade is successful, the flag is set to 1, indicating that the upgrade is successful and no abnormal restart occurs.
305 | [Mo dule 1] Run ning statu s of the batt ery | RO | E16 |  |  | 0x9088 | 37000 | 1
306 | Met er Stat us | RO | E16 |  |  | 0x90EC | 37100 | 1
307 | Grid volta ge (pha se A volta ge) | RO | I32 | V | 10 | 0x90ED | 37101 | 2
308 | Phas e B volta ge | RO | I32 | V | 10 | 0x90EF | 37103 | 2
309 | Phas e C volta ge | RO | I32 | V | 10 | 0x90F1 | 37105 | 2
310 | Grid curre nt (pha se A curre nt) | RO | I32 | A | 100 | 0x90F3 | 37107 | 2
311 | Phas e B curre nt | RO | I32 | A | 100 | 0x90F5 | 37109 | 2
312 | Phas e C curre nt | RO | I32 | A | 100 | 0x90F7 | 37111 | 2
313 | Activ e pow er | RO | I32 | W | 1 | 0x90F9 | 37113 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
314 | react ive pow er | RO | I32 | Va r | 1 | 0x90FB | 37115 | 2
315 | Pow er facto r | RO | I16 |  | 1000 | 0x90FD | 37117 | 1
316 | Grid freq uenc y | RO | I16 | Hz | 100 | 0x90FE | 37118 | 1
317 | Posit ive activ e pow er | RO | I32 | k W h | 100 | 0x90FF | 37119 | 2 | Inverter power fed to the grid
318 | Reve rse activ e pow er | RO | I32 | k W h | 100 | 0x9101 | 37121 | 2 | Electricity absorbed by the distributed system from the grid
319 | Accu mula ted react ive pow er | RO | I32 | kV ar h | 100 | 0x9103 | 37123 | 2
320 | Met er Type | RO | E16 |  |  | 0x9105 | 37125 | 1
321 | A-B line volta ge | RO | I32 | V | 10 | 0x9106 | 37126 | 2
322 | BC line volta ge | RO | I32 | V | 10 | 0x9108 | 37128 | 2
323 | CA line volta ge | RO | I32 | V | 10 | 0x910A | 37130 | 2
324 | Phas e A activ e pow er | RO | I32 | W | 1 | 0x910C | 37132 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
325 | Phas e B activ e pow er | RO | I32 | W | 1 | 0x910E | 37134 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
326 | Phas e C activ e pow er | RO | I32 | W | 1 | 0x9110 | 37136 | 2 | > 0: feeds power to the power grid; < 0: obtains power from the power grid.
327 | Met er Mod el Chec k Resu lt | RO | E16 |  |  | 0x9112 | 37138 | 1
328 | Total num ber of opti mize rs | RO | U16 |  | 1 | 0x9150 | 37200 | 1
329 | Num ber of onlin e opti mize rs | RO | U16 |  | 1 | 0x9151 | 37201 | 1
330 | Feat ure data sequ ence num ber | RO | U16 |  | 1 | 0x9152 | 37202 | 1
331 | Phys ical Loca tion Loca ting Prog ress | RO | E16 |  |  | 0x9153 | 37203 | 1
332 | Log expo rt prog ress | RO | E16 |  |  | 0x9154 | 37204 | 1
333 | Real - time data quer y prog ress | RO | E16 |  |  | 0x9155 | 37205 | 1
334 | Curr ent statu s of the phys ical locat ion | RO | E16 |  |  | 0x9156 | 37206 | 1
335 | Num ber of Sear ched Opti mize rs | RO | U16 |  | 1 | 0x9157 | 37207 | 1
336 | Rela tive Posit ionin g Stat us | RO | E16 |  |  | 0x9158 | 37208 | 1 | The previous result needs to be solidified and retained after a power failure.
337 | Layo ut File Stor age Prog ress | RO | U16 | % | 1 | 0x9159 | 37209 | 1 | 0xffff: indicates that saving the data fails.
338 | Layo ut File Cha nge SN | RO | U16 |  | 1 | 0x915A | 37210 | 1
339 | Disc onne ction dete ction prog ress | RO | U16 | % | 1 | 0x915B | 37211 | 1 | Other values are error codes. Error code definitions are as follows: 0xfe02: Off-grid running, operation forbidden 0xfe03: The equipment test is being performed and the operation is forbidden. 0xfe04: The optimizer is searching. Please try again later. 0xfe05: The optimizer is identifying a long PV string. Try again later. 0xfe07: Exporting optimizer logs is in progress. Please try again later. 0xfe08: The fast shutdown is triggered and the operation is disabled. 0xfe09: No illumination at night or all optimizers are offline. 0xfff0: No optimizer is configured or the optimizer is configured. The operation is disabled. 0xfff1: The illumination is weak. If the illumination is normal, perform the disconnection detection function again. 0xfff2: The output voltage of the optimizer is abnormal. Perform the disconnection locating function again.
340 | Disc onne cted statu s | RO | E16 |  |  | 0x915C | 37212 | 1
341 | [DC- MBU S] Net work ing statu s | RO | E16 |  |  | 0x9182 | 37250 | 1
342 | Num ber of Net work ed Net work s | RO | U16 |  |  | 0x9183 | 37251 | 1
343 | Num ber of neig hbor ing netw orks | RO | U16 |  |  | 0x9184 | 37252 | 1
344 | Fast Shut dow n Self Test Stat us | RO | E16 |  |  | 0x9185 | 37253 | 1 | 0: not executed, indicating that the system life cycle has never been executed. The previous result needs to be solidified and retained after a power failure.
345 | Run ning statu s | RO | E16 |  |  | 0x9186 | 37254 | 1
346 | SN | RO | STR |  |  | 0x9187 | 37255 | 10
347 | SN | RO | STR |  | 1 | 0x9218 | 37400 | 10
348 | Type | RO | E16 |  |  | 0x9222 | 37410 | 1
349 | Maxi mu m num ber of conn ecte d devic es | RO | U16 |  | 1 | 0x9235 | 37429 | 1
350 | RAT | RO | STR |  | 1 | 0x9236 | 37430 | 10
351 | Carri ers | RO | STR |  | 1 | 0x9240 | 37440 | 15 | The default value is reported when no query is found.
352 | Total rate d capa city of grid- tied inver ters | RO | U32 | k W | 1000 | 0x925E | 37470 | 2 | Difference from plant capacity: refers only to the total capacity of online grid- tied inverters.
353 | Conv ersio n facto r | RO | U32 |  | 1000 | 0x9260 | 37472 | 2 | Percentage of current control/percentage of control delivered by the electric power company
354 | Curr ent Perc enta ge | RO | U16 | % | 10 | 0x9262 | 37474 | 1
355 | [Sch edul e serv er] Com mun icati on statu s | RO | E16 |  |  | 0x9263 | 37475 | 1 | Dongle and Japan Electric Power Huawei server communication status (only for third-party NMSs in Japan): Dispatching server: intelligence distribution, intelligence distribution, intelligence distribution, and information distribution
356 | [Sch edul e serv er] Late st conn ectio n statu s | RO | E16 |  |  | 0x9264 | 37476 | 1
357 | [Sch edul e serv er] Late st conn ectio n time | RO | U32 |  |  | 0x9265 | 37477 | 2
358 | Soft ware versi on | RO | STR |  |  | 0x9267 | 37479 | 15 | Dongle firmware version
359 | Num ber of conn ecte d devic es | RO | U16 |  |  | 0x9276 | 37494 | 1
360 | Silen ce flag | RO | E16 |  |  | 0x9278 | 37496 | 1 | Note: This API is used only to synchronize dongle silence between the mobile app and inverter. Wait for the dongle to exit bus control in silence. Only the mobile phone app can initiate a request to the slave UPS in parallel mode.
361 | Upgr ade Stat us | RO | E16 |  |  | 0x9279 | 37497 | 1
362 | Inver ter com preh ensiv e statu s | RO | Bitfield16 |  |  | 0x928E | 37518 | 1
363 | Inver ter integ rate d statu s supp ort flag | RO | U16 |  | 1 | 0x928F | 37519 | 1

## 06_PV_String
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
176 | Sten t Syst em Stat us | RO | Bitfield32 |  |  | 0x84D0 | 34000 | 2 | BIT0–BIT15: state of support system 1–16; BIT16–BIT31: reserved for future expansion.
177 | Tilt angl e 1 sam pling | RO | I16 | ° | 100 | 0x84D2 | 34002 | 1
178 | Azim uth 1 sam pling | RO | I16 | ° | 100 | 0x84D3 | 34003 | 1
179 | Tilt angl e 2 sam pling | RO | I16 | ° | 100 | 0x84D4 | 34004 | 1
180 | Azim uth 2 sam pling | RO | I16 | ° | 100 | 0x84D5 | 34005 | 1
181 | Tilt angl e 3 sam pling | RO | I16 | ° | 100 | 0x84D6 | 34006 | 1
182 | Azim uth 3 sam pling | RO | I16 | ° | 100 | 0x84D7 | 34007 | 1
183 | Tilt angl e 4 sam pling | RO | I16 | ° | 100 | 0x84D8 | 34008 | 1
184 | Azim uth 4 sam pling | RO | I16 | ° | 100 | 0x84D9 | 34009 | 1
185 | Tilt angl e 5 sam pling | RO | I16 | ° | 100 | 0x84DA | 34010 | 1
186 | Azim uth 5 sam pling | RO | I16 | ° | 100 | 0x84DB | 34011 | 1
187 | Tilt angl e 6 sam pling | RO | I16 | ° | 100 | 0x84DC | 34012 | 1
188 | Azim uth 6 sam pling | RO | I16 | ° | 100 | 0x84DD | 34013 | 1
189 | Tilt angl e 7 sam pling | RO | I16 | ° | 100 | 0x84DE | 34014 | 1
190 | Azim uth 7 sam pling | RO | I16 | ° | 100 | 0x84DF | 34015 | 1
191 | Tilt angl e 8 sam pling | RO | I16 | ° | 100 | 0x84E0 | 34016 | 1
192 | Azim uth 8 sam pling | RO | I16 | ° | 100 | 0x84E1 | 34017 | 1
193 | Tilt angl e 9 sam pling | RO | I16 | ° | 100 | 0x84E2 | 34018 | 1
194 | Azim uth 9 sam pling | RO | I16 | ° | 100 | 0x84E3 | 34019 | 1
195 | Tilt angl e 10 sam pling | RO | I16 | ° | 100 | 0x84E4 | 34020 | 1
196 | Azim uth 10 sam pling | RO | I16 | ° | 100 | 0x84E5 | 34021 | 1
197 | Tilt angl e 11 sam pling | RO | I16 | ° | 100 | 0x84E6 | 34022 | 1
198 | Azim uth 11 sam pling | RO | I16 | ° | 100 | 0x84E7 | 34023 | 1
199 | Tilt angl e 12 sam pling | RO | I16 | ° | 100 | 0x84E8 | 34024 | 1
200 | Azim uth 12 sam pling | RO | I16 | ° | 100 | 0x84E9 | 34025 | 1
201 | Tilt angl e 13 sam pling | RO | I16 | ° | 100 | 0x84EA | 34026 | 1
202 | Beari ng 13 sam pling | RO | I16 | ° | 100 | 0x84EB | 34027 | 1
203 | Tilt angl e 14 sam pling | RO | I16 | ° | 100 | 0x84EC | 34028 | 1
204 | Azim uth 14 sam pling | RO | I16 | ° | 100 | 0x84ED | 34029 | 1
205 | Tilt angl e 15 sam pling | RO | I16 | ° | 100 | 0x84EE | 34030 | 1
206 | Beari ng angl e 15 sam pling | RO | I16 | ° | 100 | 0x84EF | 34031 | 1
207 | Tilt angl e 16 sam pling | RO | I16 | ° | 100 | 0x84F0 | 34032 | 1
208 | Beari ng 16 sam pling | RO | I16 | ° | 100 | 0x84F1 | 34033 | 1
209 | Trac king syste m cont rolle r | RO | E16 |  |  | 0x84F2 | 34034 | 1
210 | Supp ort Syst em Type | RO | E16 |  |  | 0x84F3 | 34035 | 1 | If the vendor does not support a support type, the system returns the 03 error code.
211 | Oper atin g mod e | RO | E16 |  |  | 0x84F4 | 34036 | 1
212 | Total num ber of stent s | RO | U16 |  | 1 | 0x84F5 | 34037 | 1 | For dual-axis control, the maximum number of supports is 8.
213 | Supp ort acce ss statu s | RO | Bitfield32 |  | 1 | 0x84F6 | 34038 | 2 | BIT0–BIT15: access status of support system 1–16; BIT16–BIT31: reserved for future expansion.
214 | Wor king mod e mas k | RO | Bitfield32 |  | 1 | 0x84F8 | 34040 | 2 | Each bit indicates whether a working mode is supported.
215 | Supp ort 1 Gen eral Fault Stat us | RO | E16 |  |  | 0x851B | 34075 | 1 | Data reported by the SmartLogger to the management system
216 | Supp ort 1 user- defin ed fault statu s | RO | U16 |  | 1 | 0x851C | 34076 | 1 | For details about the controller scenario definition, see the corresponding document. Data reported by the SmartLogger to the management system
217 | Supp ort 2 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x851D | 34077 | 1
218 | Supp ort 2 Cust om Fault Stat us | RO | U16 |  | 1 | 0x851E | 34078 | 1
219 | Supp ort 3 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x851F | 34079 | 1
220 | Supp ort 3 user- defin ed fault statu s | RO | U16 |  | 1 | 0x8520 | 34080 | 1
221 | Supp ort 4 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8521 | 34081 | 1
222 | Supp ort 4 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8522 | 34082 | 1
223 | Supp ort 5 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8523 | 34083 | 1
224 | Supp ort 5 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8524 | 34084 | 1
225 | Supp ort 6 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8525 | 34085 | 1
226 | Supp ort 6 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8526 | 34086 | 1
227 | Supp ort 7 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8527 | 34087 | 1
228 | Supp ort 7 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8528 | 34088 | 1
229 | Supp ort 8 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8529 | 34089 | 1
230 | Supp ort 8 Cust om Fault Stat us | RO | U16 |  | 1 | 0x852A | 34090 | 1
231 | Supp ort 9 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x852B | 34091 | 1
232 | Supp ort 9 Cust om Fault Stat us | RO | U16 |  | 1 | 0x852C | 34092 | 1
233 | Supp ort 10 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x852D | 34093 | 1
234 | Supp ort 10 Cust om Fault Stat us | RO | U16 |  | 1 | 0x852E | 34094 | 1
235 | Supp ort 11 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x852F | 34095 | 1
236 | Supp ort 11 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8530 | 34096 | 1
237 | Supp ort 12 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8531 | 34097 | 1
238 | Supp ort 12 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8532 | 34098 | 1
239 | Supp ort 13 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8533 | 34099 | 1
240 | Supp ort 13 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8534 | 34100 | 1
241 | Supp ort 14 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8535 | 34101 | 1
242 | Supp ort 14 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8536 | 34102 | 1
243 | Supp ort 15 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8537 | 34103 | 1
244 | Supp ort 15 Cust om Fault Stat us | RO | U16 |  | 1 | 0x8538 | 34104 | 1
245 | Supp ort 16 Gen eral Fault Stat us | RO | U16 |  | 1 | 0x8539 | 34105 | 1
246 | Supp ort 16 Cust om Fault Stat us | RO | U16 |  | 1 | 0x853A | 34106 | 1
247 | Run ning time of capa citor bank | RO | U32 | ho ur | 10 | 0x88B8 | 35000 | 2 | Used to inspect data.
248 | Inter nal fan 1 runn ing time | RO | U32 | ho ur | 10 | 0x88BA | 35002 | 2 | Used to inspect data.
249 | Inter nal alar m | RO | U16 | V | 1 | 0x88C2 | 35010 | 1 | Used for R&D data storage.
250 | Inter nal Tem pera ture 1 | RO | I16 | °C | 10 | 0x88CD | 35021 | 1 | Temperature of INV module A Used for R&D 5-minute data recording.
251 | Inter nal Tem pera ture 2 | RO | I16 | °C | 10 | 0x88CE | 35022 | 1 | Temperature of INV module B Used for R&D 5-minute data recording.
252 | Inter nal Tem pera ture 3 | RO | I16 | °C | 10 | 0x88CF | 35023 | 1 | INV module C temperature Used for R&D 5-minute data recording.
253 | Inter nal Tem pera ture 4 | RO | I16 | °C | 10 | 0x88D0 | 35024 | 1 | Temperature sampling of anti-reverse module 1 Used for R&D 5-minute data recording.
254 | Inter nal Tem pera ture 5 | RO | I16 | °C | 10 | 0x88D1 | 35025 | 1 | Output board relay, ambient temperature - maximum temperature Used for R&D 5-minute data recording.
255 | Inter nal Tem pera ture 6 | RO | I16 | °C | 10 | 0x88D2 | 35026 | 1 | Output board, power board input, and power board inverter temperature sampling - maximum temperature Used for R&D 5-minute data recording.
256 | Inter nal tem pera ture 7 | RO | I16 | °C | 10 | 0x88D3 | 35027 | 1 | Temperature sampling of anti-reverse module 2 Used for R&D 5-minute data recording.
257 | Inter nal tem pera ture 8 | RO | I16 | °C | 10 | 0x88D4 | 35028 | 1 | DC terminal temperature 1 / 2 - maximum temperature Used for R&D 5-minute data recording.
258 | Inter nal tem pera ture 9 | RO | I16 | °C | 10 | 0x88D5 | 35029 | 1 | AC Terminal Temperature 1 / 2 / 3 - Maximum Temperature Used for R&D 5-minute data recording.
259 | Inter nal tem pera ture 10 | RO | I16 | °C | 10 | 0x88D6 | 35030 | 1 | Used for R&D data storage.
260 | Inter nal tem pera ture 11 | RO | I16 | °C | 10 | 0x88D7 | 35031 | 1 | Used for R&D data storage.
261 | Inter nal tem pera ture 12 | RO | I16 | °C | 10 | 0x88D8 | 35032 | 1 | Used for R&D data storage.
262 | Phas e A DC com pone nt DCI | RO | I16 | A | 1000 | 0x88DE | 35038 | 1 | Used for R&D 5-minute data recording.
263 | Phas e B DC com pone nt DCI | RO | I16 | A | 1000 | 0x88DF | 35039 | 1 | Used for R&D 5-minute data recording.
264 | Phas e C DC com pone nt DCI | RO | I16 | A | 1000 | 0x88E0 | 35040 | 1 | Used for R&D 5-minute data recording.
265 | Leak age curre nt RCD | RO | I16 | m A | 1 | 0x88E1 | 35041 | 1 | Used for R&D 5-minute data recording.
266 | Posit ive bus volta ge | RO | I16 | V | 10 | 0x88E2 | 35042 | 1 | Used for R&D 5-minute data recording.
267 | Neg ative bus volta ge | RO | I16 | V | 10 | 0x88E3 | 35043 | 1 | Used for R&D 5-minute data recording.
268 | BUS nega tive volta ge to grou nd | RO | I16 | V | 10 | 0x88E4 | 35044 | 1 | Used for R&D 5-minute data recording.
269 | I-V scan statu s | RO | E16 |  |  | 0x8916 | 35094 | 1
270 | I-V scan ning capa bility | RO | E16 |  |  | 0x8917 | 35095 | 1
271 | [Ma nage men t Syst em] NMS IP addr ess | RO | U32 |  | 1 | 0x891E | 35102 | 2 | Indicates whether the NMS is successfully connected. After the NMS is connected, fill in the NMS IP address. If there is no access, the value is 0XFFFFFFFF. The customer interface is called NA.
272 | [STA ] Wire less Rout ing Acce ss Sign al Stre ngth | RO | E16 |  |  | 0x8920 | 35104 | 1 | The FE status enumeration is used by the mobile app to effectively identify the current network conditions, switch icons, and provide effective prompts.
273 | [STA ] WLA N list scan ning statu s | RO | E16 |  |  | 0x8921 | 35105 | 1
274 | Wifi- Mac | RO | MLD |  | 1 | 0x8922 | 35106 | 3
275 | [NTP ] Last NTP sync hron izati on statu s. | RO | U16 |  | 1 | 0x8928 | 35112 | 1 | 0: normal 1: abnormal
276 | [NTP ] NTP Last Sync hron izati on Time | RO | U32 |  | 1 | 0x8929 | 35113 | 2 | Epoch Second
277 | Defe rred activ atio n state | RO | E16 |  |  | 0x892B | 35115 | 1
278 | [4G] Mon thly used traffi c | RO | U32 | M B | 100 | 0x892C | 35116 | 2
279 | [4G] Mon thly Rem ainin g Traff ic | RO | U32 | M B | 100 | 0x892E | 35118 | 2
280 | [4G] Aver age daily traffi c usag e | RO | U32 | M B | 100 | 0x8930 | 35120 | 2
281 | [4G] Traff ic statu s | RO | E16 |  |  | 0x8932 | 35122 | 1
282 | [STA ] Rout er conn ectio n time | RO | U16 | s | 1 | 0x8934 | 35124 | 1 | This parameter indicates the performance indicators for connecting the inverter or dongle to the router, and the duration for connecting the inverter or dongle to the router after the SSID and password are configured on the user interface. The maximum value given here.
283 | [STA ] Rout er conn ectio n statu s | RO | E16 |  |  | 0x8935 | 35125 | 1 | Note: 3: Connection failure indicates that the route can be discovered normally and the password is correct but the result fails. 0: Not connected indicates that the required information about the SSID and password is not configured.
284 | [FE] Con necti on statu s | RO | U16 |  | 1 | 0x8936 | 35126 | 1 | 0: not connected 1: being connected 2: successful connection 3: connection failure
285 | [Sm art I- V-V- Diag nosis ] Auth oriza tion Func tion | RO | Bitfield32 |  | 1 | 0x8940 | 35136 | 2 | 2019-02-19 SEG of the Monitoring Development Dept: The original LicC does not support the scenario where different features have different expiration dates. The license features are not supported by different models. Added the mechanism support. The original API is degenerated to support only the IV feature. For subsequent features, two interfaces (status and expiration time) are extended for each additional feature.
286 | Sma rt I- V-V- Diag nosis (Lice nse) Stat us | RO | E16 |  |  | 0x8942 | 35138 | 1
287 | [Sm art I- V-V- Diag nosis ] Lice nse expir atio n date | RO | EpochSecond | s | 1 | 0x8943 | 35139 | 2 | Epoch second 0XF2A52380 (2099-1-1) is reported, indicating that the setting takes effect permanently. If there is no license, 0 or 0XFFFFFFFF is reported and NA is displayed on the GUI.
288 | Lice nse loadi ng time | RO | EpochSecond | s | 1 | 0x8945 | 35141 | 2 | Epoch Second
289 | Lice nse Dere gistr atio n Time | RO | EpochSecond | s | 1 | 0x8947 | 35143 | 2 | Epoch second 0XFFFFFFFF is reported when the status is not deregistered.
290 | Lice nse SN | RO | STR |  | 1 | 0x8949 | 35145 | 10
291 | Inval idati on code . | RO | STR |  | 1 | 0x8953 | 35155 | 64
292 | Auth oriza tion Feat ure Sign atur e | RO | E16 |  |  | 0x8993 | 35219 | 2 | 1. If bit is set to 1, the function is licensed. 2. If the bit is cleared, the function does not need to be licensed on the current model. Used to support differentiated management and control policies for models.
293 | [Stri ng moni torin g] Lice nse statu s | RO | E16 |  |  | 0x8995 | 35221 | 1 | 0: no license; 1: normal; 2: grace period; 3: deregistered; 4: The SN does not match. 5: expired;
294 | [Stri ng Mon itori ng] Lice nse Expir atio n Time | RO | EpochSecond | s | 1 | 0x8996 | 35222 | 2 | Epoch Second If the feature status is normal, 0XF2A52380(2099-1-1) is reported, indicating that the feature takes effect permanently. If the feature status is abnormal, 0 or 0XFFFFFFFF is reported, and NA is displayed on the GUI.
295 | [4G] Mod ule statu s | RO | E16 |  |  | 0x89B1 | 35249 | 1
296 | [4G] IP addr ess | RO | U32 |  | 1 | 0x89B2 | 35250 | 2
297 | [4G] Subn et Mas k | RO | U32 |  | 1 | 0x89B4 | 35252 | 2
298 | [4G] IMEI | RO | STR |  | 1 | 0x89B6 | 35254 | 10
299 | [4G] sign al stren gth | RO | U16 |  | 1 | 0x89C0 | 35264 | 1 | 0 = No signal
300 | [4G] PIN num ber inpu t time s | RO | U16 |  | 1 | 0x89C1 | 35265 | 1
301 | [4G] PIN chec k statu s | RO | E16 |  |  | 0x89C2 | 35266 | 1
302 | Activ e pow er adju stme nt statu s | RO | MLD |  |  | 0x89E4 | 35300 | 4
303 | Reac tive pow er adju stme nt statu s | RO | MLD |  |  | 0x89E8 | 35304 | 4

## 07_Grid_Params
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
364 | Syst em time (loca l time ) | RW | EpochSecond | s | 1 | 0x9C40 | 40000 | 2 | The data is in the epoch second format, that is, the local time.
365 | Q-U char acter istic curv e mod e | RW | E16 |  |  | 0x9C65 | 40037 | 1
366 | Q-U Sche dulin g Trigg er Pow er Perc enta ge | RW | I16 | % | 1 | 0x9C66 | 40038 | 1
367 | Activ e pow er is dera ted by a fixed valu e. | RW | U16 | k W | 10 | 0x9CB8 | 40120 | 1
368 | Pow er facto r | RW | I16 |  | 1000 | 0x9CBA | 40122 | 1
369 | Reac tive pow er com pens atio n (Q/S ) [low preci sion] | RW | I16 |  | 1000 | 0x9CBB | 40123 | 1 | The equipment end converts the value into a fixed Q value for reactive power control. S is Smax.
370 | Reac tive pow er adju stme nt time | RW | U16 | s | 1 | 0x9CBC | 40124 | 1 | Change requirement: The "Reactive power adjustment time" broadcast interface is added to the Q-P characteristic curve and cosphi-P characteristic curve delivery interface, which is the same as the Q-U characteristic curve 20190918.
371 | Activ e pow er perc enta ge dera ting (low preci sion) | RW | I16 | % | 10 | 0x9CBD | 40125 | 1 | Active power fine adjustment interface
372 | Activ e pow er is dera ted by a fixed valu e. | RW | U32 | W | 1 | 0x9CBE | 40126 | 2 | Value range: [0, Pmax]
373 | Nigh t react ive pow er com pens atio n (Q/S ) | RW | I16 |  | 1000 | 0x9CC0 | 40128 | 1 | The equipment end converts the value into a fixed Q value for reactive power control. S is Smax.
374 | Fixe d valu e of react ive pow er at nigh t | RW | I32 | kV ar | 1000 | 0x9CC1 | 40129 | 2
375 | Cos? - P/Pn char acter istic curv e | RW | MLD |  |  | 0x9CC5 | 40133 | 21
376 | Q-U char acter istic curv e | RW | MLD |  |  | 0x9CDA | 40154 | 21
377 | PF-U char acter istic curv e | RW | MLD |  |  | 0x9CEF | 40175 | 21
378 | [Cha racte ristic curv e] Reac tive pow er adju stme nt time | RW | U16 | s | 1 | 0x9D04 | 40196 | 1 | Change requirement: The "Reactive power adjustment time" broadcast interface is added to the Q-P characteristic curve and cosphi-P characteristic curve delivery interface, which is the same as the Q-U characteristic curve 20190918.
379 | Q-U Sche dulin g Exit Pow er Perc enta ge | RW | I16 | % | 1 | 0x9D06 | 40198 | 1
380 | Activ e pow er perc enta ge cont rol [low preci sion] | RW | I16 | % | 10 | 0x9D07 | 40199 | 1 | This interface is used in distributed mode. It is used to control the active power percentage. It is issued to the power software in the anti-backflow control, and controls the upper limit of the output active power when the power is increased due to underfrequency.
381 | Start the syste m. | WO | E16 |  |  | 0x9D08 | 40200 | 1
382 | Shut dow n. | WO | E16 |  |  | 0x9D09 | 40201 | 1
383 | Quic k pow er- on and pow er- off | WO | E16 |  |  | 0x9D0A | 40202 | 1 | Not affected by shutdown gradient
384 | reset | WO | E16 |  |  | 0x9D0D | 40205 | 1 | After receiving the command, the DSP responds immediately and then resets. After receiving the command, the inverter monitoring module sends the command to the DSP. After receiving a normal response, the inverter monitoring module sends the command to the northbound port. After 3s, the system is reset. Otherwise, the system does not restart.
385 | Insul atio n impe danc e diag nosis | WO | U16 |  | 1 | 0x9D0E | 40206 | 1 | [0, 1], 1 action After receiving the instruction, the inverter restarts and performs insulation impedance detection.
386 | Dry Cont act Sche dulin g Setti ngs | RW | MLD |  | 1 | 0x9D6C | 40300 | 33
387 | Q-P char acter istic curv e | RW | MLD |  |  | 0x9DA2 | 40354 | 21
388 | Q-U char acter istic curv e mini mu m PF limit | RW | U16 |  | 1000 | 0x9DB7 | 40375 | 1 | This MPI is used to limit the reactive power output by the QU curve by limiting the current PF value. The country code that is not required by this function is set to 0 by default, indicating that the reactive power output is not limited. The country code in EN50549 can be set to 0 to 1, and the default value is 0.9.
389 | Q-U char acter istic curv e valid ity dela y time | RW | U16 | s | 1 | 0x9DB8 | 40376 | 1 | After the QU curve reaches the trigger voltage, the reactive power starts to change after a period of time is delayed. Italy CEI0-16/21 requires that the default value be 3s, indicating that the QU curve takes effect after the triggering delay is 3s, which can be set on the GUI. For other countries, the default value is 0.
390 | Syst em Time (UTC ) | WO | EpochSecond | s | 1 | 0x9E34 | 40500 | 2 | The data is in the UTC time format.

## 08_Grid_Scheduling
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
391 | Pow er grid stan dard code | RW | U16 |  | 1 | 0xA410 | 42000 | 1 | CHINA_MV800 For details about the scope, see the Power Grid Standard Code.
392 | Outp ut mod e | RW | E16 |  |  | 0xA411 | 42001 | 1 | On the customer interface, only read signals can be displayed. Currently, only three-phase three-wire signals are supported. No configuration is required. In the future, the interface changes will be used to notify each interface.
393 | Volt age level | RW | U16 | V | 1 | 0xA412 | 42002 | 1 | Vn
394 | Freq uenc y Class | RW | U16 | Hz | 1 | 0xA413 | 42003 | 1 | Fn
395 | Repl ace the targ et mod el. | RW | U16 |  | 1 | 0xA41C | 42012 | 1 | Enumerated ID of the inverter model. For details, see the Inverter Model Definition. The default value is 65535 (0xFFFF). If the ID is invalid, the replacement requirement is not set.
396 | Rem ote pow er sche dulin g | RW | E16 |  |  | 0xA41E | 42014 | 1 | 0：Disable 1：Enable If this parameter is disabled, the inverter will be locked.
397 | react ive pow er gradi ent | RW | U32 | %/ s | 1000 | 0xA41F | 42015 | 2
398 | Activ e pow er chan ge gradi ent | RW | U32 | %/ s | 1000 | 0xA421 | 42017 | 2 | Limits the speed at which the power changes caused by the power scheduling command
399 | Sche dule d instr uctio n hold time | RW | U32 | s | 1 | 0xA423 | 42019 | 2 | Permanently valid when the value is 0.
400 | Maxi mu m appa rent pow er | RW | U32 | kV A | 1000 | 0xA425 | 42021 | 2 | ["Maximum active power",Smax]
401 | Maxi mu m activ e pow er | RW | U32 | k W | 1000 | 0xA427 | 42023 | 2 | [0.1,Pmax]
402 | appa rent pow er refer ence | RW | U32 | kV ar | 1000 | 0xA429 | 42025 | 2 | Sn: upper limit of the maximum active power (PMax), which is used as the reference for reactive power scheduling (Q/S).
403 | Activ e pow er refer ence | RW | U32 | k W | 1000 | 0xA42B | 42027 | 2 | Set the lower limit of the maximum apparent value (SMax), which is also used as the reference for active power scheduling (percentage).
404 | Plan t activ e pow er gradi ent | RW | U16 | mi n/ 10 0% | 1 | 0xA42D | 42029 | 1 | China standards require that the active power change caused by light fluctuation must meet the speed requirements during normal operation of the equipment.
405 | Plan t activ e aver age filter ing time | RW | U32 | ms | 1 | 0xA42E | 42030 | 2
406 | Filter ing time for PF-U volta ge dete ction | RW | U16 | s | 10 | 0xA430 | 42032 | 1
407 | Dry cont act sche dulin g | RW | E16 |  |  | 0xA431 | 42033 | 1
408 | Audi ble and visua l alar m | RW | E16 |  |  | 0xA432 | 42034 | 1
409 | Freq uenc y Activ e Pow er Dera ting Reco very Dela y Time | RW | U16 | s | 1 | 0xA438 | 42040 | 1
410 | Freq uenc y Activ e Pow er Dera ting Effec tive Dela y Time | RW | U16 | ms | 1 | 0xA439 | 42041 | 1
411 | Freq uenc y activ e pow er dera ting hyst eresi s | RW | E16 |  |  | 0xA43A | 42042 | 1
412 | Freq uenc y mod ulati on cont rol resp onse dead band | RW | U16 | Hz | 1000 | 0xA43B | 42043 | 1
413 | Off- grid switc hove r mod e | RW | E16 |  |  | 0xA43C | 42044 | 1
414 | Off- grid mod e | RW | E16 |  |  | 0xA43D | 42045 | 1
415 | PQ mod e | RW | E16 |  |  | 0xA43E | 42046 | 1
416 | PV Pane l Type | RW | E16 |  |  | 0xA43F | 42047 | 1
417 | PID com pens atio n direc tion | RW | E16 |  |  | 0xA440 | 42048 | 1
418 | Strin g conn ectio n mod e | RW | E16 |  |  | 0xA441 | 42049 | 1
419 | Isola tion Setti ngs | RW | E16 |  |  | 0xA442 | 42050 | 1 | On the customer interface, only read signals can be displayed. Currently, only the input is not grounded and transformer is supported. Interface changes will be used to notify each interface during setting.
420 | Freq uenc y mod ulati on cont rol pow er chan ge gradi ent | RW | U16 | %/ mi n | 1 | 0xA443 | 42051 | 1
421 | Freq uenc y mod ulati on cont rol pow er chan ge limiti ng ampl itude | RW | U16 | % | 10 | 0xA444 | 42052 | 1
422 | FM cont rol dela y resp onse time | RW | U16 | ms | 1 | 0xA445 | 42053 | 1 | Polish national requirements, open and configurable Initial delay in the frequency sensitive mode
423 | MPP T mult imod al scan ning | RW | E16 |  |  | 0xA446 | 42054 | 1
424 | MPP T scan ning inter val | RW | U16 | mi n | 1 | 0xA447 | 42055 | 1
425 | Predi cted MPP T pow er | RO | U32 | k W | 1000 | 0xA448 | 42056 | 2
426 | Pow er grid fault reco very auto mati c start up | RW | E16 |  |  | 0xA44D | 42061 | 1
427 | Pow er limit 0% shut dow n | RW | E16 |  |  | 0xA44E | 42062 | 1
428 | Auto mati c pow er- off whe n com mun icati on is disco nnec ted | RW | E16 |  |  | 0xA44F | 42063 | 1 | In a parallel system, the system automatically shuts down when the communication link is interrupted by default. The communication interruption duration is 1 minute. The PCS power system determines the priority of the default power policy and the parameter setting. The affected parameters include all parameters under "Communication Disconnection Protection".
429 | Auto mati c pow er- on after com mun icati on reco very | RW | E16 |  |  | 0xA450 | 42064 | 1
430 | Pow er Qual ity Opti miza tion Mod e | RW | E16 |  |  | 0xA451 | 42065 | 1
431 | RCD Enha nce men t | RW | E16 |  |  | 0xA452 | 42066 | 1
432 | Nigh t react ive pow er | RW | E16 |  |  | 0xA453 | 42067 | 1
433 | Abn orm al grou ndin g shut dow n | RW | E16 |  |  | 0xA454 | 42068 | 1
434 | Nigh t PID prot ectio n | RW | E16 |  |  | 0xA455 | 42069 | 1
435 | Nigh t react ive pow er para mete rs take effec t | RW | E16 |  |  | 0xA456 | 42070 | 1
436 | Com mun icati on Disc onne ction Dete ction Time | RW | U16 | s | 1 | 0xA458 | 42072 | 1 | This parameter is displayed when the protection against communication disconnection is enabled.
437 | AFCI | RW | E16 |  |  | 0xA459 | 42073 | 1
438 | AFCI dete ction adap tatio n mod e | RW | E16 |  |  | 0xA45A | 42074 | 1
439 | Com mun icati on link failu re prot ectio n | RW | E16 |  |  | 0xA45B | 42075 | 1 | Used to initiate the security protection function after the communication between the device and the northbound interface is interrupted.
440 | Failu re prot ectio n activ e pow er mod e | RW | E16 |  |  | 0xA45C | 42076 | 1 | This parameter is displayed when the protection against communication disconnection is enabled.
441 | Activ e Pow er Limit for Failu re Prot ectio n [kW] [Low Preci sion] | RW | U32 | k W | 10 | 0xA45D | 42077 | 2 | This parameter is displayed only when the communication link failure protection is set to Enable and the active power mode is set to a fixed value.
442 | Failu re prot ectio n react ive pow er mod e | RW | E16 |  |  | 0xA45F | 42079 | 1 | This parameter is displayed when the protection against communication disconnection is enabled.
443 | Freq uenc y rate prot ectio n | RW | E16 |  |  | 0xA460 | 42080 | 1
444 | Freq uenc y chan ge rate prot ectio n poin t | RW | U16 | Hz /s | 10 | 0xA461 | 42081 | 1
445 | Freq uenc y chan ge rate prot ectio n time | RW | U16 | s | 10 | 0xA462 | 42082 | 1
446 | Reac tive pow er limit for failu re prot ectio n [Q/S ] [low preci sion] | RW | I16 |  | 1000 | 0xA463 | 42083 | 1 | (Deliver Q/S value) This parameter is displayed only when Communication Disconnection Failure Protection is set to Enable and Reactive Power Mode is set to Q/S.
447 | Pow er- on volta ge uppe r limit for grid conn ectio n | RW | U16 | V | 10 | 0xA464 | 42084 | 1 | Parameters for normal reconnection
448 | Pow er- on volta ge lowe r limit for grid conn ectio n | RW | U16 | V | 10 | 0xA465 | 42085 | 1 | Parameters for normal reconnection
449 | Pow er- on freq uenc y uppe r limit for grid conn ectio n | RW | U16 | Hz | 100 | 0xA466 | 42086 | 1 | Parameters for normal reconnection
450 | Pow er- on freq uenc y lowe r limit for grid conn ectio n | RW | U16 | Hz | 100 | 0xA467 | 42087 | 1 | Parameters for normal reconnection
451 | Pow er grid reco nnec tion volta ge uppe r limit | RW | U16 | V | 10 | 0xA468 | 42088 | 1 | Parameters for reconnection after a fault
452 | Pow er Grid Reco nnec tion Volt age Low er Thre shol d | RW | U16 | V | 10 | 0xA469 | 42089 | 1 | Parameters for reconnection after a fault
453 | Pow er grid reco nnec tion freq uenc y uppe r limit | RW | U16 | Hz | 100 | 0xA46A | 42090 | 1 | Parameters for reconnection after a fault
454 | Pow er grid reco nnec tion freq uenc y lowe r limit | RW | U16 | Hz | 100 | 0xA46B | 42091 | 1 | Parameters for reconnection after a fault
455 | Auto mati c Pow er Grid Reco nnec tion Time | RW | U16 | s | 1 | 0xA46C | 42092 | 1
456 | Insul atio n impe danc e prot ectio n poin t | RW | U16 | M Ω | 1000 | 0xA471 | 42097 | 1 | Value range: [0.02, 1.5] Actual protection is implemented by the inverter based on the DC voltage. 600 V DC inverter: [0.02, 1.5] 1000 V DC inverter: [0.033, 1.5] 1500 V DC inverter: [0.05, 1.5]
457 | Volt age unba lanc e prot ectio n thres hold | RW | U16 | % | 10 | 0xA472 | 42098 | 1
458 | Phas e prot ectio n poin t | RW | U16 | ° | 10 | 0xA473 | 42099 | 1
459 | Pow er- on soft start time due to pow er grid fault s | RW | U16 | s | 1 | 0xA474 | 42100 | 1 | Power rise gradient during equipment startup after a power grid fault
460 | Cos? - P/Pn trigg er volta ge | RW | U16 | % | 1 | 0xA475 | 42101 | 1
461 | Cos? - P/Pn exit volta ge | RW | U16 | % | 1 | 0xA476 | 42102 | 1
462 | Start up soft start time | RW | U16 | s | 1 | 0xA477 | 42103 | 1
463 | Pow er grid fault reco very time | RW | U16 | s | 1 | 0xA478 | 42104 | 1
464 | Time for dete rmin ing short - term pow er grid inter rupti on | RW | U32 | ms | 1 | 0xA479 | 42105 | 2 | Quick Start After Power Grid Fault is enabled and can be set.
465 | Shut dow n gradi ent | RW | U32 | %/ s | 1000 | 0xA47B | 42107 | 2
466 | Line loss com pens atio n | RW | U16 | % | 10 | 0xA47D | 42109 | 1
467 | Grid fault zero curre nt mod e | RW | E16 |  |  | 0xA47E | 42110 | 1
468 | Grid volta ge jump trigg er thres hold | RW | U16 | % | 10 | 0xA47F | 42111 | 1 | This parameter can be set only for the VDE4120.
469 | HVR T | RW | E16 |  |  | 0xA480 | 42112 | 1
470 | HVR T Trigg er Thre shol d | RW | U16 | V | 10 | 0xA481 | 42113 | 1
471 | HVR T posit ive sequ ence react ive pow er com pens atio n facto r | RW | U16 |  | 10 | 0xA482 | 42114 | 1
472 | V phas e to grou nd | RW | E16 |  |  | 0xA483 | 42115 | 1 | For the medium-three- phase 20KTL-M3 model in Japan, the phase wire on the side where the transformer is connected to the inverter must be grounded. The phase wire on the side where the transformer is connected to the inverter can be connected in delta or star topology.
473 | Shor t- term pow er grid inter rupti on and quic k start up | RW | E16 |  |  | 0xA484 | 42116 | 1 | Indicates whether to enable the fast startup function after the power grid recovers from a short-term interruption. If this parameter is set to 0, the power grid is connected according to the normal startup process after a short-term interruption. If this parameter is set to 1, the power grid is enabled. After a short-term interruption occurs on the power grid, the quick startup process is used. Some detection items are skipped and the power grid is quickly connected to the power grid. Whether a short-term interruption occurs on the power grid depends on whether the power grid can be recovered within the "short-term interruption time".
474 | LVRT activ e curre nt main tena nce coeff icien t | RW | U16 |  | 100 | 0xA486 | 42118 | 1
475 | LVRT | RW | E16 |  |  | 0xA487 | 42119 | 1 | By default, this function is enabled in the BDEW standard. In other standards, this function is disabled by default.
476 | LVRT Trigg er Thre shol d | RW | U16 | V | 10 | 0xA488 | 42120 | 1 | Sets the threshold for triggering low voltage ride- through. The threshold must comply with the local power grid standards.
477 | Pow er grid volta ge prot ectio n shiel d duri ng VRT | RW | E16 |  |  | 0xA489 | 42121 | 1 | It is used to set whether the voltage protection function needs to be shielded during the voltage ride-through.
478 | LVRT posit ive sequ ence react ive pow er com pens atio n facto r | RW | U16 |  | 10 | 0xA48A | 42122 | 1 | During the low voltage ride through (LVRT), the device needs to generate positive- sequence reactive power to support the power grid. This parameter is used to set the positive-sequence reactive power emitted by the device. For example, if the LVRT positive-sequence reactive power compensation factor is set to 2, the positive- sequence reactive current generated by the device increases by 20% of the rated current every time the AC voltage decreases by 10% during the low-voltage ride-through process.
479 | VRT exit hyst eresi s thres hold | RW | U16 | V | 10 | 0xA48B | 42123 | 1 | Sets the LVRT/HVRT recovery threshold. LVRT recovery threshold = LVRT trigger threshold + VRT exit hysteresis threshold HVRT recovery threshold = HVRT trigger threshold – VRT exit hysteresis threshold
480 | VRT activ e curre nt limiti ng perc enta ge | RW | U16 | % | 1 | 0xA48C | 42124 | 1
481 | VRT activ e pow er reco very gradi ent | RW | U16 | %/ s | 1 | 0xA48D | 42125 | 1
482 | HVR T nega tive sequ ence react ive com pens atio n facto r | RW | U16 |  | 10 | 0xA48E | 42126 | 1
483 | LVRT nega tive sequ ence react ive pow er com pens atio n facto r | RW | U16 |  | 10 | 0xA48F | 42127 | 1 | During low voltage ride through (LVRT), the device needs to generate negative- sequence reactive power to support the power grid. This parameter is used to set the negative-sequence reactive power emitted by the device. For example, if the LVRT negative sequence reactive power compensation factor is set to 2, the negative sequence reactive current generated by the device increases by 20% of the rated current every time the AC voltage decreases by 10% during the low voltage ride-through process.
484 | phas e angl e devi atio n prot ectio n | RW | E16 |  |  | 0xA490 | 42128 | 1
485 | Activ e Islan ding Prot ectio n | RW | E16 |  |  | 0xA491 | 42129 | 1
486 | Passi ve Islan ding Prot ectio n | RW | E16 |  |  | 0xA492 | 42130 | 1
487 | OVG R Asso ciate d Shut dow n | RW | E16 |  |  | 0xA493 | 42131 | 1
488 | Dry cont act func tion | RW | E16 |  |  | 0xA494 | 42132 | 1
489 | LVRT react ive curre nt limiti ng perc enta ge | RW | U16 | % | 1 | 0xA495 | 42133 | 1 | During low voltage ride- through, the equipment needs to limit the reactive current emitted by the equipment. For example, if LVRT Reactive Current Limit Percentage is set to 50, the upper limit of the reactive current of the device is 50% of the rated current during low voltage ride-through.
490 | LVRT zero curre nt mod e thres hold | RW | U16 | V | 10 | 0xA496 | 42134 | 1 | If the zero current mode is enabled and the voltage of the grid is less than the zero current mode threshold during LVRT, the zero current mode is used. Otherwise, the zero current mode is used.
491 | LVRT mod e | RW | E16 |  |  | 0xA497 | 42135 | 1
492 | RCD curre nt limit | RW | U16 | m A | 10 | 0xA498 | 42136 | 1
493 | Volt age rise supp ressi on | RW | E16 |  |  | 0xA49A | 42138 | 1
494 | Volt age rise supp ressi on react ive pow er adju stme nt poin t | RW | U16 | % | 10 | 0xA49B | 42139 | 1 | The value of "Voltage Rise Reject Active Derating Point" must be greater than the value of "Voltage Rise Reject Reactive Adjust Point".
495 | Volt age rise supp ressi on activ e dera ting thres hold | RW | U16 | % | 10 | 0xA49C | 42140 | 1 | The value of "Voltage Rise Reject Active Derating Point" must be greater than the value of "Voltage Rise Reject Reactive Adjust Point".
496 | freq uenc y mod ulati on cont rol | RW | E16 |  |  | 0xA49D | 42141 | 1 | According to the standards of some countries or regions, the power grid frequency changes around the rated value. If the device needs to fine-tune the active power output based on the frequency modulation control adjustment rate to help stabilize the power grid frequency, set this parameter to Enable. Frequency sensitive mode (FSM), which is required by the G99 standard.
497 | freq uenc y mod ulati on cont rol diffe renti al mod ulati on rate | RW | U16 | % | 1 | 0xA49E | 42142 | 1 | Frequency sensitive mode (FSM) Droop, which is required by the G99 standard.
498 | Over freq uenc y dera ting | RW | E16 |  |  | 0xA49F | 42143 | 1 | If this parameter is set to Enable, the device derates the active power based on a certain gradient when the power grid frequency exceeds the triggering frequency of overfrequency derating.
499 | Over freq uenc y dera ting cutof f freq uenc y | RW | U16 | Hz | 100 | 0xA4A0 | 42144 | 1 | Specifies the cutoff frequency for overfrequency derating.
500 | Over freq uenc y dera ting cut- off pow er | RW | U16 | % | 1 | 0xA4A1 | 42145 | 1 | Indicates the cutoff power point for overfrequency derating.
501 | Trigg ering freq uenc y of overf requ ency dera ting | RW | U16 | Hz | 100 | 0xA4A2 | 42146 | 1 | According to the standards in some countries or regions, the active power output by the device must be derated when the power grid frequency exceeds a specified value.
502 | Over freq uenc y dera ting exit freq uenc y | RW | U16 | Hz | 100 | 0xA4A3 | 42147 | 1 | Specifies the exit frequency of overfrequency derating.
503 | Over freq uenc y dera ting pow er reco very gradi ent | RW | U16 | %/ mi n | 1 | 0xA4A4 | 42148 | 1 | Indicates the speed at which the overfrequency derating power recovers.
504 | Und erfre quen cy Pow er Incre ase | RW | E16 |  |  | 0xA4A7 | 42151 | 1 | According to the standards in some countries or regions, the power grid frequency is lower than the triggering frequency of underfrequency power increase. In this case, the active power output needs to be increased to help increase the power grid frequency. In this case, set this parameter to Enable.
505 | Und erfre quen cy Pow er Incre ase Reco very Grad ient | RW | U16 | %/ mi n | 1 | 0xA4A8 | 42152 | 1 | Indicates the speed for recovering the underfrequency power increase.
506 | LVRT char acter istic curv e | RW | MLD |  |  | 0xA4AB | 42155 | 21 | Set the low-voltage ride- through capability of the equipment. For details, see the Key Information Description Table. The SmartLogger and NMS support batch settings and provide a separate GUI for users to edit.
507 | Cutof f freq uenc y of unde rfreq uenc y pow er incre ase | RW | U16 | Hz | 100 | 0xA4C0 | 42176 | 1 | Indicates the cutoff frequency for underfrequency power increase.
508 | Cut- off pow er for unde rfreq uenc y pow er incre ase | RW | U16 | % | 1 | 0xA4C1 | 42177 | 1 | Indicates the cutoff power point for underfrequency power increase.
509 | Und erfre quen cy Pow er Incre ase Trigg ering Freq uenc y | RW | U16 | Hz | 100 | 0xA4C2 | 42178 | 1 | Set the triggering frequency for underfrequency power increase.
510 | Und erfre quen cy Pow er Incre ase Exit Freq uenc y | RW | U16 | Hz | 100 | 0xA4C3 | 42179 | 1 | Specifies the exit frequency for underfrequency power increase.
511 | Built -in PID mod e | RW | E16 |  |  | 0xA4C4 | 42180 | 1
512 | PID outp ut volta ge | RW | I16 | V | 10 | 0xA4C5 | 42181 | 1 | Fixed output. This interface is reserved. The GUI is closed.
513 | PID | RW | E16 |  |  | 0xA4C6 | 42182 | 1 | Currently reserved only for equipment
514 | Nigh t off- grid repai r | RW | E16 |  |  | 0xA4C7 | 42183 | 1
515 | Activ e pow er chan ge gradi ent | RW | U32 | %/ s | 1000 | 0xA4D0 | 42192 | 2 | Dedicated broadcast interface for the SmartLogger, which does not support incremental reporting and is used in the remote output scenario in Japan.
516 | Q-U curv e | RW | MLD |  |  | 0xA4D8 | 42200 | 21
517 | P-U curv e | RW | MLD |  |  | 0xA4ED | 42221 | 21
518 | P-U curv e adju stme nt time | RW | U16 | s | 100 | 0xA502 | 42242 | 1
519 | Und ervol tage prot ectio n thres hold for 10 min utes | RW | U16 | V | 10 | 0xA52F | 42287 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
520 | Ten- min ute unde rvolt age prot ectio n time | RW | U32 | ms | 1 | 0xA530 | 42288 | 2
521 | Ten- min ute over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA532 | 42290 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
522 | Ten- min ute over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA533 | 42291 | 2
523 | Leve l-1 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA535 | 42293 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
524 | Leve l-1 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA536 | 42294 | 2
525 | Leve l-2 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA538 | 42296 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
526 | Leve l 2 Over volta ge Prot ectio n Time | RW | U32 | ms | 1 | 0xA539 | 42297 | 2
527 | Leve l-3 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA53B | 42299 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
528 | Leve l-3 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA53C | 42300 | 2
529 | Leve l-4 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA53E | 42302 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
530 | Leve l-4 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA53F | 42303 | 2
531 | Leve l-5 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA541 | 42305 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
532 | Leve l-5 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA542 | 42306 | 2
533 | Leve l-6 over volta ge prot ectio n thres hold | RW | U16 | V | 10 | 0xA544 | 42308 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
534 | Leve l-6 over volta ge prot ectio n time | RW | U32 | ms | 1 | 0xA545 | 42309 | 2
535 | Leve l-1 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA547 | 42311 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
536 | Leve l-1 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA548 | 42312 | 2
537 | Leve l-2 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA54A | 42314 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
538 | Leve l 2 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA54B | 42315 | 2
539 | Leve l-3 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA54D | 42317 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
540 | Leve l-3 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA54E | 42318 | 2
541 | Leve l-4 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA550 | 42320 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
542 | Leve l-4 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA551 | 42321 | 2
543 | Leve l-5 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA553 | 42323 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
544 | Leve l-5 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA554 | 42324 | 2
545 | Leve l-6 unde rvolt age prot ectio n thres hold | RW | U16 | V | 10 | 0xA556 | 42326 | 1 | Vn: indicates the voltage level, which is related to the power grid code.
546 | Leve l-6 Und ervol tage Prot ectio n Time | RW | U32 | ms | 1 | 0xA557 | 42327 | 2
547 | Leve l-1 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA559 | 42329 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
548 | Leve l-1 Over freq uenc y Prot ectio n Time | RW | U32 | ms | 1 | 0xA55A | 42330 | 2
549 | Leve l-2 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA55C | 42332 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
550 | Leve l-2 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA55D | 42333 | 2
551 | Leve l-3 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA55F | 42335 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
552 | Leve l-3 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA560 | 42336 | 2
553 | Leve l-4 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA562 | 42338 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
554 | Leve l-4 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA563 | 42339 | 2
555 | Leve l-5 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA565 | 42341 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
556 | Leve l-5 overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA566 | 42342 | 2
557 | Leve l-6 overf requ ency prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA568 | 42344 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
558 | Six- level overf requ ency prot ectio n time | RW | U32 | ms | 1 | 0xA569 | 42345 | 2
559 | Leve l-1 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA56B | 42347 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
560 | Leve l-1 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA56C | 42348 | 2
561 | Leve l-2 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA56E | 42350 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
562 | Leve l-2 unde rfreq uenc y prot ectio n time | RW | U32 | ms | 1 | 0xA56F | 42351 | 2
563 | Leve l-3 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA571 | 42353 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
564 | Leve l-3 unde rfreq uenc y prot ectio n time | RW | U32 | ms | 1 | 0xA572 | 42354 | 2
565 | Leve l-4 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA574 | 42356 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
566 | Leve l-4 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA575 | 42357 | 2
567 | Leve l-5 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA577 | 42359 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
568 | Leve l-5 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA578 | 42360 | 2
569 | Leve l-6 unde rfreq uenc y prot ectio n thres hold | RW | U16 | Hz | 100 | 0xA57A | 42362 | 1 | Fn: indicates the frequency level, which is related to the power grid code.
570 | Leve l-6 Und erfre quen cy Prot ectio n Time | RW | U32 | ms | 1 | 0xA57B | 42363 | 2
571 | Eme rgen cy stop switc h DI | RW | E16 |  |  | 0xA5A0 | 42400 | 1
572 | Outp ut impe danc e enha nce men t | RW | E16 |  |  | 0xA5A3 | 42403 | 1 | After the output impedance enhancement function is enabled, you can set the output impedance enhancement frequency to increase the output impedance at the frequency.
573 | Outp ut impe danc e enha nce men t freq uenc y poin t | RW | U16 | Hz | 10 | 0xA5A4 | 42404 | 1 | The default values are 1025.0 Hz for Switzerland, 175.0 Hz for France, and 210.0 Hz for Germany.
574 | Micr ogri d adap tabili ty | RW | E16 |  |  | 0xA5A7 | 42407 | 1 | The microgrid adaptability interface is added to the inverter (including the PCS current source grid-tied). When the microgrid adaptability function is enabled, the inverter (including the PCS current source grid-tied) supports a higher optical storage ratio based on the original country code feature.
575 | Oper atin g mod e | RW | E16 |  |  | 0xA5A9 | 42409 | 1 | The default value is PQ. You need to set the working mode during site deployment. Set the working mode to VSG in the churn scenario and PQ in the grid-tied scenario. Note: After this parameter is set, the device is powered off.
576 | Und erfre quen cy Pow er Incre ase Effec tive Dela y Time | RW | U16 | ms | 1 | 0xA5BD | 42429 | 1 | Setting the Underfrequency Power Increase Effective Delay Time
577 | Strin g-to- grou nd short circu it prot ectio n auto mati c reco very | RW | E16 |  |  | 0xA5C0 | 42432 | 1 | Enabled: The string short circuit to ground alarm is automatically cleared when the alarm conditions are not met. Disabled: The string short circuit to ground alarm cannot be automatically cleared. You need to manually clear the alarm.
578 | Dela yed upgr ade | RW | E16 |  |  | 0xA65E | 42590 | 1
579 | Intell igent strin g moni torin g | RW | E16 |  |  | 0xA662 | 42594 | 1
580 | Strin g dete ction refer ence asy mm etry coeff icien t | RW | U16 |  | 100 | 0xA663 | 42595 | 1
581 | Strin g dete ction start pow er perc enta ge | RW | U16 | % | 1 | 0xA664 | 42596 | 1
582 | Com mun icati on Inter rupti on Time | RW | I16 | mi n | 1 | 0xA665 | 42597 | 1
583 | Com mun icati ons | RW | E16 |  |  | 0xA666 | 42598 | 1
584 | [RS4 85-2 ] Com mun icati on | RW | E16 |  |  | 0xA667 | 42599 | 1
585 | PMI | WO | E16 |  |  | 0xA6EA | 42730 | 1 | Broadcast command interface Note: The instruction range extension design is made here. The higher eight bits are used to mask specified inspection actions in the inspection function. This feature improves the inspection efficiency for specific purposes. Shen Yanbai 20190702
586 | IV Curv e Scan ning | WO | E16 |  |  | 0xA71B | 42779 | 1 | Broadcast command interface
587 | Dayli ght Savi ng Time | RW | E16 |  |  | 0xA794 | 42900 | 1
588 | [DST ] Offs et time | RW | I16 | mi n | 1 | 0xA795 | 42901 | 1
589 | [DST ] Start Mon th | RW | U16 |  | 1 | 0xA796 | 42902 | 1
590 | [DST ] Start date | RW | U16 |  | 1 | 0xA797 | 42903 | 1 | The number of the day in a week is expressed by the number of weeks. The value 1 indicates Monday and the value 7 indicates Sunday. - shenyanbai 20190527
591 | [DST ] Start time | RW | U16 |  | 1 | 0xA798 | 42904 | 1
592 | [DST ] Start min ute | RW | U16 |  | 1 | 0xA799 | 42905 | 1
593 | [DST ] Start seco nd | RW | U16 |  | 1 | 0xA79A | 42906 | 1
594 | [DST ] End mon th | RW | U16 |  | 1 | 0xA79B | 42907 | 1
595 | [DST ] End date | RW | U16 |  | 1 | 0xA79C | 42908 | 1 | The number of the day in a week is expressed by the number of weeks. The value 1 indicates Monday and the value 7 indicates Sunday. - shenyanbai 20190527
596 | [Day light Savi ng Time ] Ends | RW | U16 |  | 1 | 0xA79D | 42909 | 1
597 | [DST ] End min ute | RW | U16 |  | 1 | 0xA79E | 42910 | 1
598 | [DST ] End seco nd | RW | U16 |  | 1 | 0xA79F | 42911 | 1

## 09_Comms_Network
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
599 | [Syst em Time ] Year | WO | U16 |  | 1 | 0xA7F8 | 43000 | 1
600 | [Syst em Time ] Mon th | WO | U16 |  | 1 | 0xA7F9 | 43001 | 1
601 | [Syst em time ] day | WO | U16 |  | 1 | 0xA7FA | 43002 | 1
602 | [Syst em time ] hour | WO | U16 |  | 1 | 0xA7FB | 43003 | 1
603 | [Syst em Time ] Min. | WO | U16 |  | 1 | 0xA7FC | 43004 | 1
604 | [Syst em Time ] Seco nd | WO | U16 |  | 1 | 0xA7FD | 43005 | 1
605 | Time zone | RW | I16 | mi n | 1 | 0xA7FE | 43006 | 1
606 | Cloc k sour ce | RW | E16 |  |  | 0xA7FF | 43007 | 1
607 | City code | RW | U32 |  |  | 0xA800 | 43008 | 2 | (UTC+08:00) Beijing
608 | Inver ter Insta llatio n Posit ion Long itude | RW | I32 | ° | 10000000 | 0xA806 | 43014 | 2 | Set this parameter only on the app. The NMS can read the data.
609 | Inver ter Insta llatio n Posit ion Latit ude | RW | I32 | ° | 10000000 | 0xA808 | 43016 | 2 | Set this parameter only on the app. The NMS can read the data.
610 | [RS4 85-1 ] Prot ocol Type | RW | E16 |  |  | 0xA80A | 43018 | 1
611 | [RS4 85-1 ] Com mun icati on addr ess | RW | U16 |  | 1 | 0xA80B | 43019 | 1 | 0: broadcast address; 1–247: device address; 248–255: reserved
612 | [RS4 85-1 ] Baud Rate | RW | E16 |  |  | 0xA80C | 43020 | 1 | 115200 baud rate, corresponding to bit 26 of feature code 3.
613 | [RS4 85-1 ] Verif icati on mod e | RW | E16 |  |  | 0xA80D | 43021 | 1
614 | [RS4 85-1 ] Port mod e | RW | E16 |  |  | 0xA80E | 43022 | 1
615 | [RS4 85-1 ] Mod bus Prot ocol Mod el Versi on | RW | E16 |  |  | 0xA80F | 43023 | 1 | This parameter is used only when the northbound port is used in the old model replacement scenario.
616 | [RS4 85-2 ] Prot ocol Type | RW | E16 |  |  | 0xA819 | 43033 | 1
617 | [RS4 85-2 ] Com mun icati on addr ess | RW | U16 |  | 1 | 0xA81A | 43034 | 1 | 0: broadcast address 1–247: device address 248–255: reserved
618 | [RS4 85-2 ] Baud Rate | RW | E16 |  |  | 0xA81B | 43035 | 1 | 115200 baud rate, corresponding to bit 27 of feature code 3.
619 | [RS4 85-2 ] Verif icati on Mod e | RW | E16 |  |  | 0xA81C | 43036 | 1
620 | [RS4 85-2 ] Port mod e | RW | E16 |  |  | 0xA81D | 43037 | 1
621 | Prot ocol Type | RW | E16 |  |  | 0xA827 | 43047 | 1
622 | Box- type trans form er num ber | RW | U16 |  | 1 | 0xA828 | 43048 | 1 | Only the 06 function code is supported. Local application
623 | Win ding No. | RW | U16 |  | 1 | 0xA829 | 43049 | 1 | Only the 06 function code is supported. Local application
624 | Mac Offs et | RW | U16 |  | 1 | 0xA82A | 43050 | 1 | Only the 06 function code is supported. Local application
625 | Pow er setti ngs | RW | U16 | dB | 1 | 0xA82C | 43052 | 1 | Note: This parameter x 2 corresponds to the dB value.
626 | [Ma nage men t Syst em] TCP Fra me Leng th | RW | U16 |  | 1 | 0xA837 | 43063 | 1 | [320, 1500]
627 | [Ma nage men t Syst em] Appl icati on- Laye r Hear tbea t Inter val | RW | U16 | mi n | 1 | 0xA838 | 43064 | 1 | Default value: 30 minutes
628 | [Ma nage men t Syst em] TCP Hear tbea t Inter val | RW | U16 | s | 1 | 0xA839 | 43065 | 1 | 0XFFFF indicates that there is no heartbeat. If this parameter is set to 0, the default heartbeat period is 3 minutes.
629 | [Ma nage men t Syst em] Prot ocol Type | RW | E16 |  |  | 0xA83A | 43066 | 1
630 | [Ma nage men t Syst em] Serv er | RW | STR |  | 1 | 0xA83B | 43067 | 30 | Domain name address or IP address
631 | [Ma nage men t syste m] Port 1 | RW | U16 |  | 1 | 0xA859 | 43097 | 1
632 | [Ma nage men t Syst em] TLS Encr yptio n | RW | E16 |  |  | 0xA85A | 43098 | 1
633 | [Ma nage men t Syst em] Port mod e | RW | E16 |  |  | 0xA85C | 43100 | 1
634 | [FE] Key pass word | WO | MLD |  |  | 0xA85E | 43102 | 32 | Interface for delivering the key password when the app certificate is replaced
635 | [STA ] Acce ssing a Wire less Rout er | RW | E16 |  |  | 0xA88B | 43147 | 1
636 | [STA ] Wire less Rout ing Net work Nam e | RW | STR |  | 1 | 0xA88C | 43148 | 16
637 | [STA ] Wire less Rout ing Encr yptio n Mod e | RW | E16 |  |  | 0xA89C | 43164 | 1
638 | [STA ] Wire less Rout er Logi n Pass word | RW | STR |  | 1 | 0xA89D | 43165 | 32 | This parameter is not displayed in non-encryption mode.
639 | [FE] DHC P | RW | E16 |  |  | 0xA8BD | 43197 | 1
640 | [FE] IP addr ess | RW | IPv4 |  |  | 0xA8BE | 43198 | 2 | If the IP address, subnet mask, and gateway address are modified, the other two parameters must be delivered in the same frame.
641 | [FE] Subn et Mas k | RW | IPv4 |  |  | 0xA8C0 | 43200 | 2
642 | [FE] Gate way addr ess | RW | IPv4 |  |  | 0xA8C2 | 43202 | 2
643 | [STA ] Prefe rred DNS Serv er | RW | U32 |  | 1 | 0xA8C4 | 43204 | 2
644 | [STA ] Stan dby DNS serv er | RW | U32 |  | 1 | 0xA8C6 | 43206 | 2
645 | [FE] DHC P | RW | E16 |  |  | 0xA8C8 | 43208 | 1 | Decoupling mode: Feature code 2:18
646 | [FE] IP addr ess | RW | U32 |  | 1 | 0xA8C9 | 43209 | 2 | If the IP address, subnet mask, and gateway address are modified, the other two parameters must be delivered in the same frame.
647 | [FE] Subn et Mas k | RW | U32 |  | 1 | 0xA8CB | 43211 | 2
648 | [FE] Gate way addr ess | RW | U32 |  | 1 | 0xA8CD | 43213 | 2
649 | [FE] Prefe rred DNS serv er | RW | U32 |  | 1 | 0xA8CF | 43215 | 2 | Decoupling mode: Feature code 2:18
650 | [FE] Seco ndar y DNS serv er | RW | U32 |  | 1 | 0xA8D1 | 43217 | 2 | Decoupling mode: Feature code 2:18
651 | WLA N O& M Polic y | RW | E16 |  |  | 0xA8E4 | 43236 | 1 | Configures O&M policies for WLAN ports. For the SACU, policies 0, 1, and 2 can be configured. For the APP, policies 0 and 1. Permanently enabled: The WLAN port function is always available. Idle: Disable the WLAN O&M function after the idle time is 4 hours. Permanently disabled: The WLAN function is unavailable. If the power can be disabled, the power is disabled. If the power cannot be disabled, the O&M capability is disabled. Supported by SDongle and distributed inverters
652 | [AP] SSID broa dcas t | RW | U16 |  | 1 | 0xA8E5 | 43237 | 1 | 0: enabled 1: disabled Default value: 0
653 | [AP] WLA N nam e | RW | STR |  | 1 | 0xA8E6 | 43238 | 16 | Wifi-AP mode
654 | [AP] WLA N Logi n Pass word | RW | STR |  | 1 | 0xA8F6 | 43254 | 32 | The password must contain at least eight characters.
655 | [AP] Gate way IP addr ess | RW | U32 |  | 1 | 0xA917 | 43287 | 2
656 | [AP] subn et mas k | RW | U32 |  | 1 | 0xA919 | 43289 | 2
657 | [NTP ] NTP time sync hron izati on | RW | U16 |  | 1 | 0xA92F | 43311 | 1
658 | [NTP ] NTP serv er addr ess | RW | STR |  | 1 | 0xA930 | 43312 | 30
659 | [NTP ] NTP serv er port | RW | U16 |  | 1 | 0xA94E | 43342 | 1
660 | [NTP ] NTP Servi ce Time Inter val | RW | U16 | mi n | 1 | 0xA94F | 43343 | 1
661 | Devi ce nam e | RW | STR |  |  | 0xA955 | 43349 | 10 | This parameter is left blank by default. It is used by the customer to modify the device name.
662 | [App ] Initia l pow er- on flag | RW | E16 |  |  | 0xA95F | 43359 | 1 | After the SmartLogger is deployed, the power-on flag needs to be cleared.
663 | Paral lel com mun icati on mod e | RW | E16 |  |  | 0xA961 | 43361 | 1 | This interface is used to set the communication mode between the host machine and the parallel slave server in the Sdongle network access scenario. After the setting, the host machine bridges the Dongle or USB expansion module to the interface. Note: This interface is used to replace the cascade channel 43360 interface. The inverter must be compatible with this interface. When the interface has been set, the parameters must be migrated. When the high byte is 0, the SUN2000 automatically determines the parallel control entry based on the request entry.
664 | [4G] 4G mod ule | RW | E16 |  |  | 0xA96A | 43370 | 1
665 | [4G] Card No. | RW | MLD |  | 1 | 0xA97A | 43386 | 10
666 | [4G] Net work mod e | RW | E16 |  |  | 0xA9A6 | 43430 | 1
667 | [4G] APN mod e | RW | E16 |  |  | 0xA9A7 | 43431 | 1
668 | [4G] [Def ault] Iden tity auth entic atio n type | RW | E16 |  |  | 0xA9A9 | 43433 | 1
669 | [4G] [Def ault] APN | RW | STR |  | 1 | 0xA9AA | 43434 | 16
670 | [4G] [Def ault] APN user nam e | RW | STR |  | 1 | 0xA9CA | 43466 | 16
671 | [4G] [Def ault] APN user pass word | RW | STR |  | 1 | 0xA9DA | 43482 | 16
672 | [4G] Iden tity auth entic atio n type | RW | E16 |  |  | 0xA9EB | 43499 | 1
673 | [4G] APN | RW | STR |  | 1 | 0xA9EC | 43500 | 16 | APN name
674 | [4G] APN dial- up num ber | RW | STR |  | 1 | 0xA9FC | 43516 | 16 | Dial Number
675 | [4G] APN User Nam e | RW | STR |  | 1 | 0xAA0C | 43532 | 16 | APN User Name
676 | [4G] APN user pass word | RW | STR |  | 1 | 0xAA1C | 43548 | 16 | APN Password
677 | [4G] Traff ic pack age | RW | U32 | M B | 100 | 0xAA2C | 43564 | 2
678 | [4G] Mon thly used traffi c | RW | U32 | M B | 100 | 0xAA2E | 43566 | 2 | Used for traffic correction.
679 | [4G] PIN | WO | MLD |  | 1 | 0xAA30 | 43568 | 4
680 | Strin g acce ss dete ction | RW | U16 |  | 1 | 0xAA70 | 43632 | 1 | 0: disabled (default) 1: enabled
681 | Start -up curre nt | RW | U16 | A | 100 | 0xAA71 | 43633 | 1 | [3.0, 10.0] Default value: 5.0
682 | Two- in- one dete ction start ing curre nt | RW | U16 | A | 100 | 0xAA72 | 43634 | 1 | [10.0, 20.0] Default value: 15.0
683 | Strin g 1 acce ss type | RW | E16 |  |  | 0xAA73 | 43635 | 1
684 | Strin g 2 Acce ss Type | RW | E16 |  |  | 0xAA74 | 43636 | 1
685 | Strin g 3 Acce ss Type | RW | E16 |  |  | 0xAA75 | 43637 | 1
686 | Strin g 4 Acce ss Type | RW | E16 |  |  | 0xAA76 | 43638 | 1
687 | Strin g 5 Acce ss Type | RW | E16 |  |  | 0xAA77 | 43639 | 1
688 | Strin g 6 Acce ss Type | RW | E16 |  |  | 0xAA78 | 43640 | 1
689 | Strin g 7 Acce ss Type | RW | E16 |  |  | 0xAA79 | 43641 | 1
690 | Strin g 8 Acce ss Type | RW | E16 |  |  | 0xAA7A | 43642 | 1

## 10_Tracker_Feature
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
691 | Supp ort Syst em Type | RW | E16 |  |  | 0xABE0 | 44000 | 1 | If the device vendor does not support one of the modes, the system returns the 03 error code.
692 | Oper atin g mod e | RW | E16 |  |  | 0xABE1 | 44001 | 1
693 | Cont rol perio d | RW | U16 | mi n | 1 | 0xABE2 | 44002 | 1
694 | Start time of rever se traci ng in the mor ning (hou r) | RW | U16 | ho ur | 1 | 0xABE3 | 44003 | 1
695 | Start time of rever se traci ng in the mor ning (min utes) | RW | U16 | mi n | 1 | 0xABE4 | 44004 | 1
696 | Mor ning Back track ing Dura tion Min ute | RW | U16 | mi n | 1 | 0xABE5 | 44005 | 1
697 | Tilt angl e cont rol | RW | MLD |  | 1 | 0xABE6 | 44006 | 2 | HW: ID of the support system, ranging from 0 to 16. The value 0 indicates full control. LW: tilt angle. The gain is 100. The value range is [0-90]. The control angle range also meets the requirements of the upper and lower limits of tilt angle control.
698 | Beari ng cont rol | RW | MLD |  | 1 | 0xABE8 | 44008 | 2 | HW: ID of the support system, ranging from 0 to 16. 0 indicates full control. LW: azimuth preset value, gain 100, range [-90 to 90] The control angle range must meet the requirements of the upper and lower limits of azimuth control.
699 | Num ber of mot ors cont rolle d simu ltane ousl y | RW | U16 |  | 1 | 0xABEA | 44010 | 1 | If the actual number of motors is less than 16, the setting may fail.
700 | Start time of the rever se traci ng in the even ing (hou r) | RW | U16 | ho ur | 1 | 0xABEB | 44011 | 1
701 | Start time of the rever se traci ng in the even ing (min ute) | RW | U16 | mi n | 1 | 0xABEC | 44012 | 1
702 | Even ing Back track ing Dura tion Min ute | RW | U16 | mi n | 1 | 0xABED | 44013 | 1
703 | Sens or insta llatio n direc tion | RW | E16 |  |  | 0xABEE | 44014 | 1
704 | Cont rolle r time sync hron izati on | RW | E16 |  |  | 0xABEF | 44015 | 1
705 | Num ber of cont rol boxe s | RW | U16 |  | 1 | 0xABF0 | 44016 | 1
706 | Total num ber of stent s | RW | U16 |  | 1 | 0xAC12 | 44050 | 1 | When dual-axis control is used, the maximum number of support systems is 8.
707 | Insta llatio n Long itude | RW | I16 | ° | 100 | 0xAC13 | 44051 | 1 | The east longitude is positive and the west longitude is negative.
708 | Insta llatio n Dim ensi on | RW | I16 | ° | 100 | 0xAC14 | 44052 | 1 | The north latitude is positive and the south latitude is negative.
709 | Cont rol addr ess 1 | RW | U16 |  | 1 | 0xAC15 | 44053 | 1
710 | Cont rol addr ess 2 | RW | U16 |  | 1 | 0xAC16 | 44054 | 1
711 | Sout hbou nd RS48 5 Chec k Mod e | RW | E16 |  |  | 0xAC17 | 44055 | 1
712 | Sout hbou nd RS48 5 baud rate | RW | E16 |  |  | 0xAC18 | 44056 | 1
713 | Tilt angl e cont rol uppe r limit | RW | I16 | ° | 100 | 0xAC19 | 44057 | 1 | Tilt angle control upper limit must be greater than lower limit
714 | Tilt angl e cont rol lowe r limit | RW | I16 | ° | 100 | 0xAC1A | 44058 | 1 | Tilt angle control upper limit must be greater than lower limit
715 | Upp er limit of azim uth cont rol | RW | I16 | ° | 100 | 0xAC1B | 44059 | 1 | The upper limit of azimuth control must be greater than the lower limit.
716 | Low er limit for azim uth cont rol | RW | I16 | ° | 100 | 0xAC1C | 44060 | 1 | The upper limit of azimuth control must be greater than the lower limit.
717 | Sens or 1 addr ess | RW | U16 |  | 1 | 0xAC1D | 44061 | 1
718 | Sens or 2 Addr ess | RW | U16 |  | 1 | 0xAC1E | 44062 | 1
719 | Sens or 3 Addr ess | RW | U16 |  | 1 | 0xAC1F | 44063 | 1
720 | Sens or 4 Addr ess | RW | U16 |  | 1 | 0xAC20 | 44064 | 1
721 | Sens or 5 Addr ess | RW | U16 |  | 1 | 0xAC21 | 44065 | 1
722 | Sens or 6 Addr ess | RW | U16 |  | 1 | 0xAC22 | 44066 | 1
723 | Sens or 7 addr ess | RW | U16 |  | 1 | 0xAC23 | 44067 | 1
724 | Sens or 8 Addr ess | RW | U16 |  | 1 | 0xAC24 | 44068 | 1
725 | Sens or 9 Addr ess | RW | U16 |  | 1 | 0xAC25 | 44069 | 1
726 | Sens or 10 Addr ess | RW | U16 |  | 1 | 0xAC26 | 44070 | 1
727 | Sens or 11 addr ess | RW | U16 |  | 1 | 0xAC27 | 44071 | 1
728 | Sens or 12 Addr ess | RW | U16 |  | 1 | 0xAC28 | 44072 | 1
729 | Sens or 13 addr ess | RW | U16 |  | 1 | 0xAC29 | 44073 | 1
730 | Sens or 14 Addr ess | RW | U16 |  | 1 | 0xAC2A | 44074 | 1
731 | Sens or 15 Addr ess | RW | U16 |  | 1 | 0xAC2B | 44075 | 1
732 | Sens or 16 Addr ess | RW | U16 |  | 1 | 0xAC2C | 44076 | 1
733 | Trac king syste m cont rolle r | RW | E16 |  |  | 0xAC2D | 44077 | 1
734 | Cont rol addr ess 3 | RW | U16 |  | 1 | 0xAC2F | 44079 | 1
735 | Cont rol addr ess 4 | RW | U16 |  | 1 | 0xAC30 | 44080 | 1
736 | Sout hbou nd RS48 5 stop bit | RW | E16 |  |  | 0xAC31 | 44081 | 1
737 | Supp ort Fault Clea ranc e | WO | U16 |  | 1 | 0xAC32 | 44082 | 1 | 0: Clear all support faults. 1-16: Clear the fault of the specified support.
738 | GPS time (loca l time ): year | RW | U16 |  | 1 | 0xAC33 | 44083 | 1
739 | wind spee d | RW | U16 | m/ s | 1 | 0xAC39 | 44089 | 1
740 | Time zone | RW | I16 | mi n | 1 | 0xAC3A | 44090 | 1
741 | Cont rol addr ess 5 | RW | U16 |  | 1 | 0xAC3B | 44091 | 1
742 | Cont rol addr ess 6 | RW | U16 |  | 1 | 0xAC3C | 44092 | 1
743 | Cont rol addr ess 7 | RW | U16 |  | 1 | 0xAC3D | 44093 | 1
744 | Cont rol addr ess 8 | RW | U16 |  | 1 | 0xAC3E | 44094 | 1
745 | Cont rol addr ess 9 | RW | U16 |  | 1 | 0xAC3F | 44095 | 1
746 | Cont rol addr ess 10 | RW | U16 |  | 1 | 0xAC40 | 44096 | 1
747 | Cont rol addr ess 11 | RW | U16 |  | 1 | 0xAC41 | 44097 | 1
748 | Cont rol addr ess 12 | RW | U16 |  | 1 | 0xAC42 | 44098 | 1
749 | Cont rol addr ess 13 | RW | U16 |  | 1 | 0xAC43 | 44099 | 1
750 | Cont rol addr ess 14 | RW | U16 |  | 1 | 0xAC44 | 44100 | 1
751 | Cont rol addr ess 15 | RW | U16 |  | 1 | 0xAC45 | 44101 | 1
752 | Cont rol addr ess 16 | RW | U16 |  | 1 | 0xAC46 | 44102 | 1
753 | Scie nce and Tech nolo gy Jingk e Prot ocol Versi on | RW | E16 |  |  | 0xAC47 | 44103 | 1
754 | Sens or Rang e | RW | U16 | ° | 1 | 0xAC48 | 44104 | 1
755 | Cont rol preci sion | RW | U16 | ° | 100 | 0xAC49 | 44105 | 1
756 | KP | RW | I16 |  | 100 | 0xACA8 | 44200 | 1 | Debugging interface
757 | KI | RW | I16 |  | 100 | 0xACA9 | 44201 | 1 | Debugging interface
758 | KD | RW | I16 |  | 100 | 0xACAA | 44202 | 1 | Debugging interface
759 | wind spee d | WO | U16 | m/ s | 1 | 0xAD0C | 44300 | 1
760 | Win d direc tion | WO | U16 | ° | 1 | 0xAD0D | 44301 | 1
761 | Start up cont rol | WO | E16 |  |  | 0xAD0E | 44302 | 2 | BIT0–BIT15: Start command of bracket 1–bracket system 16; BIT16–BIT31: reserved for future expansion.
762 | Supp ort Fault Clea ranc e | WO | E16 |  |  | 0xAD10 | 44304 | 2 | BIT0–BIT15: Clear the faults of support 1–16 in sequence. Bits 16–32: reserved for future expansion.
763 | Stop cont rol | WO | E16 |  |  | 0xAD12 | 44306 | 2 | BIT0~BIT15: stop command of rack 1~rack system 16; BIT16–BIT31: reserved for future expansion.
764 | Tem pera ture 1 | WO | I16 | °C | 10 | 0xAD78 | 44408 | 1
765 | Hum idity 1 | WO | U16 | % RH | 10 | 0xAD7A | 44410 | 1
766 | Rest ore facto ry setti ngs. | WO | E16 |  |  | 0xAFC8 | 45000 | 1
767 | Clea ring activ e alar ms | WO | MLD |  |  | 0xAFC9 | 45001 | 2
768 | Alar m setti ng | WO | MLD |  |  | 0xAFCB | 45003 | 2
769 | Alar m clear ance | WO | E16 |  |  | 0xAFCD | 45005 | 1
770 | Alar m mas king | WO | E16 |  |  | 0xAFCE | 45006 | 1
771 | AFCI self- chec k start | WO | U16 |  | 1 | 0xAFCF | 45007 | 1 | Set the field to 0. Associate the AFCI controller in the in-position ID of the subdevice.
772 | Accu mula ted ener gy yield corre ction | WO | U32 | k W h | 100 | 0xAFD0 | 45008 | 2
773 | Clea r histo rical batt ery level. | WO | E16 |  |  | 0xAFD2 | 45010 | 1 | Including the accumulated power generation capacity and accumulated charging capacity on the power side
774 | Clea r the runn ing time infor mati on. | WO | E16 |  |  | 0xAFD3 | 45011 | 1 | Clears the accumulated running time, fault duration, and grid-tied running time.
775 | Spot Chec k | WO | E16 |  |  | 0xAFD4 | 45012 | 1
776 | Clea r the flash me mor y. | WO | U16 |  | 1 | 0xAFD6 | 45014 | 1
777 | ESN valid atio n com man d | WO | U16 |  | 1 | 0xAFD7 | 45015 | 1
778 | Rest ore the defa ult pass word . | WO | MLD |  | 1 | 0xAFD8 | 45016 | 10 | Enter the equipment ESN in the Data field.
779 | [STA ] Start scan ning the avail able WLA N list. | WO | U16 |  | 1 | 0xAFE2 | 45026 | 1 | 0
780 | [Lice nse Inter face] Lice nse Dere gistr atio n | WO | MLD |  | 1 | 0xAFE3 | 45027 | 10 | Fill the LSN in the data field.
781 | Alar m port self- chec k start | WO | U16 |  | 1 | 0xAFED | 45037 | 1 | The data field is set to 0.
782 | Audi ble and visua l alar m confi rmat ion | WO | U16 |  | 1 | 0xAFF0 | 45040 | 1 | This parameter is added to disable the audible and visual alarm function. After the alarm condition is cleared, the audible and visual alarm function is enabled again.

## 11_EnergyStorage
No. | Signal Name | R/W | Type | Unit | Gain | Address (Hex) | Address (Dec) | Num Reg | Scope / Notes
783 | Box- type trans form er num ber | RW | U16 |  | 1 | 0xB799 | 47001 | 1 | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
784 | Win ding No. | RW | U16 |  | 1 | 0xB79A | 47002 | 1 | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
785 | Mac Offs et | RW | U16 |  | 1 | 0xB79B | 47003 | 1 | Remote dedicated, supported only for commercial use, and the addresses of all versions must be the same.
786 | Oper atin g mod e | RW | E16 |  |  | 0xB79C | 47004 | 1
787 | Pow er limit for grid- tied sites | RW | I32 | W | 1 | 0xB7E7 | 47079 | 2
788 | Opti mize r | RW | E16 |  |  | 0xB810 | 47120 | 1 | Used to add the safety box. After the safety box is added, the DC-PLC status is set. Shenyanbai: This flag is forcibly set to 1 in the single-phase inverter implementation of the US version.
789 | Singl e Opti mize r Data Quer y | RW | U16 |  | 1 | 0xB816 | 47126 | 1 | Optimizer Logical Address
790 | Alias Setti ngs | WO | MLD |  | 1 | 0xB819 | 47129 | 11 | W0: optimizer address; (small end) W1–10: alias character string
791 | Phys ical locat ion | WO | E16 |  |  | 0xB824 | 47140 | 1 | Anti-crosstalk is disabled.
792 | Imp ortin g Logs | WO | E16 |  |  | 0xB825 | 47141 | 1
793 | Brok en line dete ction | WO | E16 |  |  | 0xB827 | 47143 | 1
794 | Expo rt com plete logs. | WO | E16 |  |  | 0xB828 | 47144 | 1
795 | Setti ng the Accu mula ted Ener gy Yield | WO | MULTIDATA | 1 |  | 0xB829 | 47145 | 3 | Gain: 1000 Unit: kWh
796 | Baud Rate | RW | E16 |  |  | 0xB82E | 47150 | 1 | The MBUS register is 43113.
797 | Anti- cross talk | RW | E16 |  |  | 0xB82F | 47151 | 1 | The MBUS register is 47022.
798 | Net work freq uenc y band | RW | E16 |  |  | 0xB830 | 47152 | 1 | The MBUS register is 43116.
799 | Net work ing | RW | E16 |  |  | 0xB831 | 47153 | 1 | The MBUS register is 47010.
800 | Pack et loss rate test | RW | E16 |  |  | 0xB832 | 47154 | 1
801 | Secu rity mod e | RW | E16 |  |  | 0xB834 | 47156 | 1 | When the PLC enters and exits the unlock mode, the CCO is reset.
802 | Fast pow er- dow n enab le | RW | E16 |  |  | 0xB835 | 47157 | 1
803 | Fast Shut dow n Self- Test | WO | U16 |  |  | 0xB836 | 47158 | 1
804 | Forw ard pow er | RW | E16 |  |  | 0xB8C4 | 47300 | 1
805 | Cabl e conn ectio n posit ion | RW | E16 |  |  | 0xB8C5 | 47301 | 1
806 | CT rate d curre nt | RW | U16 | A | 1 | 0xB8C6 | 47302 | 1
807 | Met er mod el | RW | E16 |  |  | 0xB8C7 | 47303 | 1 | Note: 47002 conflicts with the winding number of the [Remote Setting]. The winding number is reassigned. This interface will be used in later versions. Naming format: manufacturer-model
808 | Met er addr ess | RW | U16 |  | 1 | 0xB8C8 | 47304 | 1 | Note: 47003 conflicts with [Remote Settings] MAC Offset. This interface will be used in later versions.
809 | Met er nam e | RW | MLD |  | 1 | 0xB8C9 | 47305 | 15 | Used to store the name of the meter during model loading.
810 | Enab le auto mati c addr ess alloc atio n. | RW | E16 |  |  | 0xB928 | 47400 | 1
811 | Start addr ess for auto mati c addr ess assig nme nt | RW | U16 |  | 1 | 0xB929 | 47401 | 1
812 | Com mun icati on mod ule addr ess | RW | U16 |  | 1 | 0xB936 | 47414 | 1
813 | Activ e pow er cont rol mod e | RW | E16 |  |  | 0xB937 | 47415 | 1
814 | Maxi mu m pow er fed to the grid (kW) | RW | I32 | k W | 1000 | 0xB938 | 47416 | 2
815 | Maxi mu m Feed Grid Pow er (%) | RW | I16 | % | 10 | 0xB93A | 47418 | 1
816 | Restr ictio n mod e | RW | E16 |  |  | 0xB93B | 47419 | 1
817 | Pow er decr ease adju stme nt perio d | RW | U16 | s | 10 | 0xB93C | 47420 | 1
818 | Maxi mu m prot ectio n time | RW | U16 | s | 10 | 0xB93D | 47421 | 1
819 | Pow er Incre ase Thre shol d | RW | U32 | k W | 1000 | 0xB93E | 47422 | 2
820 | Activ e pow er limit for fail prot ectio n [%] [low preci sion] | RW | I16 | % | 10 | 0xB940 | 47424 | 1 | Not displayed on the GUI. The gains of the old interface are different. This function is used only to support the batch settings of the SmartLogger.
821 | react ive pow er cont rol mod e | RW | E16 |  |  | 0xB941 | 47425 | 1
822 | Reac tive fixed valu e | RW | I32 | kV ar | 1000 | 0xB942 | 47426 | 2
823 | targ et pow er facto r | RW | I16 |  | 1000 | 0xB944 | 47428 | 1
824 | Reac tive pow er adju stme nt perio d | RW | U16 | s | 10 | 0xB945 | 47429 | 1
825 | Adju sting Dea d Zone | RW | U16 |  | 1000 | 0xB946 | 47430 | 1
826 | Com pens atin g dela y | RW | U16 | s | 10 | 0xB947 | 47431 | 1
827 | Failu re prot ectio n react ive pow er limit [PF] | RW | I16 |  | 1000 | 0xB948 | 47432 | 1 | This parameter is displayed only when Communication Disconnection Failure Protection is set to Enabled and Reactive Power Mode is set to Power Factor.
828 | Plan t capa city | RW | U32 | k W | 1000 | 0xB949 | 47433 | 2
829 | Pow er plan t DC capa city | RW | U32 | k W | 1000 | 0xB94B | 47435 | 2
830 | [Re mot e Outp ut] Certif icate | RW | E16 |  |  | 0xB94D | 47437 | 1 | Note: "Output Control" is a direct reference in Japanese name, which essentially expresses the active output control under server scheduling. Currently, this function is required only by Japan. Update the name when the general function requires it. 20190223 Shen Yanbai
831 | [Re mot e outp ut] PV plan t ID | RW | MLD |  |  | 0xB94E | 47438 | 13 | Only 26 digits are supported.
832 | [Re mot e outp ut] Rem ote outp ut cont rol serv er | RW | STR |  |  | 0xB95B | 47451 | 30 | Other server addresses can be manually entered.
833 | [Re mot e Outp ut] Rem ote Outp ut Cont rol Time | RW | U16 | mi n | 1 | 0xB979 | 47481 | 1 | It refers to the time that the output of the plant is controlled from 0% to 100%.
834 | [Re mot e outp ut] Con necti ng to the disp atch serv er | WO | U16 |  | 1 | 0xB97A | 47482 | 1
835 | close d loop cont rolle r | RW | E16 |  |  | 0xB97B | 47483 | 1 | Note: The external controller uses the exponential data source or Dongle. In this case, the inverter does not perform the closed-loop control algorithm.
836 | [Loc al Acce ss] Link Enab led | RW | E16 |  |  | 0xB9EA | 47594 | 1
837 | [Loc al acce ss] Clien t 1 IP addr ess | RW | IPv4 |  | 1 | 0xB9EB | 47595 | 2
838 | Sche dule Task | RW | E16 |  |  | 0xBA3A | 47674 | 1 | South Australia Dynamic Feeder Requirements
839 | Maxi mu m Feed Grid Pow er Defa ult | RW | I32 | k W | 1000 | 0xBA3B | 47675 | 2 | Power limit on the grid-tied point when the default task is executed for the dynamic feeder network in South Australia.
840 | Defa ult activ e pow er chan ge gradi ent | RW | U32 | %/ s | 1000 | 0xBA3D | 47677 | 2 | Power change rate during switchover between the default task and the planned task in South Australia dynamic feeder network requirements
841 | Feed ing pow er over- thres hold prot ectio n shut dow n | RW | U16 | 1 |  | 0xBB4E | 47950 | 1
842 | Feed thres hold - cross ing prot ectio n shut dow n thres hold | RW | I32 | 10 00 |  | 0xBB4F | 47951 | 2
843 | Feed thres hold - cross ing prot ectio n shut dow n time | RW | U16 | 1 |  | 0xBB51 | 47953 | 1
844 | [Ma nage men t Syst em - 1] Man age men t Syst em Acce ss | RW | U16 | N/ A |  | 0xBB95 | 48021 | 1
845 | [Ma nage men t Syst em- 1] Prot ocol Type | RW | E16 |  |  | 0xBBD7 | 48087 | 1 | Automatically adapt to the "1" protocol for the SkyTeam OEM model.
846 | Grou nd short circu it prot ectio n | RW | E16 |  |  | 0xBBDA | 48090 | 1

## A1_Alarm_Info
Table 5-1 Alarm Information
No. | Alarm Group | Bit | Alarm Name | Alarm ID | Level
1 | Alarm 1 | 0 | High String Input Voltage | 2001 | Major
2 | Alarm 1 | 1 | DC Arc Fault[1] | 2002 | Major
3 | Alarm 1 | 2 | String Reverse Connection | 2011 | Major
4 | Alarm 1 | 3 | String Current Backfeed | 2012 | Warning
5 | Alarm 1 | 4 | Abnormal String Power | 2013 | Warning
6 | Alarm 1 | 5 | AFCI Self-Check Fail.[1] | 2021 | Major
7 | Alarm 1 | 6 | Phase Wire Short-Circuited to PE | 2031 | Major
8 | Alarm 1 | 7 | Grid Loss | 2032 | Major
9 | Alarm 1 | 8 | Grid Undervoltage | 2033 | Major
10 | Alarm 1 | 9 | Grid Overvoltage | 2034 | Major
11 | Alarm 1 | 10 | Grid Volt. Imbalance | 2035 | Major
12 | Alarm 1 | 11 | Grid Overfrequency | 2036 | Major
13 | Alarm 1 | 12 | Grid Underfrequency | 2037 | Major
14 | Alarm 1 | 13 | Unstable Grid Frequency | 2038 | Major
15 | Alarm 1 | 14 | Output Overcurrent | 2039 | Major
16 | Alarm 1 | 15 | Output DC Component Overhigh | 2040 | Major
17 | Alarm 2 | 0 | Abnormal Residual Current | 2051 | Major
18 | Alarm 2 | 1 | Abnormal Grounding | 2061 | Major
19 | Alarm 2 | 2 | Low Insulation Resistance | 2062 | Major
20 | Alarm 2 | 3 | Overtemperature | 2063 | Minor
21 | Alarm 2 | 4 | Device Fault | 2064 | Major
22 | Alarm 2 | 5 | Upgrade Failed or Version Mismatch | 2065 | Minor
23 | Alarm 2 | 6 | License Expired | 2066 | Warning
24 | Alarm 2 | 7 | Faulty Monitoring Unit | 61440 | Minor
25 | Alarm 2 | 8 | Faulty Power Collector[2] | 2067 | Major
26 | Alarm 2 | 9 | Battery abnormal | 2068 | Minor
27 | Alarm 2 | 10 | Active Islanding | 2070 | Major
28 | Alarm 2 | 11 | Passive Islanding | 2071 | Major
29 | Alarm 2 | 12 | Transient AC Overvoltage | 2072 | Major
30 | Alarm 2 | 13 | Peripheral port short circuit[3] | 2075 | Warning
31 | Alarm 2 | 14 | Churn output overload[4] | 2077 | Major
32 | Alarm 2 | 15 | Abnormal PV module configuration | 2080 | Major
33 | Alarm 3 | 0 | Optimizer fault[5] | 2081 | Warning
34 | Alarm 3 | 1 | Built-in PID operation abnormal[6] | 2085 | Minor
35 | Alarm 3 | 2 | High input string voltage to ground. | 2014 | Major
36 | Alarm 3 | 3 | External Fan Abnormal | 2086 | Major
37 | Alarm 3 | 4 | Battery Reverse Connection[7] | 2069 | Major
38 | Alarm 3 | 5 | On-grid/Off-grid controller abnormal[4] | 2082 | Major
39 | Alarm 3 | 6 | PV String Loss | 2015 | Warning
40 | Alarm 3 | 7 | Internal Fan Abnormal | 2087 | Major
41 | Alarm 3 | 8 | DC Protection Unit Abnormal[8] | 2088 | Major

## A2_cosφ_P_Curve
Table 5-2 cosφ-P/Pn Characteristic Curve
Description | Data Type | Gain | Unit | Value Range
Number of points | U16 | 1 | N/A | [2, 10]
P/P value at point 1 n | U16 | 10 | % | [0, 100]
cosφ value at point 1 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 2 n | U16 | 10 | % | [0, 100]
cosφ value at point 2 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 3 n | U16 | 10 | % | [0, 100]
cosφ value at point 3 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 4 n | U16 | 10 | % | [0, 100]
cosφ value at point 4 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 5 n | U16 | 10 | % | [0, 100]
cosφ value at point 5 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 6 n | U16 | 10 | % | [0, 100]
cosφ value at point 6 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 7 n | U16 | 10 | % | [0,100]
cosφ value at point 7 | I16 | 1000 | N/A | (–1,–0.8]U[0.8,1]
P/P value at point 8 n | U16 | 10 | % | [0, 100]
cosφ value at point 8 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 9 n | U16 | 10 | % | [0, 100]
cosφ value at point 9 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/P value at point 10 n | U16 | 10 | % | [0, 100]
cosφ value at point 10 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
Number of points | U16 | 1 | N/A | [2, 10]
U/U value at point 1 n | U16 | 10 | % | [80, 136]
Q/S value at point 1 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 2 n | U16 | 10 | % | [80, 136]
Q/S value at point 2 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 3 n | U16 | 10 | % | [80, 136]
Q/S value at point 3 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 4 n | U16 | 10 | % | [80, 136]
Q/S value at point 4 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 5 n | U16 | 10 | % | [80, 136]
Q/S value at point 5 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 6 n | U16 | 10 | % | [80, 136]
Q/S value at point 6 | I16 | 1000 | N/A | [–0.6, 0.6]

## A3_Q_U_Curve
Table 5-3 Q-U Characteristic Curve
Description | Data Type | Gain | Unit | Value Range
Number of points | U16 | 1 | N/A | [2, 10]
U/U value at point 1 n | U16 | 10 | % | [80, 136]
Q/S value at point 1 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 2 n | U16 | 10 | % | [80, 136]
Q/S value at point 2 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 3 n | U16 | 10 | % | [80, 136]
Q/S value at point 3 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 4 n | U16 | 10 | % | [80, 136]
Q/S value at point 4 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 5 n | U16 | 10 | % | [80, 136]
Q/S value at point 5 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 6 n | U16 | 10 | % | [80, 136]
Q/S value at point 6 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 7 n | U16 | 10 | % | [80, 136]
Q/S value at point 7 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 8 n | U16 | 10 | % | [80, 136]
Q/S value at point 8 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 9 n | U16 | 10 | % | [80, 136]
Q/S value at point 9 | I16 | 1000 | N/A | [–0.6, 0.6]
U/U value at point 10 n | U16 | 10 | % | [80, 136]
Q/S value at point 10 | I16 | 1000 | N/A | [–0.6, 0.6]

## A4_PF_U_Curve
Table 5-4 PF-U Characteristic Curve
Description | Data Type | Gain | Unit | Value Range
Number of points | U16 | 1 | N/A | [2, 10]
U/U value at point 1 n | U16 | 10 | % | [80, 136]
PF value at point 1 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 2 n | U16 | 10 | % | [80, 136]
PF value at point 2 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 3 n | U16 | 10 | % | [80, 136]
PF value at point 3 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 4 n | U16 | 10 | % | [80, 136]
PF value at point 4 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 5 n | U16 | 10 | % | [80, 136]
PF value at point 5 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 6 n | U16 | 10 | % | [80, 136]
PF value at point 6 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 7 n | U16 | 10 | % | [80, 136]
PF value at point 7 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 8 n | U16 | 10 | % | [80, 136]
PF value at point 8 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 9 n | U16 | 10 | % | [80, 136]
PF value at point 9 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/U value at point 10 n | U16 | 10 | % | [80, 136]
PF value at point 10 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]

## A5_Grid_Codes
Table 5-5 List of Grid Codes
No. | Standard | Applicable Country / Region
0 | VDE-AR-N-4105 | Germany
1 | NB/T 32004 | China
2 | UTE C 15-712-1(A) | France
3 | UTE C 15-712-1(B) | France
4 | UTE C 15-712-1(C) | France
5 | VDE 0126-1-1-BU | Bulgaria
6 | VDE 0126-1-1-GR(A) | Greece
7 | VDE 0126-1-1-GR(B) | Greece
8 | BDEW-MV | Germany
9 | G59-England | UK
10 | G59-Scotland | UK
11 | G83-England | UK
12 | G83-Scotland | UK
13 | CEI0-21 | Italy
14 | EN50438-CZ | Czech Republic
15 | RD1699/661 | Spain
16 | RD1699/661-MV480 | Spain
17 | EN50438-NL | Netherlands
18 | C10/11 | Belgium
19 | AS4777 | Australia
20 | IEC61727 | General
21 | Custom (50 Hz) | Custom
22 | Custom (60 Hz) | Custom
23 | CEI0-16 | Italy
24 | CHINA-MV480 | China
25 | CHINA-MV | China
26 | TAI-PEA | Thailand
27 | TAI-MEA | Thailand
28 | BDEW-MV480 | Germany
29 | Custom MV480 (50 Hz) | Custom
30 | Custom MV480 (60 Hz) | Custom
31 | G59-England-MV480 | UK
32 | IEC61727-MV480 | General
33 | UTE C 15-712-1-MV480 | France
34 | TAI-PEA-MV480 | Thailand
35 | TAI-MEA-MV480 | Thailand
36 | EN50438-DK-MV480 | Denmark
37 | Japan standard (50 Hz) | Japan
38 | Japan standard (60 Hz) | Japan
39 | EN50438-TR-MV480 | Turkey
40 | EN50438-TR | Turkey
41 | C11/C10-MV480 | Belgium
42 | Philippines | Philippines
43 | Philippines-MV480 | Philippines
44 | AS4777-MV480 | Australia
45 | NRS-097-2-1 | South Africa
46 | NRS-097-2-1-MV480 | South Africa
47 | KOREA | South Korea
48 | IEEE 1547-MV480 | USA
49 | IEC61727-60Hz | General
50 | IEC61727-60Hz-MV480 | General
51 | CHINA_MV500 | China
52 | ANRE | Romania
53 | ANRE-MV480 | Romania
54 | ELECTRIC RULE NO.21- MV480 | California, USA
55 | HECO-MV480 | Hawaii, USA
56 | PRC_024_Eastern-MV480 | Eastern USA
57 | PRC_024_Western- MV480 | Western USA
58 | PRC_024_Quebec-MV480 | Quebec, Canada
59 | PRC_024_ERCOT-MV480 | Texas, USA
60 | PO12.3-MV480 | Spain
61 | EN50438_IE-MV480 | Ireland
62 | EN50438_IE | Ireland
63 | IEEE 1547a-MV480 | USA
64 | Japan standard (MV420-50 Hz) | Japan
65 | Japan standard (MV420-60 Hz) | Japan
66 | Japan standard (MV440-50 Hz) | Japan
67 | Japan standard (MV440-60 Hz) | Japan
68 | IEC61727-50Hz-MV500 | General
70 | CEI0-16-MV480 | Italy
71 | PO12.3 | Spain
72 | Japan standard (MV400-50 Hz) | Japan
73 | Japan standard (MV400-60 Hz) | Japan
74 | CEI0-21-MV480 | Italy
75 | KOREA-MV480 | South Korea
76 | Egypt ETEC | Egypt
77 | Egypt ETEC-MV480 | Egypt
78 | CHINA_MV800 | China
79 | IEEE 1547-MV600 | USA
80 | ELECTRIC RULE NO.21- MV600 | California, USA
81 | HECO-MV600 | Hawaii, USA
82 | PRC_024_Eastern-MV600 | Eastern USA
83 | PRC_024_Western- MV600 | Western USA
84 | PRC_024_Quebec-MV600 | Quebec, Canada
85 | PRC_024_ERCOT-MV600 | Texas, USA
86 | IEEE 1547a-MV600 | USA
87 | EN50549-LV | Ireland
88 | EN50549-MV480 | Ireland
89 | Jordan-Transmission | Jordan
90 | Jordan-Transmission- MV480 | Jordan
91 | NAMIBIA | Namibia
92 | ABNT NBR 16149 | Brazil
93 | ABNT NBR 16149- MV480 | Brazil
94 | SA_RPPs | South Africa
95 | SA_RPPs-MV480 | South Africa
96 | INDIA | India
97 | INDIA-MV500 | India
98 | ZAMBIA | Zambia
99 | ZAMBIA-MV480 | Zambia
100 | Chile | Chile
101 | Chile-MV480 | Chile
102 | CHINA-MV500-STD | China
103 | CHINA-MV480-STD | China
104 | Mexico-MV480 | Mexico
105 | Malaysian | Malaysia
106 | Malaysian-MV480 | Malaysia
107 | KENYA_ETHIOPIA | East Africa
108 | KENYA_ETHIOPIA- MV480 | East Africa
109 | G59-England-MV800 | UK
110 | NIGERIA | Nigeria
111 | NIGERIA-MV480 | Nigeria
112 | DUBAI | Dubai
113 | DUBAI-MV480 | Dubai
114 | Northern Ireland | Northern Ireland
115 | Northern Ireland-MV480 | Northern Ireland
116 | Cameroon | Cameroon
117 | Cameroon-MV480 | Cameroon
118 | Jordan-Distribution | Jordan
119 | Jordan-Distribution- MV480 | Jordan
120 | Custom MV600-50 Hz | Custom
121 | AS4777-MV800 | Australia
122 | INDIA-MV800 | India
123 | IEC61727-MV800 | General
124 | BDEW-MV800 | Germany
125 | ABNT NBR 16149- MV800 | Brazil
126 | UTE C 15-712-1-MV800 | France
127 | Chile-MV800 | Chile
128 | Mexico-MV800 | Mexico
129 | EN50438-TR-MV800 | Turkey
130 | TAI-PEA-MV800 | Thailand
131 | Philippines-MV800 | Philippines
132 | Malaysian-MV800 | Malaysia
133 | NRS-097-2-1-MV800 | South Africa
134 | SA_RPPs-MV800 | South Africa
135 | Jordan-Transmission- MV800 | Jordan
136 | Jordan-Distribution- MV800 | Jordan
137 | Egypt ETEC-MV800 | Egypt
138 | DUBAI-MV800 | Dubai
139 | SAUDI-MV800 | Saudi Arabia
140 | EN50438_IE-MV800 | Ireland
141 | EN50549-MV800 | Ireland
142 | Northern Ireland-MV800 | Northern Ireland
143 | CEI0-21-MV800 | Italy
144 | IEC 61727-MV800-60Hz | General
145 | NAMIBIA_MV480 | Namibia
146 | Japan (LV202-50 Hz) | Japan
147 | Japan (LV202-60 Hz) | Japan
148 | Pakistan-MV800 | Pakistan
149 | BRASIL-ANEEL-MV800 | Brazil
150 | Israel-MV800 | Israel
151 | CEI0-16-MV800 | Italy
152 | ZAMBIA-MV800 | Zambia
153 | KENYA_ETHIOPIA- MV800 | East Africa
154 | NAMIBIA_MV800 | Namibia
155 | Cameroon-MV800 | Cameroon
156 | NIGERIA-MV800 | Nigeria
157 | ABUDHABI-MV800 | Abu Dhabi
158 | LEBANON | Lebanon
159 | LEBANON-MV480 | Lebanon
160 | LEBANON-MV800 | Lebanon
161 | ARGENTINA-MV800 | Argentina
162 | ARGENTINA-MV500 | Argentina
163 | Jordan-Transmission-HV | Jordan
164 | Jordan-Transmission- HV480 | Jordan
165 | Jordan-Transmission- HV800 | Jordan
166 | TUNISIA | Tunisia
167 | TUNISIA-MV480 | Tunisia
168 | TUNISIA-MV800 | Tunisia
169 | JAMAICA-MV800 | Jamaica
170 | AUSTRALIA-NER | Australia
171 | AUSTRALIA-NER-MV480 | Australia
172 | AUSTRALIA-NER-MV800 | Australia
173 | SAUDI | Saudi Arabia
174 | SAUDI-MV480 | Saudi Arabia
175 | Ghana-MV480 | Ghana
176 | Israel | Israel
177 | Israel-MV480 | Israel
178 | Chile-PMGD | Chile
179 | Chile-PMGD-MV480 | Chile
180 | VDE-AR-N4120-HV | Germany
181 | VDE-AR-N4120-HV480 | Germany
182 | VDE-AR-N4120-HV800 | Germany
183 | IEEE 1547-MV800 | USA
184 | Nicaragua-MV800 | Nicaragua
185 | IEEE 1547a-MV800 | USA
186 | ELECTRIC RULE NO.21- MV800 | California, USA
187 | HECO-MV800 | Hawaii, USA
188 | PRC_024_Eastern-MV800 | Eastern USA
189 | PRC_024_Western- MV800 | Western USA
190 | PRC_024_Quebec-MV800 | Quebec, Canada
191 | PRC_024_ERCOT-MV800 | Texas, USA
192 | Custom-MV800-50Hz | Custom
193 | RD1699/661-MV800 | Spain
194 | PO12.3-MV800 | Spain
195 | Mexico-MV600 | Mexico
196 | Vietnam-MV800 | Vietnam
197 | CHINA-LV220/380 | China
198 | SVG-LV | Dedicated
199 | Vietnam | Vietnam
200 | Vietnam-MV480 | Vietnam
201 | Chile-PMGD-MV800 | Chile
202 | Ghana-MV800 | Ghana
203 | TAIPOWER | Taiwan
204 | TAIPOWER-MV480 | Taiwan
205 | TAIPOWER-MV800 | Taiwan
206 | IEEE 1547-LV208 | USA
207 | IEEE 1547-LV240 | USA
208 | IEEE 1547a-LV208 | USA
209 | IEEE 1547a-LV240 | USA
210 | ELECTRIC RULE NO.21- LV208 | USA
211 | ELECTRIC RULE NO.21- LV240 | USA
212 | HECO-O+M+H-LV208 | USA
213 | HECO-O+M+H-LV240 | USA
214 | PRC_024_Eastern-LV208 | USA
215 | PRC_024_Eastern-LV240 | USA
216 | PRC_024_Western-LV208 | USA
217 | PRC_024_Western-LV240 | USA
218 | PRC_024_ERCOT-LV208 | USA
219 | PRC_024_ERCOT-LV240 | USA
220 | PRC_024_Quebec-LV208 | USA
221 | PRC_024_Quebec-LV240 | USA
222 | ARGENTINA-MV480 | Argentina
223 | Oman | Oman
224 | Oman-MV480 | Oman
225 | Oman-MV800 | Oman
226 | Kuwait | Kuwait
227 | Kuwait-MV480 | Kuwait
228 | Kuwait-MV800 | Kuwait
229 | Bangladesh | Bangladesh
230 | Bangladesh-MV480 | Bangladesh
231 | Bangladesh-MV800 | Bangladesh
232 | Chile-Net_Billing | Chile
233 | EN50438-NL-MV480 | Netherlands
234 | Bahrain | Bahrain
235 | Bahrain-MV480 | Bahrain
236 | Bahrain-MV800 | Bahrain
238 | Japan-MV550-50Hz | Japan
239 | Japan-MV550-60Hz | Japan
241 | ARGENTINA | Argentina
242 | KAZAKHSTAN-MV800 | Kazakhstan
243 | Mauritius | Mauritius
244 | Mauritius-MV480 | Mauritius
245 | Mauritius-MV800 | Mauritius
246 | Oman-PDO-MV800 | Oman
247 | EN50438-SE | Sweden
248 | TAI-MEA-MV800 | Thailand
249 | Pakistan | Pakistan
250 | Pakistan-MV480 | Pakistan
251 | PORTUGAL-MV800 | Portugal
252 | HECO-L+M-LV208 | USA
253 | HECO-L+M-LV240 | USA
254 | C10/11-MV800 | Belgium
255 | Austria | Austria
256 | Austria-MV480 | Austria
257 | G98 | UK
258 | G99-TYPEA-LV | UK
259 | G99-TYPEB-LV | UK
260 | G99-TYPEB-HV | UK
261 | G99-TYPEB-HV-MV480 | UK
262 | G99-TYPEB-HV-MV800 | UK
263 | G99-TYPEC-HV-MV800 | UK
264 | G99-TYPED-MV800 | UK
265 | G99-TYPEA-HV | UK
266 | CEA-MV800 | India
267 | EN50549-MV400 | Europe
268 | VDE-AR-N4110 | Germany
269 | VDE-AR-N4110-MV480 | Germany
270 | VDE-AR-N4110-MV800 | Germany
271 | Panama-MV800 | Panama
272 | North Macedonia- MV800 | Nprth Macedonia
273 | NTS | Spain
274 | NTS-MV480 | Spain
275 | NTS-MV800 | Spain

## A6_ES_TOU_Periods
Table 5-6 Time-of-Use Electricity Price Periods
Description | Data Type | Gain | Unit | Value Range
Number of periods | U16 | 1 | N/A | [0, 10]
Start time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Electricity price in period 1 | U32 | 1000 | N/A | N/A
Start time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Electricity price in period 2 | U32 | 1000 | N/A | N/A
... | ... | ... | ... | ...
Start time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Electricity price in period 10 | U32 | 1000 | N/A | N/A

## A7_ES_Fixed_Periods
Table 5-7 Fixed Charging/Discharging Periods
Description | Data Type | Gain | Unit | Value Range
Number of periods | U16 | 1 | N/A | [0, 10]
Start time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Charging and discharging power in period 1 | I32 | 1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.
Start time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Charging and discharging power in period 2 | I32 | 1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.
... | ... | ... | ... | ...
Start time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Charging and discharging power in period 10 | I32 | 1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.

## A8_Optimizer_SysInfo
4.1 Optimizer System Information Format
Data | Length (Byte) | Remarks
Feature data of optimizer 1 | 108 | For details about the data domain definition, see Table2 Feature data unit format(V102).
Feature data of optimizer 2 | 108 | N/A
... | ... | N/A
Feature data of optimizer N | 108 | N/A

## A9_Optimizer_Realtime
4.2 Optimizer Real-time Data Format
Data | Length (Byte) | Remarks
Optimizer address | 2 | RS485 address
Online status | 2 | 0: offline 1: online 2: disconnected
String number | 2 | N/A
Position in current string | 2 | relative positive connection starting point
SN | 20 | N/A
Software version | 30 | N/A
Alias | 20 | N/A
Model | 30 | N/A
File version | 4 | V101
Reserved | 8 | N/A
Optimizer data unit 1 | N | 12 + 26 x Number of optimizers , For details about the definition of this unit, see the data unit format.
Optimizer data unit 2 | N | N/A
... | N/A | N/A
Optimizer data unit n | N | n indicates the number of data records that meet the filter condition. Each piece of data contains all optimizer data for a time node.
Time | 4 | Epoch seconds, local time
Reserved | 4 | N/A
Length | 2 | N/A
Number of optimizers | 2 | N/A
Real-time data of optimizer 1 | 26 | For details about the definition of this unit, see the real-time data format.
Real-time data of optimizer 2 | 26 | N/A
... | ... | N/A
Real-time data of optimizer n | 26 | n is the number of optimizers.
Optimizer address | 2 | Logical communication address
Output power | 2 | Gain: 10 Unit: W
Voltage to ground | 2 | Gain: 10 Unit: V
Alarm | 4 | Bit00: input overvoltage Bit01: input undervoltage Bit02: output overvoltage Bit04: overtemperature Bit06: output short circuit Bit07: EEPROM fault Bit08: internal hardware fault Bit09: abnormal voltage to ground Bit 10: power-off due to heartbeat timeout Bit 11: fast shutdown Bit 12: request escape alarm Bit 13: version mismatch alarm Bit 16: input overvoltage Bit 17: overtemperature Bit 18: output short circuit Bit 19: internal hardware fault Bit 20: version mismatch alarm Bit 21: backfeed alarm Bit 22: abnormal output voltage Bit 23: upgrade failure Bit 31: alarm display selection, 1=Display bit 16 to bit 30 alarms, 0: Bits 0 to 15 are displayed.
Output voltage | 2 | Gain: 10 Unit: V
Output current | 2 | Gain: 100 Unit: A
Input voltage | 2 | Gain: 10 Unit: V
Input current | 2 | Gain: 100 Unit: A
Temperature | 2 | Gain: 10 Unit: °C
Running status | 2 | 0: offline 1: standby 3: faulty 4: running 12: power-off
Accumulated energy yield | 4 | Gain: 1000 Unit: kWh