## Protocol Overview
Solis RS485 Modbus RTU – Protocol Overview
Parameter | Value | Notes
Slave Address | 1 ~ 247 | Broadcast: 0xFF (write-only, no response)
Baud Rate | 9600 bps
Parity | None
Data Bits | 8
Stop Bits | 1
Mode | RTU
Frame Interval | >300 ms | Recommended max frame = 100 bytes (50 registers)
Function Codes | 03H | Read Holding Registers (40001-49999) – read setting content
| 04H | Read Input Registers (30001-39999) – read operation info
| 06H | Write Single Holding Register (40001-49999)
| 10H | Write Multiple Holding Registers (40001-49999)
Byte Order | Big-Endian | High byte first; except 02H: low byte first. EPM section: Little-Endian
CRC | CRC-16 (lookup table) | High byte first

## Data Types
Data Type Definitions
Type | Description | Byte Order
U16 | 2-byte unsigned integer | High byte first then low byte
S16 | 2-byte signed integer | High byte first then low byte
U32 | 4-byte unsigned integer | High word first, within each word high byte first
S32 | 4-byte signed integer | High word first, within each word high byte first

## Model Parameter (FC04)
5.1 Inverter Model Parameter (FC=04, no address offset)
Register (Dec) | Name | Type | Unit | Remark
35000 | SOLIS inverter type definition | U16 | — | 1110H=Single Phase (0.7-8K1P/7-10K1P/no-screen) 1111H=Single phase microinverter (0.6-0.8K1P) 1120H=Three Phase (5-25K3P/5-30K3P no-screen) 1121H=Three Phase (25-50K/50-70K/80-110K/90-136K/125K) 1123H=Three Phase MAX/PRO 1124H=Three Phase 320K 0000H=Undefined model High 8 bits = protocol major ver; Low 8 bits = machine type

## Operation Info (FC04)
5.2 Operation Info (FC=04, address offset NOT needed)
Register (Dec) | Name | Type | Unit | Remark
3000 | Product model | U16 | 1 | Inverter model number; contact technical support for details
3001 | DSP software version | U16 | 1 | 0xAABB: AA=slave DSP major ver, BB=main DSP major ver
3002 | HMI Major Version | U16 | 1 | High byte empty; low byte = major version number
3003 | AC output type | U16 | 1 | 0=Single phase, 1=3-phase 4-wire, 2=Phase 3-wire, 3=Phase 3-wire/3-phase
3004 | DC input type | U16 | 1 | 0=1 DC input, 1=2 DC input … 19=20 DC input. Determines PV/MPPT register selection
3005-3006 | Active power | S32 | 1 W
3007-3008 | Total DC output power | U32 | 1 W
3009-3010 | Total energy | U32 | 1 kWh | Associate with 3117 for decimal part
3011-3012 | Energy this month | U32 | 1 kWh
3013-3014 | Energy last month | U32 | 1 kWh
3015 | Energy today | U16 | 0.1 kWh
3016 | Reserve | U16 | 0.1 kWh
3017-3018 | Energy this year | U32 | 1 kWh
3019-3020 | Energy last year | U32 | 1 kWh
3021 | HMI version | U16 | 1 | 0xAABB: AA=minor, BB=major
3022 | DC voltage 1 | U16 | 0.1 V | See 3004 for MPPT/PV register routing
3023 | DC current 1 | U16 | 0.1 A
3024 | DC voltage 2 | U16 | 0.1 V
3025 | DC current 2 | U16 | 0.1 A
3026 | DC voltage 3 | U16 | 0.1 V
3027 | DC current 3 | U16 | 0.1 A
3028 | DC voltage 4 | U16 | 0.1 V
3029 | DC current 4 | U16 | 0.1 A
3030 | Alarm code data | U16 | 1 | See Appendix 1; use with 3044 to subdivide fault
3031 | Initialize ground voltage value | U16 | 0.1 V
3032 | DC busbar voltage | U16 | 0.1 V
3033 | DC half-busbar voltage | U16 | 0.1 V
3034 | AB line voltage / A phase voltage | U16 | 0.1 V | 3003=1: phase voltage; =2: line voltage (230K only)
3035 | BC line voltage / B phase voltage | U16 | 0.1 V
3036 | CA line voltage / C phase voltage | U16 | 0.1 V
3037 | A phase current | U16 | 0.1 A
3038 | B phase current | U16 | 0.1 A
3039 | C phase current | U16 | 0.1 A
3040 | Reserved | U16 | —
3041 | Standard working mode | U16 | 1 | 00=No response, 01=Volt-watt, 02=Volt-var, 03=Fixed PF, 04=Fix reactive power, 05=Power-PF, 06=Rule21 Volt-watt
3042 | Inverter temperature | S16 | 0.1 °C | AC NTC (IGBT)
3043 | Grid Frequency | U16 | 0.01 Hz
3044 | Inverter status | U16 | 1 | See Appendix 1; use with 3030 to subdivide info
3045-3046 | Limited active power adj. rated power output | S32 | 1 W | Max active power output; associated with FC06 3070
3047-3048 | Reactive power reg. rated power output | S32 | 1 Var | Max reactive power output; associated with FC06 3071
3049 | Inverter control word | U16 | 1 | See Appendix 3
3050 | Actual value of limited active power | U16 | 1% | 0-100%; 10000=100%
3051 | Actual adjust value of power factor | S16 | 0.01 | Range -1~-0.80, 0.80~1; 1000=1.00
3052 | Actual power factor adjustment | S16 | 0.001 | For standard mode 3 fixed PF; range -1~-0.8, 0.8~1
3053 | Reactive power value | S16 | 1% | Range -60%~+60%; 6000=60%
3054 | Standard | U16 | 1 | See Appendix 4
3055 | Power curve number | U16 | 1
3056-3057 | Reactive power value | S32 | 1 Var
3058-3059 | Apparent power value | S32 | 1 VA
3060 | Real-time power factor | S16 | 0.001 | Only 50-70K/255K series
3061 | Inverter SN_1 | U16 | 1 | Hex; SN[3:0] in little-endian pairs
3062 | Inverter SN_2 | U16 | 1
3063 | Inverter SN_3 | U16 | 1
3064 | Inverter SN_4 | U16 | 1
3065-3072 | Reserved | U16 | 1
3073 | System time – year | U16 | 1 | 0-99
3074 | System time – month | U16 | 1 | 1-12
3075 | System time – day | U16 | 1 | 1-31
3076 | System time – hour | U16 | 1 | 0-23
3077 | System time – minute | U16 | 1 | 0-59
3078 | System time – second | U16 | 1 | 0-59
3079 | DRM | U16 | 1 | DRM Number
3080-3085 | Reserved | U16 | —
3086 | Leakage current protection value | U16 | 1 mA
3087 | Insulation resistance protection value | U16 | 1 kΩ
3088-3089 | Reserved | U16 | —
3090 | Power limit switch | U16 | 1 | 0xAA=enabled; 0x55=off (power returns to 100%). Feedback of hold reg 3070
3091 | Reactive power switch | U16 | 1 | 0x55=Off; 0xA1=reactive ratio valid; 0xA2=PF02 setting valid
3092 | Real Time PV insulation resistance | U16 | 1 kΩ | Range 0-32000 kΩ
3093 | Inverter Temperature | S16 | 0.1 °C
3094 | Inverter installation Method | U16 | 1 | 0=90° (default); 1=15°
3095 | Derating/Limit status information | U16 | 1 | 255K series; See Appendix 2
3096 | Fault Code 01 | U16 | 1 | See Appendix 2
3097 | Fault Code 02 | U16 | 1 | See Appendix 2
3098 | Fault Code 03 | U16 | 1 | See Appendix 2
3099 | Fault Code 04 | U16 | 1 | See Appendix 2
3100 | Fault Code 05 | U16 | 1 | See Appendix 2
3101-3105 | Reserved | U16 | —
3106 | Ileak Real time data | U16 | 1 mA
3107 | Grid filter number | U16 | 1
3108 | Master dsp sub version | U16 | 1 | Low byte only; combine with 3001 for full version
3109 | Real time power percentage | U16 | 0.01% | Real-time power / rated power
3110 | Inverter rated apparent power | U16 | 10 VA
3111 | Internal EPM Switch | U16 | 1 | Value varies by model; see PDF §5.2
3112 | Internal EPM backflow power | S16 | 100 W | + to grid; - from grid
3113 | Internal EPM failsafe switch | U16 | 1 | BIT00=FailSafe; BIT01=MET-CT FailSafe
3114 | Internal EPM real time backflow power | U16 | 10 W
3115 | Internal EPM Hard Switch | U16 | 1 | 00=Null; 01=ON; 02=OFF
3116 | Internal EPM Hard Limit | S16 | 100 W
3117 | Total Energy – Decimal Part | U16 | 0.001 kWh | Associate with 3009-3010
3118 | CT Link Test | U16 | 1 | 0=OK; 1=Fail; 2=Can't judge
3119 | G100 Running Status | U16 | 1 | 1=Normal; 2=Overrun; 3=Fault; 4=Off
3120 | ARC-Fault Number of occurrences | U16 | 1
3121 | Italy Single Self-Test | U16 | 1 | 01-30: test items; see PDF §5.2
3122 | Italy Full Self-test | U16 | 1 | 1=Single self-test; 2=Full self-test
3123 | 01-59.S1 Voltage | U16 | 0.1 V
3124 | 01-59.S1 Time | U16 | 1 ms
3125 | 02-59.S2 Voltage | U16 | 0.1 V
3126 | 02-59.S2 Time | U16 | 1 ms
3127 | 03-27.S1 Voltage | U16 | 0.1 V
3128 | 03-27.S1 Time | U16 | 1 ms
3129 | 04-27.S2 Voltage | U16 | 0.1 V
3130 | 04-27.S2 Time | U16 | 1 ms
3131 | 05-81>.S1 Frequency | U16 | 0.01 Hz
3132 | 05-81>.S1 Time | U16 | 1 ms
3133 | 06-81<.S1 Frequency | U16 | 0.01 Hz
3134 | 06-81<.S1 Time | U16 | 1 ms
3135 | 07-81>.S2F Frequency | U16 | 0.01 Hz
3136 | 07-81>.S2F Time | U16 | 1 ms
3137 | 08-81<.S2F Frequency | U16 | 0.01 Hz
3138 | 08-81<.S2F Time | U16 | 1 ms
3139 | 09-81>.S2S Frequency | U16 | 0.01 Hz
3140 | 09-81>.S2S Time | U16 | 1 ms
3141 | 10-81<.S2S Frequency | U16 | 0.01 Hz
3142 | 10-81<.S2S Time | U16 | 1 ms
3143 | DSP1 Version | U16 | 1 | 80-110K PRO; 0xAABB: AA=slave DSP main ver, BB=master DSP main ver
3144 | DSP2 Version | U16 | 1
3145 | DSP3 Version | U16 | 1
3146 | DSP4 Version | U16 | 1
3147 | Voltage Ride-through enable switch | U16 | 1 | BIT00=LVRT; BIT01=US Rule21 VRT; BIT02=US Rule21 FRT; BIT03=Brazil LVRT; BIT04=BDEW LVRT
3148 | Voltage Ride-through enable flag bit | U16 | 1 | 0xA5=VRT disable; 0x5A=VRT enable
3149 | AFCI board model | U16 | 1 | 0=Old AFCI; 1=Lingshi; 2=TI
3150 | AFCI board Version | U16 | 1
3151 | AFCI faulty data sets | U16 | 1 | 1=HMI obtained all DSP fault data; 0=not obtained
3152 | AFCI board CT module hardware fault check | U16 | 1 | BIT00-BIT04 = Module 1-5; 0=OK; 1=Fault
3153 | AFCI board arc fault check result | U16 | 1 | 1-30=PV string; 31-35=module arc fault
3154 | Standard operating mode Status | U16 | 1 | BIT00=Volt-watt; BIT01=Volt-var; BIT02=Fixed PF; BIT03=Fix reactive; BIT04=Power-PF
3155 | Power on Display Select National Standard status | U16 | 1 | 0x0000=invalid; 0x0001=waiting; 0x0002=setting; 0x0003=complete
3156 | Reserved | U16 | —
3157 | External PID Status | U16 | 1 | BIT00=PID On/Off
3158 | Volt-Var Vref real-time value | U16 | 0.1 V
3159 | DC daily power generation | U16 | 0.1 kWh
3160 | Accuracy Flag | U16 | 1 | BIT00=1: OFD/UFR Fstart accuracy 0.001 Hz; =0: 0.01 Hz
3161 | Meter or dual 485 optional function switch | U16 | 1 | 0=meter comm; 1=dual 485 comm (5-25K series)
3162-3203 | Reserved | U16 | —
3204 | DSP1_A phase AC voltage | U16 | 0.1 V | 80-110K MAX/PRO voltage calibration
3205 | DSP1_B phase AC voltage | U16 | 0.1 V
3206 | DSP1_C phase AC voltage | U16 | 0.1 V
3207 | DSP2_A phase AC voltage | U16 | 0.1 V
3208 | DSP2_B phase AC voltage | U16 | 0.1 V
3209 | DSP2_C phase AC voltage | U16 | 0.1 V
3210 | DSP3_A phase AC voltage | U16 | 0.1 V
3211 | DSP3_B phase AC voltage | U16 | 0.1 V
3212 | DSP3_C phase AC voltage | U16 | 0.1 V
3213 | DSP4_A phase AC voltage | U16 | 0.1 V
3214 | DSP4_B phase AC voltage | U16 | 0.1 V
3215 | DSP4_C phase AC voltage | U16 | 0.1 V
3216-3219 | Reserved | U16 | —
3220 | Broadcast Batch Upgrade Flag | U16 | 1 | High 8=ARM; Low 8=DSP; 0=not support; 1=support
3221 | Inverter initial setting state | U16 | 1 | See Appendix 5
3222 | Reserved (Bit error rate HMI-DSP) | U16 | 0.1%
3223 | Safety Version | U16 | 1
3224 | AFCI SelfCheck Completed | U16 | 1
3225 | IGBT Self-Check Flag Bit | U16 | 1 | 0=not triggered; 1=triggering; 2=success; 4=end
3226 | Reserved | U16 | —
3228 | One Click Reset Enable Command Status | U16 | 1 | 0000H=Disable; 0059H=Enable (use FC06 addr 3302)
3229 | One Click Reset Operating Command Status | U16 | 1 | 0000H=Disable; 0045H=Enable; 5min timeout
3230-3247 | SN Number | U16 | 1 | ASCII; 2 chars per register (e.g. 3230='01', 3231='23')
3248-3249 | Total consumption of household loads | S32 | 0.01 kWh | Single-phase + CT load monitoring only
3250 | Meter placement | U16 | 1 | BIT00=load side; BIT01=main grid side; BIT02=24H consumption
3251 | Meter AC voltage A | U16 | 0.1 V
3252 | Meter AC current A | U16 | 0.01 A
3253 | Meter AC voltage B | U16 | 0.1 V
3254 | Meter AC current B | U16 | 0.01 A
3255 | Meter AC voltage C | U16 | 0.1 V
3256 | Meter AC current C | U16 | 0.01 A
3257-3258 | Meter Active power A | S32 | 0.001 kW
3259-3260 | Meter Active power B | S32 | 0.001 kW
3261-3262 | Meter Active power C | S32 | 0.001 kW
3263-3264 | Meter Total active power | S32 | 0.001 kW
3265-3266 | Meter Reactive power A | S32 | 1 Var
3267-3268 | Meter Reactive power B | S32 | 1 Var
3269-3270 | Meter Reactive power C | S32 | 1 Var
3271-3272 | Meter Total reactive power | S32 | 1 Var
3273-3274 | Meter Apparent power A | S32 | 1 VA
3275-3276 | Meter Apparent power B | S32 | 1 VA
3277-3278 | Meter Apparent power C | S32 | 1 VA
3279-3280 | Meter Apparent power | S32 | 1 VA
3281 | Meter Power factor | S16 | 0.001 | -1.000~-0.800, +0.800~+1.000
3282 | Meter Grid frequency | U16 | 0.01 Hz
3283-3284 | Meter Grid power total active energy | U32 | 0.01 kWh
3285-3286 | Meter Grid power transmission total active energy | U32 | 0.01 kWh
3287 | PV string voltage/current combination description | U16 | 1 | 0000H=1V:2I; 0003H=1V:3I; used with 3289-3335
3289 | PV21 Current | S16 | 0.1 A
3290 | PV22 Current | S16 | 0.1 A
3291 | PV23 Current | S16 | 0.1 A
3292 | PV24 Current | S16 | 0.1 A
3293 | PV25 Current | S16 | 0.1 A
3294 | PV26 Current | S16 | 0.1 A
3295 | PV27 Current | S16 | 0.1 A
3296 | PV28 Current | S16 | 0.1 A
3297 | PV29 Current | S16 | 0.1 A
3298 | PV30 Current | S16 | 0.1 A
3299 | Total PV Voltage | U16 | 0.1 V
3300 | Total PV Current | S16 | 0.1 A
3301 | PV1 Current | S16 | 0.1 A
3302 | PV2 Current | S16 | 0.1 A
3303 | PV3 Current | S16 | 0.1 A
3304 | PV4 Current | S16 | 0.1 A
3305 | PV5 Current | S16 | 0.1 A
3306 | PV6 Current | S16 | 0.1 A
3307 | PV7 Current | S16 | 0.1 A
3308 | PV8 Current | S16 | 0.1 A
3309 | PV9 Current | S16 | 0.1 A
3310 | PV10 Current | S16 | 0.1 A
3311 | PV11 Current | S16 | 0.1 A
3312 | PV12 Current | S16 | 0.1 A
3313 | PV13 Current | S16 | 0.1 A
3314 | PV14 Current | S16 | 0.1 A
3315 | PV15 Current | S16 | 0.1 A
3316 | PV16 Current | S16 | 0.1 A
3317 | PV17 Current | S16 | 0.1 A
3318 | PV18 Current | S16 | 0.1 A
3319 | PV19 Current | S16 | 0.1 A
3320 | PV20 Current | S16 | 0.1 A
3321 | PVStr1 Voltage | U16 | 0.1 V
3322 | PVStr2 Voltage | U16 | 0.1 V
3323 | PVStr3 Voltage | U16 | 0.1 V
3324 | PVStr4 Voltage | U16 | 0.1 V
3325 | PVStr5 Voltage | U16 | 0.1 V
3326 | PVStr6 Voltage | U16 | 0.1 V
3327 | PVStr7 Voltage | U16 | 0.1 V
3328 | PVStr8 Voltage | U16 | 0.1 V
3329 | PVStr9 Voltage | U16 | 0.1 V
3330 | PVStr10 Voltage | U16 | 0.1 V
3331 | PVStr11 Voltage | U16 | 0.1 V
3332 | PVStr12 Voltage | U16 | 0.1 V
3333 | PVStr13 Voltage | U16 | 0.1 V
3334 | PVStr14 Voltage | U16 | 0.1 V
3335 | PVStr15 Voltage | U16 | 0.1 V
3336 | PVStr16 Voltage | U16 | 0.1 V
3337 | PV31 Current | U16 | 0.1 A
3338 | PV32 Current | U16 | 0.1 A
3339-3499 | Reserve | U16 | —
3500 | MPPT 1V | U16 | 0.1 V | If 3004≥8: use 3287-3338 for PV, 3500-3546 for MPPT
3501 | MPPT 2V | U16 | 0.1 V
3502 | MPPT 3V | U16 | 0.1 V
3503 | MPPT 4V | U16 | 0.1 V
3504 | MPPT 5V | U16 | 0.1 V
3505 | MPPT 6V | U16 | 0.1 V
3506 | MPPT 7V | U16 | 0.1 V
3507 | MPPT 8V | U16 | 0.1 V
3508 | MPPT 9V | U16 | 0.1 V
3509 | MPPT 10V | U16 | 0.1 V
3510 | MPPT 11V | U16 | 0.1 V
3511 | MPPT 12V | U16 | 0.1 V
3512 | MPPT 13V | U16 | 0.1 V
3513 | MPPT 14V | U16 | 0.1 V
3514 | MPPT 15V | U16 | 0.1 V
3515-3529 | Reserve | U16 | —
3530 | MPPT 1I | S16 | 0.1 A
3531 | MPPT 2I | S16 | 0.1 A
3532 | MPPT 3I | S16 | 0.1 A
3533 | MPPT 4I | S16 | 0.1 A
3534 | MPPT 5I | S16 | 0.1 A
3535 | MPPT 6I | S16 | 0.1 A
3536 | MPPT 7I | S16 | 0.1 A
3537 | MPPT 8I | S16 | 0.1 A
3538 | MPPT 9I | S16 | 0.1 A
3539 | MPPT 10I | S16 | 0.1 A
3540 | MPPT 11I | S16 | 0.1 A
3541 | MPPT 12I | S16 | 0.1 A
3542 | MPPT 13I | S16 | 0.1 A
3543 | MPPT 14I | S16 | 0.1 A
3544 | MPPT 15I | S16 | 0.1 A
3545 | MPPT 16V | S16 | 0.1 V
3546 | MPPT 16I | S16 | 0.1 A
3547-3566 | Reserve | U16 | —
3570 | A Phase Module NTC Temperature | U16 | 0.1 °C | 250K series
3571 | B Phase Module NTC Temperature | U16 | 0.1 °C
3572 | C Phase Module NTC Temperature | U16 | 0.1 °C
3573 | DC NTC1 Temperature | U16 | 0.1 °C
3574 | DC NTC2 Temperature | U16 | 0.1 °C
3575 | DC NTC3 Temperature | U16 | 0.1 °C
3576 | DC NTC4 Temperature | U16 | 0.1 °C
3577 | DC NTC5 Temperature | U16 | 0.1 °C
3578 | DC NTC6 Temperature | U16 | 0.1 °C
3579 | DC NTC7 Temperature | U16 | 0.1 °C
3580 | DC NTC8 Temperature | U16 | 0.1 °C
3581-3600 | Reserve | U16 | —
3601 | Adjustable PV quantity | U16 | 1 | 1=adjustable (running); 0=not adjustable
3602-3603 | Active power adj upward value | S32 | 1 W
3604-3605 | Active power adj downward value | S32 | 1 W
3606-3607 | Capacitive reactive power adj upward | S32 | 1 Var
3608-3609 | Capacitive reactive power adj downward | S32 | 1 Var
3610-3611 | Inductive reactive power adj upward | S32 | 1 Var
3612-3613 | Inductive reactive power adj downward | S32 | 1 Var
3614 | ABC three-phase upper limit under max reactive power | U16 | 0.1 V
3615 | ABC three-phase lower limit under max reactive power | U16 | 0.1 V
3616 | PV total active power control switch | U16 | 1 | 0=off; 1=on
3617 | PV total reactive power control switch | U16 | 1 | 0=off; 1=on
3618 | PV total voltage control switch | U16 | 1 | 0=off; 1=on
3619 | Inverter initialization completed | U16 | 1 | 0=not completed; 1=completed
3620 | Active power control status | U16 | 1 | 0=off; 1=on
3621 | Reactive power control status | U16 | 1 | 0=off; 1=on
3622 | Voltage control status | U16 | 1 | 0=off; 1=on
3623 | Is it in full generation condition | U16 | 1 | 0=not fully; 1=fully generating
3624 | Reactive power can be output at night | U16 | 1 | 0=cannot; 1=can
3625 | Active power control completed | U16 | 1 | 0=not completed; 1=completed
3626 | Reactive power control completed | U16 | 1 | 0=not completed; 1=completed
3627 | Voltage adjustment completed | U16 | 1 | 0=not completed; 1=completed
3628 | Is it controllable remotely? | U16 | 1 | 0=uncontrollable; 1=controllable
3629 | DC switch position | U16 | 1 | 0=off; 1=on
3630 | AC switch position | U16 | 1 | 0=off; 1=on
3631 | Emergency shutdown | U16 | 1 | 0=disabled; 1=enabled
3632 | Starting | U16 | 1 | 0=completed; 1=in progress
3633 | Alarm operation | U16 | 1 | 0=no alarm; 1=alarm running
3634-3637 | Reserved | U16 | —
3650 | 59.S1 Voltage (B phase) | U16 | 0.1 V
3651 | 59.S1 Time (B phase) | U16 | 1 ms
3652 | 59.S2 Voltage (B phase) | U16 | 0.1 V
3653 | 59.S2 Time (B phase) | U16 | 1 ms
3654 | 27.S1 Voltage (B phase) | U16 | 0.1 V
3655 | 27.S1 Time (B phase) | U16 | 1 ms
3656 | 27.S2 Voltage (B phase) | U16 | 0.1 V
3657 | 27.S2 Time (B phase) | U16 | 1 ms
3658 | 81>.S1 Frequency (B phase) | U16 | 0.01 Hz
3659 | 81>.S1 Time (B phase) | U16 | 1 ms
3660 | 81<.S1 Frequency (B phase) | U16 | 0.01 Hz
3661 | 81<.S1 Time (B phase) | U16 | 1 ms
3662 | 81>.S2F Frequency (B phase) | U16 | 0.01 Hz
3663 | 81>.S2F Time (B phase) | U16 | 1 ms
3664 | 81<.S2F Frequency (B phase) | U16 | 0.01 Hz
3665 | 81<.S2F Time (B phase) | U16 | 1 ms
3666 | 81>.S2S Frequency (B phase) | U16 | 0.01 Hz
3667 | 81>.S2S Time (B phase) | U16 | 1 ms
3668 | 81<.S2S Frequency (B phase) | U16 | 0.01 Hz
3669 | 81<.S2S Time (B phase) | U16 | 1 ms
3670 | 59.S1 Voltage (C phase) | U16 | 0.1 V
3671 | 59.S1 Time (C phase) | U16 | 1 ms
3672 | 59.S2 Voltage (C phase) | U16 | 0.1 V
3673 | 59.S2 Time (C phase) | U16 | 1 ms
3674 | 27.S1 Voltage (C phase) | U16 | 0.1 V
3675 | 27.S1 Time (C phase) | U16 | 1 ms
3676 | 27.S2 Voltage (C phase) | U16 | 0.1 V
3677 | 27.S2 Time (C phase) | U16 | 1 ms
3678 | 81>.S1 Frequency (C phase) | U16 | 0.01 Hz
3679 | 81>.S1 Time (C phase) | U16 | 1 ms
3680 | 81<.S1 Frequency (C phase) | U16 | 0.01 Hz
3681 | 81<.S1 Time (C phase) | U16 | 1 ms
3682 | 81>.S2F Frequency (C phase) | U16 | 0.01 Hz
3683 | 81>.S2F Time (C phase) | U16 | 1 ms
3684 | 81<.S2F Frequency (C phase) | U16 | 0.01 Hz
3685 | 81<.S2F Time (C phase) | U16 | 1 ms
3686 | 81>.S2S Frequency (C phase) | U16 | 0.01 Hz
3687 | 81>.S2S Time (C phase) | U16 | 1 ms
3688 | 81<.S2S Frequency (C phase) | U16 | 0.01 Hz
3689 | 81<.S2S Time (C phase) | U16 | 1 ms
3700-3701 | Rated active power | U32 | W | US versions
3702-3703 | Active power at PF=+0.8 rated full load | U32 | W
3704 | Leading power factor +0.8 | U16 | 0.01
3705-3706 | Active power at PF=-0.8 rated full load | U32 | W
3707 | Lagging power factor -0.8 | U16 | 0.01
3708 | Normal operating performance category | U16 | 1 | 1=CAT_A; 2=CAT_B
3709 | Abnormal operating performance category | U16 | 1 | 1=CAT_I; 2=CAT_II; 3=CAT_III
3710 | AC rated voltage | U16 | V
3711 | AC 1st overvoltage upper limit | U16 | 0.1 V
3712 | AC 1st undervoltage lower limit | U16 | 0.1 V
3713 | Control mode | U16 | 1 | Bit0=Over-freq derating; Bit1=Volt-watt; Bit2=Volt-var; Bit3=Fixed reactive; Bit4=Fixed PF; Bit5=P-Q
3714 | Admittance parameters | U16 | 0.001 | Scale varies by model
3715 | Manufacturer | U16 | 1 | 0=Null; 1=Ginlong
3716 | Hardware version number (mainboard) | U16 | 1 | 0x1010-0x1024 see PDF §5.2
3717-3718 | Real-time reactive power | U32 | 1 Var
3719-3720 | Capacitive max reactive power (60% S) | U32 | 1 Var
3721-3722 | Inductive max reactive power (60% S) | U32 | 1 Var
3733 | IV curve type identification code | U16 | 1 | 0x00=undefined; 0x01=60-point; 0x02=128-point
3734 | IV curve 128 point scanning flags | U16 | 1 | See PDF §5.2 for flag values
3735 | String Number | U16 | 1 | Use FC06 3239 to query string data
3736 | IV_PV Voltage1 | U16 | 0.1 V | 128-point IV curve data (4 frames, 64 data each)
3737 | IV_PV Current1 | S16 | 0.01 A
3738 | IV_PV Voltage2 | U16 | 0.1 V
3739 | IV_PV Current2 | S16 | 0.01 A
3740-3799 | IV_PV Voltage3~Current32 | — | 0.1V/0.01A | Pairs continue; see PDF §5.2
33601 | Energy Read Progress | U16 | 1% | 0=not started; 1-99%=in progress; 100%=done
33602 | Energy Check Method | U16 | 1 | 1=by month (daily detail); 2=by year (monthly detail); 3=total (10-year annual)
33603 | Energy Detailed Type | U16 | 1 | 1=PV generation; 2=grid-side transmission; 3=grid-side generation
33604-33634 | XYearYMonth 1Day~31Day | U16 | 0.1 kWh | Daily energy for queried month
33635-33658 | XYear 1Month~12Month | U32 | 0.1 kWh | Monthly energy for queried year (high+low 16-bit pairs)
33659-33678 | 0Year~9Year | U32 | 1 kWh | Annual energy for 10 years
33679 | Historical fault/alert data read progress | U16 | 1% | 0=not started; 100%=done
33680 | Serial numbers of 5 historical fault/alert data | U16 | 1 | 1=latest 1-5; 2=6-10; …; 8=36-40
33681 | Fault/Alarm 1 occurred: Year | U16 | 1
33682 | Fault/Alarm 1 occurred: Month-Day | U16 | 1 | High byte=month; Low byte=day
33683 | Fault/Alarm 1 occurred: Hour:Minute | U16 | 1 | High byte=hour; Low byte=minute
33684 | Fault/Alarm 1 status | U16 | 1
33685 | Fault/Alert 1 data | U16 | 1
33686-33690 | Fault/Alarm 2 (Year/MonDay/HourMin/Status/Data) | U16 | — | Same structure as record 1
33691-33695 | Fault/Alarm 3 | U16 | —
33696-33700 | Fault/Alarm 4 | U16 | —
33701-33705 | Fault/Alarm 5 | U16 | —

## Setting (FC03-06-10)
5.3 Inverter Setting (FC=03/06/10, send address = register - 1)
Register (Dec) | Name | Type | Unit | Remark
3000 | Year | U16 | 1 | 00-99
3001 | Month | U16 | 1 | 1-12
3002 | Day | U16 | 1 | 1-31
3003 | Hours | U16 | 1 | 0-23
3004 | Mins | U16 | 1 | 0-59
3005 | Seconds | U16 | 1 | 0-59
3006 | Slave address | U16 | 1 | Only FC06
3007 | ON/OFF | U16 | 1 | 0xBE=ON; 0xDE=OFF; 0x10=Night ON enable; 0x11=Night ON disable; 0x20=24H Consumption Enable; 0x21=Disable
3008 | Reserve | U16 | —
3009 | Power curve No. | U16 | 1
3010 | 81>S1 | U16 | 0.01 Hz | 100=1Hz; range 48-53Hz; default 50.2Hz
3011 | 81>S1-T | U16 | 0.01 s | 100=1s; 0.05-0.5s; default 0.10s
3012 | 81<S1 | U16 | 0.01 Hz | Default 49.8Hz
3013 | 81<S1-T | U16 | 0.01 s | Default 0.10s
3014 | 81>S2F | U16 | 0.01 Hz | Default 51.5Hz
3015 | 81>S2F-T | U16 | 0.01 s | Default 0.10s
3016 | 81<S2F | U16 | 0.01 Hz | Default 47.5Hz
3017 | 81<S2F-T | U16 | 0.01 s | Default 0.10s
3018 | 81>S2S | U16 | 0.01 Hz | Default 51.5Hz
3019 | 81>S2S-T | U16 | 0.01 s | 0.05-5.0s; default 1.0s
3020 | 81<S2S | U16 | 0.01 Hz | Default 47.5Hz
3021 | 81<S2S-T | U16 | 0.01 s | 0.05-5.0s; default 4.0s
3022 | Restart Inverter | U16 | 1 | 55AAH=Restart; only 80-110K PRO; FC06 only
3023 | DRM S1 Limit 1 | U16 | 0.01% | Range 0-100%
3024 | DRM S1 Limit 2 | U16 | 0.01%
3025 | DRM S1 Limit 3 | U16 | 0.01%
3026 | DRM S1 Limit 4 | U16 | 0.01%
3027 | DRM ON/OFF | U16 | 1 | 0x0000=OFF; 0x00AA=ON; turns off EPM automatically
3028 | Restart the HMI | U16 | 1 | 0xAA55=valid; FC single write; 3 times within 6s
3029 | Inverter installation Method | U16 | 1 | 0=90° (default); 1=15°
3030 | Night SVG Q Set | S16 | 0.01% | 10000=100%; -60%~60%; default 0%
3031 | Remote active power limit percentage | U16 | 0.01% | Only when 3080-BIT2=1; power-off saving needed
3032 | Reserve | U16 | —
3033 | VRT Enable Switch | U16 | 1 | BIT00=LVRT; BIT01=US Rule21 VRT; BIT02=FRT; BIT03=Brazil LVRT; BIT04=BDEW LVRT; BIT05=NRS(South Africa) LVRT; power-off save needed
3034 | BDEW LVRT K value | U16 | 1 | Range 0-10
3035-3040 | Reserve | U16 | —
3041 | 50549_2 VRT enable | U16 | 1 | 0=disabled; 1=enabled
3042 | 50549_2 low voltage ride through mode | U16 | 1 | 0=None; 1=Add reactive; 2=Add reactive+active priority; 3=Add reactive+reactive limit; 4=Add reactive+zero current; 5=Zero current
3043 | 50549_2 static voltage range lower limit % | U16 | 0.01% | Range 8000-10000; default 9000
3044 | 50549_2 static voltage range upper limit % | U16 | 0.01% | Range 10000-12000; default 11000
3045 | 50549_2 K1 during VRT | U16 | — | 50549-2: acc 1; VDE4110/50549-SW/NC-RFG: acc 0.1
3046 | 50549_2 K2 during VRT | U16 | — | Same accuracy rules as K1
3047 | 50549_2 VRT voltage change % | U16 | 0.01%
3048 | 50549_2 VRT reactive power upper limit % | U16 | 0.01%
3049 | 50549_2 VRT zero current mode voltage lower limit % | U16 | 0.01%
3050 | Reserved | U16 | —
3051 | Reactive power limitation | S16 | 0.01% | 10000=100%; range -6000~+6000; mode 04 only; enable 3071=A1; power-off save with 3069
3052 | Power limitation | U16 | 0.01% | 10000=100%; range 0-110%; enable 3070=AA; power-off save with 3069
3053 | PF Setting | S16 | 0.001 | 800=0.80; 1000=1.00; range -1~-0.80, 0.80~1; power-off save with 3069
3054 | PF Setting 02 | S16 | 0.001 | For mode 03 fixed PF; enable 3071=A2; power-off save with 3069
3055 | Reserve | U16 | —
3056-3057 | Calibrate total generation | U32 | 1 kWh
3058-3059 | Calibrate current month generation | U32 | 1 kWh
3060-3061 | Calibrate last month generation | U32 | 1 kWh
3062 | Calibrate today generation | U16 | 0.1 kWh
3063 | Calibrate yesterday generation | U16 | 0.1 kWh
3064-3065 | Calibrate this year generation | U32 | 1 kWh
3066-3067 | Calibrate last year generation | U32 | 1 kWh
3068 | Standard number | U16 | 1 | See Appendix 4
3069 | Power-off saving function | U16 | 1 | BIT00=save for 3052/3149/3150/3157; BIT01=for 3053; BIT02/03=for 3051/3130-3146/3073 etc. Flash write limit: <10000 times
3070 | Power limitation switch | U16 | 1 | 0xAA=ON; 0x55=OFF (power to 100%). Default 0xAA. For 3052/3081. 5-25K/25-50K/50-70K series
3071 | Reactive power switch | U16 | 1 | 0x55=OFF(PF=1); 0xA1=reactive setting valid; 0xA2=PF02 setting valid. Default 0x55
3072 | Day Time PID Switch | U16 | 1 | 0xAA=ON; 0x55=OFF. 255K series
3073 | Working mode | U16 | 1 | 00=No response; 01=Volt-watt; 02=Volt-var; 03=Fixed PF; 04=Fix reactive; 05=Power-PF; 06=Rule21 Volt-watt; 0C=P-Q; power-off save: set 3069=1
3074 | Italy Standard Switching Mode | U16 | 1 | 0=Off; 1=Local Control; 2=External Signal
3075 | Italy Single Test | U16 | 1 | 01-30: see PDF §5.3; power-off save (Italy only)
3076 | Italy Full Test | U16 | 1 | 0=stop/not start; 2=start
3077 | AFCI ON/OFF | U16 | 1 | 3149=0: 1=Open/0=Close. 3149=1or2: 1=enable sub switch; 0=not enable
3078 | CT Direction Set | U16 | 1 | 0xAA=Correct; 0x55=Reverse (towards grid)
3079 | AFCI Level | U16 | 1 | Range 0-7; default 0
3080 | Power control word | U16 | 1 | BIT0=max power limit flag; BIT2=remote active power limit enable (with 3031)
3081 | Limit power actual value | S16 | 10 W | Use FC06 3070=AA then set; 5-25K/25-50K/50-70K/80-110K
3082 | CT Ratio Setting | U16 | 1 | e.g. 3000=3000:1; 1ph inverters only
3083 | Limiting reactive power adjustment value | S16 | 10 Var | Use FC06 3071 then set; 5-25K/25-50K/50-70K/80-110K
3084 | Leakage current protection | U16 | 1 mA | Range 50-800mA; default 240mA
3085 | PV insulation protection | U16 | 1 kΩ | Range 20k-1000k; default 200K
3086 | Reserve | U16 | —
3087 | ARC_Fault Manual Reset | U16 | 1 | 0x00AA=Manual Reset (only if >5 faults in 24h)
3088 | VRT Enable Flag bit | U16 | 1 | 0xA5=Disable; 0x5A=Enable
3089 | Grid code accuracy set flag | U16 | 1 | Low 8: 0x0001=V 0.1V/T 0.01s/F 0.01Hz; 0x0000=V 1V/T 0.1s/F 0.1Hz; High 8: 0x01xx=single rule mode
3090 | OV-G-V 01 | U16 | 1 | User-def code; FC10 only
3091 | OV-G-V-T 01 | U16 | 1 | 0.10-9.0s default 1.0s
3092 | OV-G-V 02 | U16 | 1
3093 | OV-G-V-T 02 | U16 | 1 | 0.10-1.0s default 0.2s
3094 | UN-G-V 01 | U16 | 1
3095 | UN-G-V-T 01 | U16 | 1 | 0.10-9.0s default 1.0s
3096 | UN-G-V 02 | U16 | 1
3097 | UN-G-V-T 02 | U16 | 1 | 0.10-1.0s default 0.2s
3098 | OV-G-F 01 | U16 | 1
3099 | OV-G-F-T 01 | U16 | 1 | 0.10-9.0s default 1.0s
3100 | OV-G-F 02 | U16 | 1
3101 | OV-G-F-T 02 | U16 | 1 | 0.10-9.0s default 0.2s
3102 | UN-G-F 01 | U16 | 1
3103 | UN-G-F-T 01 | U16 | 1 | 0.10-9.0s default 1.0s
3104 | UN-G-F 02 | U16 | 1
3105 | UN-G-F-T 02 | U16 | 1 | 0.10-9.0s default 0.2s
3106 | Startup time | U16 | 1 s | Range 10-600s; default 60s
3107 | Reconnect time | U16 | 1 s | Range 10-600s; default 60s
3108 | Recover V upper limit | U16 | 0.1 V | Default=OV-G-V01
3109 | Recover V lower limit | U16 | 0.1 V | Default=UN-G-V01
3110 | Recover F upper limit | U16 | 0.01 Hz | Default=OV-G-F01
3111 | Recover F lower limit | U16 | 0.01 Hz | Default=UN-G-F01
3112 | Startup V upper limit | U16 | 0.1 V | Default 253.0V
3113 | Startup V lower limit | U16 | 0.1 V | Default 195.5V
3114 | Startup F upper limit | U16 | 0.01 Hz | Default 50.1Hz
3115 | Startup F lower limit | U16 | 0.01 Hz | Default 49.5Hz
3116 | Denmark Freq Change Protection Threshold | U16 | 0.1 Hz/s | 1000=1Hz/s; range 0-3500; default 2500
3117 | Denmark Freq Change Protection Time | U16 | 1 ms | Range 0-5000; default 80
3118 | Working mode control switch | U16 | 1 | BIT00=overvoltage active power auto limit; BIT01=Vref control enable (3126-3127)
3119 | OV-G-V03 | U16 | 0.1 V
3120 | OV-G-V03-T | U16 | 10 ms
3121 | UN-G-V03 | U16 | 0.1 V
3122 | UN-G-V03-T | U16 | 10 ms | Range 0.5-21.0s; default 2.0s
3123 | Reserve | U16 | —
3124 | National standard special switch | U16 | 1 | BIT00-BIT01: island detection (00=default; 01=Danish; 10=off; 11=both)
3125 | Shutdown command for active/reactive power control | U16 | 1 | 01=turn off Volt-Watt; 02=turn off all reactive functions
3126 | Volt-Var Vref Setting | U16 | 0.1 V | Power-off save: 3069 BIT03/02; set Vref before mode 2 voltage; enable 3118 BIT01
3127 | Volt-Var Vref Time Setting | U16 | 0.1 s | Range 300-5000s; default 300s
3128 | 02 working mode V2-Q2 Percent | S16 | 0.01% | -60%~60%; >0=leading; <0=lagging
3129 | 02 working mode V3-Q3 Percent | S16 | 0.01%
3130 | 01/06 working mode V1Set | U16 | 0.1 V | Power-off save: 3069 BIT03/02
3131 | 01/06 working mode V2Set | U16 | 0.1 V
3132 | 01/06 working mode V3Set | U16 | 0.1 V
3133 | 01/06 working mode V4Set | U16 | 0.1 V
3134 | 01/06 working mode P1% | U16 | 0.01% | 10000=100%; range 0-100%
3135 | 01/06 working mode P2% | U16 | 0.01%
3136 | 01/06 working mode P3% | U16 | 0.01%
3137 | 01/06 working mode P4% | U16 | 0.01%
3138 | 02 working mode V1Set | U16 | 0.1 V | Set Vref (3126-3127) first
3139 | 02 working mode V2Set | U16 | 0.1 V
3140 | 02 working mode V3Set | U16 | 0.1 V
3141 | 02 working mode V4Set | U16 | 0.1 V
3142 | 02 working mode MaxLeadingVar% | U16 | 1% | 10000=100%; range 0-60%; default 30%
3143 | 02 working mode MaxLaggingVar% | U16 | 1% | 10000=100%; range 0~-60%; default -30%
3144 | 05 working mode Pb% | U16 | 1% | 10000=100%; range 50-100%; default 100%
3145 | 05 working mode Pc% | U16 | 1% | 10000=100%; range 50-100%; default 100%
3146 | 05 working mode PFcSet | S16 | 0.01 | 800=0.80; 1000=1.00; range -1~-0.9, +0.9~+1.0
3147 | 10 mins over voltage | U16 | 0.1 V
3148 | Power ramp rate (Wgra) general | U16 | 0.01% | 10000=100%; range 5-600%; default 16.67%
3149 | Power ramp up rate | U16 | 0.01% | 3000=30%/min; range 10-100%; default 16.66%; AUS only; power-off save: 3069=1
3150 | Power ramp down rate | U16 | 0.01% | 3000=30%/min; range 10-100%; default 50%; AUS only
3151 | Internal EPM Switch | U16 | 1 | Values vary by model; see PDF §5.3
3152 | Internal EPM backflow power | S16 | 100 W | + to grid; - from grid
3153 | Internal EPM failsafe switch | U16 | 1 | 0=off; 1=on
3154 | Internal EPM Hard Switch | U16 | 1 | 00=Null; 01=ON(Meter in Grid); 02=OFF; 03=ON(Meter in Load)
3155 | Internal EPM Hard Limit | S16 | 100 W | + to grid; - from grid
3156 | Backflow Work mode | U16 | 1 | 00=3PH Sum; 01=3PH Sum; 02=Min Phase×3
3157 | Power Control Slope | U16 | 0.01% | 3000=30%/min; range 10-100%; power-off save: 3069 BIT0
3158 | RD244_EPM_ON/OFF setting | U16 | 1 | 0x00AA=On; 0x0055=Close; default 0x0055
3159 | Factory Reset | U16 | 1 | 0x00AA=Enable; clears alarms, resets settings to default
3160 | Reset 01 Working Mode | U16 | 1 | 0x00AA=Enable
3161 | Reset 02 Power rate limit | U16 | 1 | 0x00AA=Enable
3162 | Reset 03 Freq Derate Set | U16 | 1 | 0x00AA=Enable
3163 | Reset 04 10min overvoltage | U16 | 1 | 0x00AA=Enable
3164 | G100 Control Switch | U16 | 1 | 0x55=off; 0x56=Meter in grid; 0x57=CT in grid
3165 | Backflow Current | S16 | 0.01 A | 100=1.00A; range 0-99A; default 16A
3166 | Clear G100 Alarm | U16 | 1 | 0xA5=Clear; others invalid
3167 | G100 Clear Alarm Type Select | U16 | 1 | 1=home(≤3 times/30 days); 2=non-home(4h wait); 3=installer(no limit)
3168 | 05 P-PF mode Point A power % | U16 | 1 | 10000=100%; range 0~-60%; default -30%; power-off save: 3069 BIT03/02
3169 | 05 P-PF mode Point A PF | U16 | 1 | 800=0.80; 1000=1.00
3170 | 05 P-PF mode Point B PF | U16 | 1
3171 | 05 P-PF mode Point D power % | U16 | 1
3172 | 05 P-PF mode Point D PF | U16 | 1
3173 | 02 Volt-Var – voltage preset point | U16 | 0.1 V | 10=1V
3174 | HVRT boost bus voltage command enable flag | U16 | 1 | 0=not enabled; 1=enabled
3175 | No restart after PV insulation failure | U16 | 1 | 0x00=off; 0x01=on; 0x2A=clear fault (no power-off save)
3176 | Default Export Limit Value (AU SAPN) | U16 | 100 W | Power-off saving
3177 | Default Export Limit Enable Switch (AU SAPN) | U16 | 1 | 00AAH=Enable(use 3176); 0000H=Disable(use 3152)
3178 | SAPN Enable switch | U16 | 1 | 0055H=enable; 0000H=not enabled
3179 | Safety Fault & Ride through Switch | U16 | 1 | BIT00=safety fault sync; BIT01=VRT enable; MAX projects only
3180 | Shading MPPT Scan Enable | U16 | 1 | 0=OFF; 1=ON; set with 3181 using FC10
3181 | Shading MPPT Scan Time interval | U16 | 1 min | Default 30min; range 10-180min; set with 3180 using FC10
3182 | EN50549 Reconnect Slope Limit (Wgra_Rec) | U16 | 0.1% | 1000=100%; range 5-3000%; default 10%
3183 | EN50549 Startup Slope Limit (Wgra_nor) | U16 | 0.1% | Default 600%
3184 | Power Ramp up Slope Limit (Wgra+) | U16 | 0.01% | Default 16.67%
3185 | Power Ramp down Slope Limit (Wgra-) | U16 | 0.01% | Default 16.67%
3186 | EN50549 P-Lock in | U16 | 1% | 100=100%; range 0-100%; default 20%
3187 | EN50549 P-Lock out | U16 | 1% | Default 5%
3188 | 05 Mode P-PF Ulockin Vset (Brazil/Dubai/CEI021) | U16 | 0.1 V
3189 | 05 Mode P-PF Ulockout Vset | U16 | 0.1 V
3190 | Change slope Wnor (Rule21/Hawaii) | U16 | 0.01% | 10000=100%; range 1-100%; default 100%/s
3191 | Change slope Wcon (Rule21/Hawaii) | U16 | 0.01% | Default 2%/s; duplicate of FC03/06/10 reg 3320
3192 | Rule21 normal working power change slope enable | U16 | 1 | 0=disabled; 1=enable
3194 | RS485 baud rate switching | U16 | 1 | 0=9600; 1=19200; 2=38400; 3=57600; 4=115200
3195 | Power factor control mode | U16 | 1 | 0=Mode0(set by DATA00-01); 1=VDE4105 curve; 2=Brazil curve; default 0
3196 | Real-time active power compensation parameter | U16 | 0.001 | Default 1.000; range 0.800-1.200
3200 | Overfrequency load shedding special function | U16 | 1 | BIT00=Swedish freq sensitivity; BIT01=OFD enable; BIT02=UFR enable
3201 | FSM power change limit % | U16 | 0.01% | Range 5-10%
3202 | Droop settings for FSM | U16 | 0.01% | Range 2-12%
3203 | FSM response dead zone | U16 | 1 mHz | Range 0-500mHz
3204 | FSM frequency insensitivity | U16 | 1 mHz | Range 0-1000mHz
3205-3222 | Reserved | U16 | —
3223-3224 | Actual adjustment value of power limit | S32 | 10 | 320K series; enable 3070=AA then set 3081
3225-3226 | Limited reactive power adjustment value | S32 | 10 | 320K series; enable 3071 then set 3083
3227 | Electric meter or dual 485 optional function switch | U16 | 1 | 0=meter; 1=dual 485; 5-25K series
3229 | Bluetooth Connection Status | U16 | 1 | 1=No conn; 2=Connecting; 3=Connected
3230 | Datalogger 1 Connection Status | U16 | 1 | 1=No; 2=Connecting; 3=Connected
3231 | Datalogger 2 Connection Status | U16 | 1 | Disconnect after 10min no frame
3232 | WIFI Signal Strength | U16 | 1% | 0-100%
3233 | Password Level | U16 | 1 | 1=installer; 2=user; 3=administrator; Bluetooth APP
3234 | 1st/2nd digit password | U16 | 1 | MD5 16-bit encrypted ASCII; little-endian
3235 | 3rd/4th digit password | U16 | 1
3236 | 5th/6th digit password | U16 | 1
3238 | IV curve 128 points request flag | U16 | 1 | 0=no op; 1=request scan
3239 | IV curve 128 point string number | U16 | 1 | Low 8=string no.; High 8=read count (0-3 for V/I frames)
3240 | IV curve start scan enable | U16 | 1 | 1=start; 0=no scan; query 3341 for quantity after start
3241 | IV curve starting voltage | U16 | 1 V | FC03/10; 25-50K
3242 | IV curve interval voltage | U16 | 1 V | FC03/10
3243 | Get current IV curve No. | U16 | 1 | Step1: scan; Step2: set no.; Step3: read FC04 3341-3462
3244 | Remote Request AFCI Fault Signature Data Switch | U16 | 1 | 1=on; 0=off
3245 | Obtained module/frame number | U16 | 1 | Low 8=module no.; High 8=frame no. (1-17)
3246 | Remote AFCI fault characteristic non-stop flag | U16 | 1 | 1=non-stop on AFCI fault; 0=no action
3247 | AFCI board sub switch | U16 | 1 | BIT00=MPPT full open; BIT01-BIT10=MPPT1-10 switch; when 3149=1or2 and 3077=1
3248-3251 | Reserved | U16 | —
3252 | Learning enable switch (Lingshi AFCI) | U16 | 1 | 1=on; 0=off; FC10
3253 | Self-Learning time setting | U16 | 1 | 1=12h; 2=24h; etc.; set 3252=1 simultaneously
3254 | Self-learning result clear switch | U16 | 1 | 1=on; 0=off
3255-3259 | Reserved | U16 | —
3294 | AD debug array | U16 | 1 | Range 1-10
3295-3296 | Read DSP fixed address variable value | U32 | 1 | 3295=high 16bit addr; 3296=low 16bit addr
3297-3298 | Read ARM fixed address variable value | U32 | 1 | Same structure
3299 | Calibrate real-time power parameter | U16 | 1 | Range 800-1200; default 1000; e.g. 1200=power×1.2
3300 | Clear Generation Data | U16 | 1 | 0x55AA=clear; FC06 only
3301 | Fan self-test | U16 | 1 | 0000H=not started; 0001H=started; check 3044 for F011H
3302 | One Click Reset Enable Command | U16 | 1 | 0001H=enable; read FC04 3228 for random value xxxxH
3303 | One Click Reset Operating Command | U16 | 1 | xxxxH=execute (xxxxH = FC04 3228 value); 0045H=end flag
3304 | Special Function Control Word 01 | U16 | 1 | BIT00=Boost; BIT01=DC inject adj; BIT02=0% power relay; BIT03=AFCI self-check; BIT04=AFCI mode; BIT05=phase-line GND; BIT07=AC HW OC low sensitivity; BIT11=MPPT parallel mode
3305 | Grid V A compensation | S16 | 0.1 V | ±50V; 1ph=phase A only
3306 | Grid V B compensation | S16 | 0.1 V
3307 | Grid V C compensation | S16 | 0.1 V
3308 | Grid V A compensation Rated value | S16 | 0.1 V | PRO series; inverter calculates diff
3309 | Grid V B compensation Rated value | S16 | 0.1 V
3310 | Grid V C compensation Rated value | S16 | 0.1 V
3311 | Enable 'Power ON display to select grid code' Flag | U16 | 1 | 00=disabled; 01=enabled
3312 | Special control word 02 | U16 | 1 | BIT00=const V MPPT mode; BIT01=multi-ch MPPT parallel; BIT02=relay protect; BIT03=ileak protect; BIT04=GND protect; BIT05=grid dist02; BIT06=grid current AD protect
3313 | Voltage in constant voltage MPPT mode | U16 | 0.1 V | Range 100-850V; used with 3312 BIT00
3314 | Grid filter Setting | U16 | 1 | Range 0-7
3315 | Special control word 03 | U16 | 1 | BIT00=NoSmallPulse; BIT01=IgFollow; BIT02=PV midpoint GND protect
3316 | External EPM FailSafe Switch | U16 | 1 | 0x0000=off; 0x00AA=5G_EPM FailSafe on; 0x0055=other EPM FailSafe on
3317 | PCC voltage (Rule21Phase3) | U16 | 0.1 V | 1P: 200-250 default 240V; 3P: 260-290 default 277.1V
3318 | PCC offset voltage (Rule21Phase3) | U16 | 0.1 V | Range -20~20; default 0V
3320 | US Code reconnection power recovery slope | U16 | 0.01% | 1=0.01%; range 0.1-100%; default 0.33%
3321 | P_Q Mode P1 | U16 | 0.01% | 100=1%; range 0-70%Pn; default 20%Pn
3322 | P_Q Mode P2 | U16 | 0.01% | Range 40-80%Pn; default 50%Pn
3323 | P_Q Mode P3 | U16 | 0.01% | Range 50-100%Pn; default 100%Pn
3324 | P_Q Mode P4 | U16 | 0.01%
3325 | P_Q Mode P5 | U16 | 0.01%
3326 | P_Q Mode Q1 | U16 | 0.01% | Range -60~60%Sn; default 0
3327 | P_Q Mode Q2 | U16 | 0.01%
3328 | P_Q Mode Q3 | U16 | 0.01% | Default -44%Sn
3329 | P_Q Mode Q4 | U16 | 0.01%
3330 | P_Q Mode Q5 | U16 | 0.01%
3331 | Volt Var P3Tau | U16 | 0.01 s | Range 0.5-60s; default 10s
3332 | Volt Var Q3Tau | U16 | 0.01 s | Range 1-90s; default 5s
3334 | DRM7 Reactive power | S16 | 0.01% | Range -60%~0; default -30
3335 | Active priority or reactive power priority | U16 | 1 | 0=Q priority; 1=P priority; default 0
3336 | Meter Setting | U16 | 1 | 0=DDSD1352C; 1=ACR10RD16TE; 2=ACR10RD16TE4; 3=DTSD1352; 4=SDM630mct; 5=AGF-AE-D/200
3337 | Volt Var Qdroop | U16 | 0.01% | Range 2-7%; default 2%
3338 | Overfrequency load shedding power lower limit % | U16 | 0.01% | 10000=100%
3339 | CT sampling power threshold | U16 | 1 W | CT_FailSafe disturbance detection
3340 | Fan de-icing main switch | U16 | 1 | 0=off; 1=on; default 0
3341 | Fan start interval | U16 | 0.1 s | Range 1200-6000
3342 | Fan de-icing temperature threshold | S16 | 0.1 °C | Range -100~150
3343 | Start SVG start time – month | U16 | 1 | Range 1-12
3344 | Open SVG start time – day | U16 | 1 | Range 1-31
3345 | Enable SVG end time – month | U16 | 1 | Range 1-12
3346 | Enable SVG end time – day | U16 | 1 | Range 1-31
3400 | Frequency Derating Mode | U16 | 1 | 00-14H; 00=No req; 01=AUS; 03=VDE4105/ES; 04=US Rule21/Brazil; 0D=China 2018; 13H=Hawaii/US1547/KS3-LVRT; see PDF §5.3
3401 | UnderFrequency Ramping Fstart | U16 | 0.01 Hz | Mode 01H/03H/08H/13H/14H
3402 | UnderFrequency Ramping Droop | U16 | 0.1% | Mode 03H/08H/13H/14H
3403 | Overfrequency Derating Response Time | U16 | 0.01 s | Mode 13H
3404 | Overfrequency Derating Droop | U16 | 0.01% | Mode 03H/0AH/0CH/11H/12H/13H/08H/0DH
3405 | Overfrequency Derating Fstart | U16 | 0.01 Hz | Mode 03H/0AH/0CH/11H/12H/13H/01H/04H/09H/14H/08H
3407 | Overfrequency Derating Fstop | U16 | 0.01 Hz | Mode 01H/09H/04H/14H/08H; 50Hz: 51.0-54.0 default 52.0Hz
3408 | Overfrequency Derating HystEna | U16 | 1 | Mode 08H; 1=enable; 0=disable
3410 | UnderFrequency Ramping Fstop | U16 | 0.01 Hz | Mode 01H; 47.0-49.0Hz default 48.0Hz
3413 | EN50549 OFD Start Frequency f1 | U16 | 0.01 Hz | Mode 0EH; 50.2-52.0Hz default 50.20Hz
3414 | 0E Mode EN50549 OFD HystEnable | U16 | 1 | 0=droop mode; 1=step mode
3415 | 0E Mode EN50549 OFD HystFreq fstop | U16 | 0.01 Hz | Range 50.0-f1Hz; default 50.20Hz
3416 | 0E Mode EN50549 OFD HystFreq Response Time Tstop | U16 | 1 s | 0-600s; default 30s
3417 | 0E Mode EN50549 OFD Droop | U16 | 0.01% | Range 2-12%; default 5%
3418 | 0E/04 Mode OFD Frequency Response delay Tintendelay | U16 | 0.01 s | 0-2s; default 0s
3419 | 0EH/08H mode OFD minimum power | U16 | 0.01% | 100=1%; 320K applicable
3420 | Voltage ride through ΔU enable switch | U16 | 1 | 0xA2=Disable; 0x2A=Enable; 320K
3421 | VRT zero current mode zero current threshold voltage upper limit | U16 | 0.01% | 10000=100%; 320K
3422-3451 | Reserved | U16 | —
3452 | Special control word 04 | U16 | 1 | BIT6=boost self-test switch; BIT7=NTC temp anomaly detect
3453 | Special control word 05 | U16 | 1 | BIT0-BIT13=DC reverse connection fault switches for channels 1-14
3500 | External fan start/stop condition switch | U16 | 1 | BIT0=temp (always on); BIT1=power; BIT2=current
3501 | External fan temperature starting point | U16 | 0.1 °C | Range 0-120°C
3502 | External fan temperature stop point | U16 | 0.1 °C | Stop ≤ Start
3503 | External fan power starting point | U16 | 1% | Range 0-110%
3504 | External fan power stop point | U16 | 1%
3505 | External fan current starting point | U16 | 0.1 A | Range 0-100A
3506 | External fan current stop point | U16 | 0.1 A
3507 | External fan speed ctrl curve temperature point 1 | U16 | 0.1 °C | Range 2-118°C
3508 | External fan speed ctrl curve temperature point 2 | U16 | 0.1 °C | Range 4-120°C; ≥(T1+2)
3509 | External fan speed ctrl curve speed 1 | U16 | 1% | T≤T1 speed
3510 | External fan speed ctrl curve speed 2 | U16 | 1% | T1<T≤T2 speed
3511 | External fan speed ctrl curve speed 3 | U16 | 1% | T>T1 speed
3512 | External fan initialization switch | U16 | 1 | 0x0000=closed; 0x00AA=on (restores 3500-3511 to initial)
43501 | History Energy Data Check method | U16 | 1 | 1=by month; 2=by year; 3=total 10yr; write with 43502-43503 simultaneously
43502 | History Energy Data Check Year/Month | U16 | 1 | High byte=year(0-99); Low byte=month(1-12 or 0x00)
43503 | Data type of historical energy data | U16 | 1 | 1=PV generation; 2=grid-side transmission; 3=grid-side generation
43506 | Query method of fault/warning records | U16 | 1 | 1=fault; 2=warning; write with 43507 simultaneously
43507 | Query sequence number of fault/warning records | U16 | 1 | 1=latest 1-5; 2=6-10; …; 8=36-40

## EPM Operate (FC04)
5.4 EPM Operating Info (FC=04, no address offset)
Register (Dec) | Name | Type | Unit | Remark
36000 | EPM AC V A | U16 | V | 10=1V
36001 | EPM AC I A | U16 | A | 10=1A
36002 | EPM AC V B | U16 | V
36003 | EPM AC I B | U16 | A
36004 | EPM AC V C | U16 | V
36005 | EPM AC I C | U16 | A
36006 | EPM_Power A | S16 | W | 1=100W
36007 | EPM_Power B | S16 | W
36008 | EPM_Power C | S16 | W
36009-36010 | EPM_Power Total | S32 | W | 1=100W; Little Endian
36011-36012 | Inverter Total Power | S32 | W | 1=100W; Little Endian
36013-36014 | Reserve | — | —
36015 | Power control percent | U16 | — | 10000=100%
36016 | CT ratio | U16 | 1 | 1-10 (v05+) or 1-100; EPM-5G/PLUS
36017 | Backflow power setting value | S16 | W | 1=100W
36018 | Inverter number setting value | U16 | 1
36019 | Year | U16 | — | 00-99
36020 | Month | U16 | 1
36021 | Day | U16 | 1
36022 | Hours | U16 | 1
36023 | Mins | U16 | 1
36024 | Seconds | U16 | 1
36025 | FailSafe ON/OFF | U16 | 1 | 0=OFF; 1=ON; default OFF (after Ver06)
36026 | Grid PF | S16 | — | -1.0~-0.8, +0.8~+1.0
36027 | Grid Freq (Meter) | U16 | Hz | 100=1Hz
36028-36029 | Total Load power | U32 | W | 1=100W; calculated from inverter+EPM; Little Endian
36030-36049 | Reserve | — | —
36050-36051 | Inverter total generation energy | U32 | kWh | 100=1kWh; Little Endian
36052-36053 | Load total consumption energy | U32 | kWh | 100=1kWh; Little Endian
36054-36055 | Grid import total active energy | U32 | kWh | 100=1kWh; Little Endian
36056-36057 | Grid export total active energy | U32 | kWh | 100=1kWh; Little Endian
36058 | EPM data transmission Switch | U16 | 1 | 0=OFF; 1=ON; default 0
36059 | Batch upgrade flag | U16 | 1 | 0=not support; 1=support
36060 | EPM model | U16 | 1 | 0x00E0=5G-EPM; 0x0000=Unknown/2G-EPM

## EPM Setting (FC03-06-10)
5.5 EPM Setting (FC=03/06/10, no address offset)
Register (Dec) | Name | Type | Unit | Remark
36500 | Year | U16 | — | 00-99
36501 | Month | U16 | — | 1-12
36502 | Day | U16 | —
36503 | Hours | U16 | —
36504 | Mins | U16 | —
36505 | Seconds | U16 | —
36506 | Slave Address | U16 | —
36507 | CT ratio | U16 | — | 1=100
36508 | Backflow power | S16 | W | 1=100W
36509 | Inverter number | U16 | —
36510 | EPM mode | U16 | — | 01=Sum of 3-phase power; 02=Min phase×3
36511 | FailSafe ON/OFF | U16 | — | 0=OFF; 1=ON; default OFF
36512 | Reserve | — | —
36513 | EPM data transmission Switch | U16 | — | 0=OFF; 1=ON; default 0
36514 | Inverter type Select | U16 | — | 0x55=PV inverter (Meter Info OFF); 0xAA=Hybrid (Meter Info ON); default 0x55

## Status Codes (App1)
Appendix 1: Inverter Status & Fault Codes
Code (Hex) | Fault/Status Name | Display Code
0000H (0000) | Normal / Waiting | Generating / Waiting
0000H (0001) | — | Grid Off
0001H | — | OpenRun
0002H | Waiting SoftRun | SoftRun
0003H (0000) | Initializing Generating | Generating
0003H (0001) | — | LimByTemp
0003H (0002) | — | LimByFreq
0003H (0004) | — | LimByVg
0003H (0008) | — | LimByVar
0003H (0010) | — | LimByUnFr
0003H (0020) | — | Ramp-up
0003H (0040) | — | Overload
0003H (0100) | — | LimByDRM
0003H (0200) | — | LimByEPM
1004H | Grid off | Grid Off
F010H | Grid surge (Warning) | Surge Alarm
F011H | FAN fault (Warning) | Fan Alarm
F013H | AC SPD ERROR (Warning) | VgSpdFail
F014H | DC SPD ERROR (Warning) | DcSpdFail
F015H | Fan fault External (Warning) | Fan_H Alarm
F016H | Fuse Alarm | FuseFail
F017H | AC Phase Ground Fault | L&PE FAIL
F018H | DSP Communication Error | DSP_Comm Alarm
F019H (0000) | 0000_Boost Error | BoostFail
F01CH | IGBT Temperature Difference | IGBT TEMP DIF
1010H (0000) | Grid Over Voltage | OV-G-V
1010H (0001) | Grid Over Voltage 01 | OV-G-V01
1010H (0002) | Grid Over Voltage 02 | OV-G-V02
1010H (0003) | Grid Over Voltage 03 | OV-G-V03
1010H (0004) | Grid Over Voltage 04 | OV-G-V04
1010H (0005) | Grid Over Voltage 05 | OV-G-V05
1011H (0000) | Grid Under Voltage | UN-G-V
1011H (0001) | Grid Under Voltage 01 | UN-G-V01
1011H (0002) | Grid Under Voltage 02 | UN-G-V02
1012H (0000) | Grid Over Frequency | OV-G-F
1012H (0001) | Grid Over Frequency 01 | OV-G-F01
1012H (0002) | Grid Over Frequency 02 | OV-G-F02
1013H (0000) | Grid Under Frequency | UN-G-F
1013H (0001) | Grid Under Frequency 01 | UN-G-F01
1013H (0002) | Grid Under Frequency 02 | UN-G-F02
1014H | Grid reverse | Backfeed_Iac
1015H | No Grid | NO-Grid
1016H | Grid Unbalance | G-PHASE
1017H | Grid Frequency Fluctuation | G-F-FLU
1018H | Grid Over Current | OV-G-I
1019H | Grid current tracking fault | IGFOL-F
101AH | Grid phase abnormal | PHASE-FAULT
101CH | IGBT shift fault | IGBTSift-Pro
101DH (0001) | Static overvoltage 1 | G100-VH
101DH (0002) | Static overvoltage 2 | G100-OV1
101DH (0003) | Dynamic overvoltage | G100-D-VH
101DH (0004) | Static undervoltage 1 | G100-UV1
101DH (0005) | Static undervoltage 2 | G100-VL
101DH (0006) | Dynamic undervoltage | G100-D-VL
1020H (0000) | DC Over Voltage | OV-DC
1020H (0001) | DC Over Voltage 01 | OV-DC01
1020H (0002) | DC Over Voltage 02 | OV-DC02
1020H (0003) | PV Ground Fault | PVGndRun Fau
1020H (0004) | DC Boost Fault | BoostFail
1021H | DC Bus Over Voltage | OV-BUS
1022H | DC Bus Unbalance | UNB-BUS
1023H (0000) | DC Bus Under Voltage | UN-BUS
1023H (0001) | DC Bus Under Voltage 01 | UN-BUS01
1023H (0002) | DC Bus Under Voltage 02 | UN-BUS02
1024H | DC Bus Unbalance 2 | UNB2-BUS
1025H | DC Channel A Over Current | OV-DCA-I
1026H | DC Channel B Over Current | OV-DCB-I
1027H | DC interference | DC-INTF.
1028H | DC reverse | Reve-DC
1029H | PV mid-point grounding | PvMidIso
102AH | Bus voltage inconsistent (master-slave DSP) | Vbus-Sam
1030H | Grid Interference Protection | GRID-INTF.
1031H | DSP Initial Protection | INI-FAULT
1032H | Temperature Protection | OV-TEM01
1033H (0000) | PV Insulation fault | PV ISO-PRO
1033H (0001) | PV Insulation fault 01 | PV ISO-PRO1
1033H (0002) | PV Insulation fault 02 | PV ISO-PRO2
1034H (0000) | Leakage Current Protection | ILeak-PRO
1034H (0001) | Leakage Current Protection 01 | ILeak-PRO01
1034H (0002) | Leakage Current Protection 02 | ILeak-PRO02
1034H (0003) | Leakage Current Protection 03 | ILeak-PRO03
1034H (0004) | Leakage Current Protection 04 | ILeak-PRO04
1035H | Relay Protection | RelayChk-FAIL
1036H (0000) | DSP_B Communication Fault | DSP-B-Com-Fau
1036H (0001) | DSP_B Sampling Fault | DSP-B-Sam-Fau
1037H | DC Injection Protection | DCInj-FAULT
1038H | 12V Under Voltage Faulty | 12Power-FAULT
1039H | Leakage Current Check Protection | ILeak-Check
103AH | Under temperature protection | UN-TEM
103DH | L&PE Fault | L&PE-FAULT
103EH | NTC Over Temp | OV-TEM02
1040H | AFCI Check Fault | AFCI-Check
1041H | AFCI Fault | ARC-FAULT
1046H | Grid INTF 02 | GRID-INTF02
1047H | Grid current sampling error | IG-AD
1048H | IGBT over current | IGBT-OV-I
1050H | Instantaneous overcurrent grid side | OV-IgTr
1051H | Battery OV HW fault (hybrid) / DC bus HW OV (inverter) | OV-Vbatt-H / OV-BUS-H
1052H | LLC hardware overcurrent | OV-ILLC
1053H | Battery OV detection / EPM HardLimit | OV-Vbatt / EPM-HardLimit
1054H | Battery undervoltage detection | UN-Vbatt
1055H | Battery not connected | NO-Battery
1056H | Bypass Overvoltage Fault | OV-VBackup
1057H | Bypass overload fault | Over-Load
1058H | DSP self-check exception | DspSelfChk
1059H | Vg sampling exception | Vg-Sample
105AH | DSP hardware mismatch | HardFault
105BH | DSP detects battery overcurrent | BAT-DOC
2010H | Fail Safe | Fail Safe
2011H | Fail Safe | Fail Safe
2012H | Battery communication failure | CAN_Comm_FAIL
2014H | DSP communication failure | DSP_Comm_FAIL
2015H | BMS warning fault 01 | Alarm1-BMS
2016H | Inconsistent battery selection | BatName-FAIL
2017H | BMS warning fault 02 | Alarm2-BMS
2018H | DRM connection failed | DRM_LINK_FAIL
2019H | Abnormal meter selection | MET_SEL_FAIL
201AH | CT Connect Error | CT_FAULT
201BH | DRM Control off grid | DRM_CTL_Off
2020H | High ambient temp (lead-acid) | HighTemp.AMB
2021H | Low ambient temp (lead-acid) | LowTemp.AMB
2030H | Grid-connected Backup overload | BKAC Overload
2040H | EPM hard limit protection | EPM-HardLimit
2041H | AFCI board communication fail | AFCI-Comm-Fail
2042H | AFCI board CT module fail | AFCI-CTModule-Fail
2043H | G100 overcurrent protection State 2 excursion | G100 Overrun

## Fault Code Bits (App2)
Appendix 2: Fault Code Bit Definitions (FC04 registers 3095-3101)
Register | Bit | Fault Name | Value
3095 | BIT00 | LimByTemp | 0=No; 1=Yes
3095 | BIT01 | LimByFreq | 0=No; 1=Yes
3095 | BIT02 | LimByVg | 0=No; 1=Yes
3095 | BIT03 | LimByVar | 0=No; 1=Yes
3095 | BIT04 | LimByUnFr | 0=No; 1=Yes
3095 | BIT05 | Ramp-up | 0=No; 1=Yes
3095 | BIT06 | Overload | 0=No; 1=Yes
3095 | BIT07 | reserved | 0=No; 1=Yes
3095 | BIT08 | LimByDRM | 0=No; 1=Yes
3095 | BIT09 | LimByEPM | 0=No; 1=Yes
3095 | BIT10-15 | reserved | 0=No; 1=Yes
3096 | BIT0 | Grid voltage AB overvoltage | 0=No; 1=Yes
3096 | BIT1 | Grid voltage BC overvoltage | 0=No; 1=Yes
3096 | BIT2 | Grid voltage CA overvoltage | 0=No; 1=Yes
3096 | BIT3 | Grid voltage AB undervoltage | 0=No; 1=Yes
3096 | BIT4 | Grid voltage BC undervoltage | 0=No; 1=Yes
3096 | BIT5 | Grid voltage CA undervoltage | 0=No; 1=Yes
3096 | BIT6 | Grid Over Frequency | 0=No; 1=Yes
3096 | BIT7 | Grid Under Frequency | 0=No; 1=Yes
3096 | BIT8 | Grid Unbalance | 0=No; 1=Yes
3096 | BIT9 | reserved | 0=No; 1=Yes
3096 | BIT10 | Grid Frequency Fluctuation | 0=No; 1=Yes
3096 | BIT11 | Grid phase abnormal | 0=No; 1=Yes
3096 | BIT12 | No Grid | 0=No; 1=Yes
3096 | BIT13 | Grid reverse | 0=No; 1=Yes
3096 | BIT14 | Grid AB transient overvoltage | 0=No; 1=Yes
3096 | BIT15 | Hardware overcurrent screening failure | 0=No; 1=Yes
3097 | BIT0 | DC Over Voltage 01 | 0=No; 1=Yes
3097 | BIT1 | DC Over Voltage 02 | 0=No; 1=Yes
3097 | BIT2 | DC reverse | 0=No; 1=Yes
3097 | BIT3 | Master-slave bus voltage inconsistent | 0=No; 1=Yes
3097 | BIT4 | DC Bus Over Voltage | 0=No; 1=Yes
3097 | BIT5 | DC Bus Under Voltage | 0=No; 1=Yes
3097 | BIT6 | DC Bus Unbalance | 0=No; 1=Yes
3097 | BIT7 | DC bus voltage detection abnormality | 0=No; 1=Yes
3097 | BIT8 | Grid voltage AB avg overvoltage | 0=No; 1=Yes
3097 | BIT9 | Grid voltage BC avg overvoltage | 0=No; 1=Yes
3097 | BIT10 | Grid voltage CA avg overvoltage | 0=No; 1=Yes
3097 | BIT11 | PV mid-point grounding | 0=No; 1=Yes
3097 | BIT12 | DCBoost Fault | 0=No; 1=Yes
3097 | BIT13 | DC hardware overcurrent (ch1-4) | 0=No; 1=Yes
3097 | BIT14 | Grid current tracking fault | 0=No; 1=Yes
3097 | BIT15 | Grid voltage effective value instantaneous OV | 0=No; 1=Yes
3098 | BIT0 | Phase A effective value overcurrent | 0=No; 1=Yes
3098 | BIT1 | Phase B effective value overcurrent | 0=No; 1=Yes
3098 | BIT2 | Phase C effective value overcurrent | 0=No; 1=Yes
3098 | BIT3 | DC1 average overcurrent | 0=No; 1=Yes
3098 | BIT4 | DC2 average overcurrent | 0=No; 1=Yes
3098 | BIT5 | AC hardware overcurrent (ABC) | 0=No; 1=Yes
3098 | BIT6 | DC component of current exceeds limit | 0=No; 1=Yes
3098 | BIT7 | Grid voltage AB overvoltage 02 | 0=No; 1=Yes
3098 | BIT8 | Grid voltage BC overvoltage 02 | 0=No; 1=Yes
3098 | BIT9 | Grid voltage CA overvoltage 02 | 0=No; 1=Yes
3098 | BIT10 | Grid voltage AB undervoltage 02 | 0=No; 1=Yes
3098 | BIT11 | Grid voltage BC undervoltage 02 | 0=No; 1=Yes
3098 | BIT12 | Grid voltage CA undervoltage 02 | 0=No; 1=Yes
3098 | BIT13 | Grid overfrequency 02 | 0=No; 1=Yes
3098 | BIT14 | Grid underfrequency 02 | 0=No; 1=Yes
3098 | BIT15 | Grid overvoltage 03 | 0=No; 1=Yes
3099 | BIT0 | Battery overcurrent | 0=No; 1=Yes
3099 | BIT1 | Module over temperature | 0=No; 1=Yes
3099 | BIT2 | System overtemperature | 0=No; 1=Yes
3099 | BIT3 | Relay failure | 0=No; 1=Yes
3099 | BIT4 | PV midpoint grounding | 0=No; 1=Yes
3099 | BIT5 | Low temperature protection | 0=No; 1=Yes
3099 | BIT6 | Negative ground fault | 0=No; 1=Yes
3099 | BIT7 | Positive ground fault | 0=No; 1=Yes
3099 | BIT8 | 12V undervoltage fault | 0=No; 1=Yes
3099 | BIT9 | Leakage current fault 01 (30mA) | 0=No; 1=Yes
3099 | BIT10 | Leakage current fault 02 (60mA) | 0=No; 1=Yes
3099 | BIT11 | Leakage current fault 03 (150mA) | 0=No; 1=Yes
3099 | BIT12 | Leakage current fault 04 (300mA) | 0=No; 1=Yes
3099 | BIT13 | Leakage current sensor failure | 0=No; 1=Yes
3099 | BIT14 | Grid Disturbance 02 | 0=No; 1=Yes
3099 | BIT15 | Grid current sampling abnormality | 0=No; 1=Yes
3100 | BIT0 | Instantaneous overcurrent grid side | 0=No; 1=Yes
3100 | BIT1 | Battery OV HW / Vbus HW | 0=No; 1=Yes
3100 | BIT2 | LLC hardware overcurrent | 0=No; 1=Yes
3100 | BIT3 | Battery OV detection failure | 0=No; 1=Yes
3100 | BIT4 | Battery UV detection failure | 0=No; 1=Yes
3100 | BIT5 | Level 2 HW overcurrent AC side | 0=No; 1=Yes
3100 | BIT6 | Master-slave DSP comm abnormality | 0=No; 1=Yes
3100 | BIT7 | Detect anomalies from DSP | 0=No; 1=Yes
3100 | BIT8 | AFCI self-test failure | 0=No; 1=Yes
3100 | BIT9 | AFCI failure | 0=No; 1=Yes
3100 | BIT10 | Battery not connected fault | 0=No; 1=Yes
3100 | BIT11 | DSP self-test abnormality | 0=No; 1=Yes
3100 | BIT12 | Grid voltage sampling abnormality | 0=No; 1=Yes
3100 | BIT13 | DSP SW/HW mismatch | 0=No; 1=Yes
3100 | BIT14 | Inverter overvoltage fault | 0=No; 1=Yes
3100 | BIT15 | Load overload fault | 0=No; 1=Yes
3101 | BIT00 | Fail Safe | 0=No; 1=Yes
3101 | BIT01 | DRM controlled off-grid | 0=No; 1=Yes
3101 | BIT02 | CT connection abnormality | 0=No; 1=Yes
3101 | BIT03 | DRM not connected | 0=No; 1=Yes
3101 | BIT04-07 | reserved | 0=No; 1=Yes
3101 | BIT08 | EPM hard limit protection | 0=No; 1=Yes
3101 | BIT09 | AFCI board comm abnormality | 0=No; 1=Yes
3101 | BIT10 | AFCI board CT module hardware abnormality | 0=No; 1=Yes
3101 | BIT11 | G100 overcurrent protection | 0=No; 1=Yes
3101 | BIT12-15 | reserved | 0=No; 1=Yes

## Message Examples
Section 6: Message Frame Examples
Type | Send (Hex) | Response (Hex) | Send Explanation | Response Explanation
Error response | 01 04 0B B6 00 01 D2 08 | 01 84 02 C2 C1 | Addr=01, FC=04, Reg=0BB6, Count=1 | Addr=01, FC=84(04+80H), ErrCode=02 (Invalid address)
FC04 read 1 reg | 01 04 0B B7 00 01 83 C8 | 01 04 02 00 43 F8 C1 | Addr=01, FC=04, StartReg=0BB7, Count=1 | 2 bytes: 0x0043
FC04 read 2 regs | 01 04 0B B7 00 02 C3 C9 | 01 04 04 00 43 02 07 4A F2 |  | Data1=0x0043, Data2=0x0207
FC03 read 1 reg | 01 03 0B B7 00 01 36 08 | 01 03 02 00 13 F9 89 |  | Data=0x0013
FC03 read 3 regs | 01 03 0B B7 00 03 B7 C9 | 01 03 0C 00 13 00 02 00 14 AF 79 |  | Year=19, Month=2, Day=20
FC06 write reactive switch | 01 06 0B FE 00 A1 2B A6 | 01 06 0B FE 00 A1 2B A6 | Addr=01, FC=06, Reg=0BFE(=3070-1), Val=0x00A1 | Echo response
FC06 write reactive limitation 60% | 01 06 0B EA 17 70 A4 0E | 01 06 0B EA 17 70 A4 0E | Reg=0BEA(=3051-1), Val=0x1770=6000=60% | Echo response
FC10 write 3 regs | 01 10 0B B7 00 03 06 00 13 00 02 00 14 51 65 | 01 10 0B B7 00 03 32 0A | 6 bytes data: Year=19, Month=2, Day=20 | Response: addr+count only
Broadcast FC06 | FF 06 0B EB 1F 40 E7 C4 | (No response) | Addr=FF, Reg=0BEB(=3052-1), Val=0x1F40=8000=80kW | Broadcast; slave does not reply