## SUMMARY
항목 | 값 | 비고
제조사 | Senergy (APD) | Solarize 프로토콜 호환
프로토콜 버전 | V1.2.4
용량 | 50kW
MPPT (actual) | 4 | PDF max: 9
Strings per MPPT | 2
Total Strings | 8 | PDF max: 24
IV Scan | Yes | 4 trackers x 2 strings x 64 points
DER-AVM | Yes
카테고리 | Count
INFO | 12
MONITORING | 53 | AC(12)+MPPT4(12)+Temp(1)+Grid(12)+String8(16)
STATUS | 1 | Inverter Mode
ALARM | 3 | 48-bit (3x16)
DER_CONTROL | 11
DER_MONITOR | 11
IV_SCAN | 12 | 4 x (1V + 2I)
H01 매칭 | 20/20 (100%) | 전 필드 매칭 성공
DER 매칭 (제어) | 5/5 (100%) | ON/OFF, PF, Q, P, Mode
DER 매칭 (모니터링) | 11/11 (100%) | V/I/P/Q/PF/F/Status

## ALL
No | Category | Definition | Address | Reg | Type | Unit/Scale | R/W | Comment | H01 Field | H01 Match | DER Match
1 | INFO | Device Model name | 0x1A00 | 8 | string | ASCII | RO |  |  | - | -
2 | INFO | Device Serial number | 0x1A10 | 8 | string | ASCII | RO |  |  | - | -
3 | INFO | Master firmware version | 0x1A1C | 3 | string | ASCII | RO |  |  | - | -
4 | INFO | Slave firmware version | 0x1A26 | 3 | string | ASCII | RO |  |  | - | -
5 | INFO | MPPT Number | 0x1A3B | 1 | U16 |  | RO | 1=1 MPPT |  | - | -
6 | INFO | Nominal Voltage | 0x1A44 | 1 | U16 | 0.1V | RO | 2200=220V |  | - | -
7 | INFO | Nominal Frequency | 0x1A45 | 1 | U16 | 0.01Hz | RO | 5000=50Hz |  | - | -
8 | INFO | Nominal Active Power (Low) | 0x1A46 | 1 | U16 | 1W | RO | 50000W |  | - | -
9 | INFO | Nominal Active Power (High) | 0x1A4E | 1 | U16 | 1W | RO |  |  | - | -
10 | INFO | Grid Phase Number | 0x1A48 | 1 | U16 |  | RO | 3=three phase |  | - | -
11 | INFO | EMS Firmware Version | 0x1A60 | 3 | string | ASCII | RO |  |  | - | -
12 | INFO | LCD firmware version | 0x1A8E | 3 | string | ASCII | RO |  |  | - | -
13 | MONITORING | L1 Voltage | 0x1001 | 1 | U16 | 0.1V | RO |  | r_voltage | O | -
14 | MONITORING | L1 Current | 0x1002 | 1 | U16 | 0.01A | RO |  | r_current | O | -
15 | MONITORING | L1 Power | 0x1003 | 2 | S32 | 0.1W | RO |  | r_power | O | -
16 | MONITORING | L1 Frequency | 0x1005 | 1 | U16 | 0.01Hz | RO |  | frequency | O | -
17 | MONITORING | L2 Voltage | 0x1006 | 1 | U16 | 0.1V | RO |  | s_voltage | O | -
18 | MONITORING | L2 Current | 0x1007 | 1 | U16 | 0.01A | RO |  | s_current | O | -
19 | MONITORING | L2 Power | 0x1008 | 2 | S32 | 0.1W | RO |  | s_power | O | -
20 | MONITORING | L2 Frequency | 0x100A | 1 | U16 | 0.01Hz | RO |  |  | - | -
21 | MONITORING | L3 Voltage | 0x100B | 1 | U16 | 0.1V | RO |  | t_voltage | O | -
22 | MONITORING | L3 Current | 0x100C | 1 | U16 | 0.01A | RO |  | t_current | O | -
23 | MONITORING | L3 Power | 0x100D | 2 | S32 | 0.1W | RO |  | t_power | O | -
24 | MONITORING | L3 Frequency | 0x100F | 1 | U16 | 0.01Hz | RO |  |  | - | -
25 | MONITORING | MPPT1 Voltage | 0x1010 | 1 | U16 | 0.1V | RO |  | mppt1_voltage | O | -
26 | MONITORING | MPPT1 Current | 0x1011 | 1 | S16 | 0.01A | RO |  | mppt1_current | O | -
27 | MONITORING | MPPT1 Power | 0x1012 | 2 | U32 | 0.1W | RO |  | mppt1_power | O | -
28 | MONITORING | MPPT2 Voltage | 0x1014 | 1 | U16 | 0.1V | RO |  | mppt2_voltage | O | -
29 | MONITORING | MPPT2 Current | 0x1015 | 1 | S16 | 0.01A | RO |  | mppt2_current | O | -
30 | MONITORING | MPPT2 Power | 0x1016 | 2 | U32 | 0.1W | RO |  | mppt2_power | O | -
31 | MONITORING | MPPT3 Voltage | 0x1018 | 1 | U16 | 0.1V | RO |  | mppt3_voltage | O | -
32 | MONITORING | MPPT3 Current | 0x1019 | 1 | S16 | 0.01A | RO |  | mppt3_current | O | -
33 | MONITORING | MPPT3 Power | 0x101A | 2 | U32 | 0.1W | RO |  | mppt3_power | O | -
34 | MONITORING | MPPT4 Voltage | 0x103E | 1 | U16 | 0.1V | RO |  | mppt4_voltage | O | -
35 | MONITORING | MPPT4 Current | 0x103F | 1 | S16 | 0.01A | RO |  | mppt4_current | O | -
36 | MONITORING | MPPT4 Power | 0x1040 | 2 | U32 | 0.1W | RO |  | mppt4_power | O | -
37 | MONITORING | Inner Temperature | 0x101C | 1 | S16 | 1C | RO |  | temperature | O | -
38 | MONITORING | Grid total Active Power | 0x1037 | 2 | S32 | 0.1W | RO | L1+L2+L3 | ac_power | O | -
39 | MONITORING | Grid total Reactive Power | 0x1039 | 2 | S32 | 0.1Var | RO | L1+L2+L3 | reactive_power | O | -
40 | MONITORING | PV Today Peak Power | 0x103B | 2 | S32 | 0.1W | RO |  |  | - | -
41 | MONITORING | Power Factor | 0x103D | 1 | S16 | 0.001 | RO |  | power_factor | O | -
42 | MONITORING | PV total input power | 0x1048 | 2 | U32 | 0.1W | RO | All MPPT sum | pv_power | O | -
43 | MONITORING | Decimals of total energy | 0x104C | 1 | U16 | Wh | RO | 0x1021 decimal part | cumulative_energy(dec) | O | -
44 | MONITORING | Total Energy | 0x1021 | 2 | U32 | kWh | RO |  | cumulative_energy | O | -
45 | MONITORING | Total generation time | 0x1023 | 2 | U32 | Hour | RO |  |  | - | -
46 | MONITORING | Today Energy | 0x1027 | 2 | U32 | Wh | RO |  | daily_energy | O | -
47 | MONITORING | Fuse open data | 0x1034 | 2 | U16 |  | RO | B1-B8 |  | - | -
48 | MONITORING | External fan speed duty | 0x120C | 1 | U16 | 1% | RO |  |  | - | -
49 | MONITORING | DER-AVM meter connect status | 0x1210 | 1 | U16 |  | RO | 0:disconn, 1:conn |  | - | -
50 | MONITORING | String1 input voltage | 0x1050 | 1 | U16 | 0.1V | RO |  | string1_voltage | O | -
51 | MONITORING | String1 input current | 0x1051 | 1 | S16 | 0.01A | RO |  | string1_current | O | -
52 | MONITORING | String2 input voltage | 0x1052 | 1 | U16 | 0.1V | RO |  | string2_voltage | O | -
53 | MONITORING | String2 input current | 0x1053 | 1 | S16 | 0.01A | RO |  | string2_current | O | -
54 | MONITORING | String3 input voltage | 0x1054 | 1 | U16 | 0.1V | RO |  | string3_voltage | O | -
55 | MONITORING | String3 input current | 0x1055 | 1 | S16 | 0.01A | RO |  | string3_current | O | -
56 | MONITORING | String4 input voltage | 0x1056 | 1 | U16 | 0.1V | RO |  | string4_voltage | O | -
57 | MONITORING | String4 input current | 0x1057 | 1 | S16 | 0.01A | RO |  | string4_current | O | -
58 | MONITORING | String5 input voltage | 0x1058 | 1 | U16 | 0.1V | RO |  | string5_voltage | O | -
59 | MONITORING | String5 input current | 0x1059 | 1 | S16 | 0.01A | RO |  | string5_current | O | -
60 | MONITORING | String6 input voltage | 0x105A | 1 | U16 | 0.1V | RO |  | string6_voltage | O | -
61 | MONITORING | String6 input current | 0x105B | 1 | S16 | 0.01A | RO |  | string6_current | O | -
62 | MONITORING | String7 input voltage | 0x105C | 1 | U16 | 0.1V | RO |  | string7_voltage | O | -
63 | MONITORING | String7 input current | 0x105D | 1 | S16 | 0.01A | RO |  | string7_current | O | -
64 | MONITORING | String8 input voltage | 0x105E | 1 | U16 | 0.1V | RO |  | string8_voltage | O | -
65 | MONITORING | String8 input current | 0x105F | 1 | S16 | 0.01A | RO |  | string8_current | O | -
66 | STATUS | Inverter Mode | 0x101D | 1 | U16 |  | RO | 0x00=Initial, 0x01=Standby, 0x03=On-Grid, 0x04=Off-Grid, 0x05=Fault, 0x09=Shutdown | status | O | -
67 | ALARM | Error Code1 | 0x101E | 1 | U16 |  | RO | B0:DC-bias overcurr B1:Relay abnormal B2:Remote off B3:Over temp B4:GFCI B5:PV reverse B6:Sys type err B7:Fan B8:DC-link B9:DC-link OV B10:Comm err B11:SW incompat B12:Storage B13:Data B14:Inv abnormal B15:Boost | alarm1 | O | -
68 | ALARM | Error Code2 | 0x101F | 1 | U16 |  | RO | B0:Grid OV B1:Grid UV B2:Grid absent B3:Grid OF B4:Grid UF B5:PV OV B6:PV insul B7:Leakage B8:Power limit B9:PSU abnormal B10:PV string B11:PV UV B12:Irrad weak B13:Grid abnormal B14:Arc fault B15:AC avg V high | alarm2 | O | -
69 | ALARM | Error Code3 | 0x1020 | 1 | U16 |  | RO | B0:Rsvd B1:EEPROM fail B2:Rsvd B3:PID B4:AFCI lost B5:Logger lost B6:Meter lost B7:Inv lost B8:Grid N B9:SPD B10:Parallel ID B11:SYN signal B12:BAT B13:GRID B14:Gen V abnormal B15:Rsvd | alarm3 | O | -
70 | DER_CONTROL | DER-AVM mode | 0x1211 | 1 | U16 |  | RW | 0:self, 1:DER-AVM |  | - | O
71 | DER_CONTROL | Power factor setting | 0x07D0 | 1 | S16 | 0.001 | RW | [-1000,-800],[800,1000] Def 1000 | pf_set | - | O
72 | DER_CONTROL | Action mode | 0x07D1 | 1 | U16 |  | RW | 0:self, 2:DER-AVM, 5:Q(V). Def 2 | action_mode | - | O
73 | DER_CONTROL | Reactive power % setting | 0x07D2 | 1 | S16 | 0.1% | RW | [-484,484] Def 0 | q_set | - | O
74 | DER_CONTROL | Active power % setting | 0x07D3 | 1 | U16 | 0.1% | RW | [0,1100] Def 1000=no limit | p_limit | - | O
75 | DER_CONTROL | Inverter off | 0x0834 | 1 | U16 |  | RW | 0:on, 1:off. Def 0 | on_off | - | O
76 | DER_CONTROL | Clear PV insulation warning | 0x0835 | 1 | U16 |  | RW | 0:Non-active, 1:Clear |  | - | -
77 | DER_CONTROL | Power derating % by Modbus | 0x3005 | 1 | U16 |  | RW | [0,110] |  | - | -
78 | DER_CONTROL | Output reactive power mode | 0x5030 | 1 | U16 |  | RW | 0~9 modes |  | - | -
79 | DER_CONTROL | Power factor (grid code) | 0x5031 | 1 | S16 | 0.001 | RW | [-1000,-800],[800,1000] |  | - | -
80 | DER_CONTROL | Q Reference reactive power | 0x5032 | 1 | S16 | 0.1kVAR | RW |  |  | - | -
81 | DER_MONITOR | DEA-AVM L1 Current | 0x03E8 | 2 | S32 | 0.1A | RO |  | r_current(dea) | - | O
82 | DER_MONITOR | DEA-AVM L2 Current | 0x03EA | 2 | S32 | 0.1A | RO |  | s_current(dea) | - | O
83 | DER_MONITOR | DEA-AVM L3 Current | 0x03EC | 2 | S32 | 0.1A | RO |  | t_current(dea) | - | O
84 | DER_MONITOR | DEA-AVM L1 Voltage | 0x03EE | 2 | S32 | 0.1V | RO |  | r_voltage(dea) | - | O
85 | DER_MONITOR | DEA-AVM L2 Voltage | 0x03F0 | 2 | S32 | 0.1V | RO |  | s_voltage(dea) | - | O
86 | DER_MONITOR | DEA-AVM L3 Voltage | 0x03F2 | 2 | S32 | 0.1V | RO |  | t_voltage(dea) | - | O
87 | DER_MONITOR | DEA-AVM Grid Active Power | 0x03F4 | 2 | S32 | 0.1kW | RO | L1+L2+L3 | ac_power(dea) | - | O
88 | DER_MONITOR | DEA-AVM Grid Reactive Power | 0x03F6 | 2 | S32 | Var | RO | L1+L2+L3 | reactive_power(dea) | - | O
89 | DER_MONITOR | DEA-AVM Power Factor | 0x03F8 | 2 | S32 | 0.001 | RO |  | pf(dea) | - | O
90 | DER_MONITOR | DEA-AVM Frequency | 0x03FA | 2 | S32 | 0.1Hz | RO |  | freq(dea) | - | O
91 | DER_MONITOR | DEA-AVM Status Flag 1 | 0x03FC | 2 | S32 |  | RO | B1:Inv action B2:CB action B3:Run state B4:AP ctrl ack B5:Inv ctrl ack | status_flag(dea) | - | O
92 | IV_SCAN | Tracker 1 voltage | 0x8000 | 64 | U16 | 0.1V | RO | 64 points |  | - | -
93 | IV_SCAN | String 1-1 current | 0x8040 | 64 | S16 | 0.01A | RO | 64 points |  | - | -
94 | IV_SCAN | String 1-2 current | 0x8080 | 64 | S16 | 0.01A | RO | 64 points |  | - | -
95 | IV_SCAN | Tracker 2 voltage | 0x8140 | 64 | U16 | 0.1V | RO | 64 points |  | - | -
96 | IV_SCAN | String 2-1 current | 0x8180 | 64 | S16 | 0.01A | RO | 64 points |  | - | -
97 | IV_SCAN | String 2-2 current | 0x81C0 | 64 | S16 | 0.01A | RO | 64 points |  | - | -
98 | IV_SCAN | Tracker 3 voltage | 0x8280 | 64 | U16 | 0.1V | RO | 64 points |  | - | -
99 | IV_SCAN | String 3-1 current | 0x82C0 | 64 | S16 | 0.01A | RO | 64 points |  | - | -
100 | IV_SCAN | String 3-2 current | 0x8300 | 64 | S16 | 0.01A | RO | 64 points |  | - | -
101 | IV_SCAN | Tracker 4 voltage | 0x83C0 | 64 | U16 | 0.1V | RO | 64 points |  | - | -
102 | IV_SCAN | String 4-1 current | 0x8400 | 64 | S16 | 0.01A | RO | 64 points |  | - | -
103 | IV_SCAN | String 4-2 current | 0x8440 | 64 | S16 | 0.01A | RO | 64 points |  | - | -

## H01_MATCH
No | H01 Field (UDP Protocol) | Size | Unit | Modbus Register | Address | Scale | Match
1 | PV 전압 | 2B | V | MPPT1~4 Voltage 평균(>100V) | 0x1010~0x103E | 0.1V→1V | O
2 | PV 전류 | 2B | A | String1~8 Current 합계 | 0x1051~0x105F | 0.01A→1A | O
3 | PV 출력 | 4B | W | PV total input power | 0x1048 | 0.1W→1W | O
4 | R (RS)상 전압 | 2B | V | L1 Voltage | 0x1001 | 0.1V→1V | O
5 | S (ST)상 전압 | 2B | V | L2 Voltage | 0x1006 | 0.1V→1V | O
6 | T (TR)상 전압 | 2B | V | L3 Voltage | 0x100B | 0.1V→1V | O
7 | R상 전류 | 2B | A | L1 Current | 0x1002 | 0.01A→1A | O
8 | S상 전류 | 2B | A | L2 Current | 0x1007 | 0.01A→1A | O
9 | T상 전류 | 2B | A | L3 Current | 0x100C | 0.01A→1A | O
10 | 인버터 출력 | 4B | W | Grid total Active Power | 0x1037 | 0.1W→1W | O
11 | 역률 | 2B | %x10 | Power Factor | 0x103D | 0.001→%x10 | O
12 | 주파수 | 2B | Hzx10 | L1 Frequency | 0x1005 | 0.01Hz→Hzx10 | O
13 | 누적 발전량 | 8B | Wh | Total Energy + Decimals | 0x1021+0x104C | kWh→Wh | O
14 | 상태 정보 1 | 2B |  | Inverter Mode | 0x101D | U16 | O
15 | 상태 정보 2 | 2B |  | Error Code1 | 0x101E | U16 | O
16 | 상태 정보 3 | 2B |  | Error Code2 | 0x101F | U16 | O
17 | 상태 정보 4 | 2B |  | Error Code3 | 0x1020 | U16 | O
18 | MPPT 전압 x4 | 2Bx4 | Vx10 | MPPT1~4 Voltage | 0x1010~0x103E | 0.1V→Vx10 | O
19 | MPPT 전류 x4 | 2Bx4 | Ax10 | MPPT1~4 Current | 0x1011~0x103F | 0.01A→Ax10 | O
20 | STRING 전류 x8 | 2Bx8 | Ax10 | String1~8 Current | 0x1051~0x105F | 0.01A→Ax10 | O
H01 매칭 결과
매칭: 20/20 (100%)

## DER_MATCH
No | DER Field (UDP Protocol) | Direction | Modbus Register | Address | Scale/Range | Match
1 | 인버터 기동/정지 | Control(W) | Inverter off | 0x0834 | 0:on, 1:off | O
2 | 역률 설정 값 | Control(W) | Power factor setting | 0x07D0 | 0.001, [-1000,-800]∪[800,1000] | O
3 | 동작 모드 | Control(W) | Action mode | 0x07D1 | 0:self, 2:DER-AVM, 5:Q(V) | O
4 | 무효전력 설정 값 | Control(W) | Reactive power % setting | 0x07D2 | 0.1%, [-484,484] | O
5 | 유효전력 설정 값 | Control(W) | Active power % setting | 0x07D3 | 0.1%, [0,1100] 1000=100% | O
6 | R상 전류 | Monitor(R) | DEA-AVM L1 Current | 0x03E8 | S32, 0.1A | O
7 | S상 전류 | Monitor(R) | DEA-AVM L2 Current | 0x03EA | S32, 0.1A | O
8 | T상 전류 | Monitor(R) | DEA-AVM L3 Current | 0x03EC | S32, 0.1A | O
9 | R (RS)상 전압 | Monitor(R) | DEA-AVM L1 Voltage | 0x03EE | S32, 0.1V | O
10 | S (ST)상 전압 | Monitor(R) | DEA-AVM L2 Voltage | 0x03F0 | S32, 0.1V | O
11 | T (TR)상 전압 | Monitor(R) | DEA-AVM L3 Voltage | 0x03F2 | S32, 0.1V | O
12 | 유효전력 | Monitor(R) | DEA-AVM Grid Active Power | 0x03F4 | S32, 0.1kW | O
13 | 무효전력 | Monitor(R) | DEA-AVM Grid Reactive Power | 0x03F6 | S32, Var | O
14 | 역률 | Monitor(R) | DEA-AVM Power Factor | 0x03F8 | S32, 0.001 | O
15 | 주파수 | Monitor(R) | DEA-AVM Frequency | 0x03FA | S32, 0.1Hz | O
16 | 상태 플래그 | Monitor(R) | DEA-AVM Status Flag 1 | 0x03FC | S32, bit field | O
DER-AVM 매칭 결과
제어(Control): 5/5 (100%)
모니터링(Monitor): 11/11 (100%)