## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | 1KW-50KW
프로토콜 버전 | V3.05
설비 타입 | inverter
MPPT | 2
String | 2
String 모니터링 | No (MPPT당 1 String)
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | 1KW-50KW Modbus RS485 RTU Protocol.pdf
추출 일시 | 2026-04-03 16:35
H01 매칭 | 19/21
DER 매칭 | 33/33
추출 레지스터 | 127
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Fw versionM | 0x000A | 03 | U16 |  | RO
2 | Fw version L | 0x000B | 03 | U16 |  | RO
3 | Fw version2H | 0x000C | 03 | ASCII |  | RO
4 | Fw version2M | 0x000D | 03 | U16 |  | RO
5 | Fw version2L | 0x000E | 03 | U16 |  | RO
6 | L2_CURRENT | 0x0013 | 04 | U16 | A 0.1 | RO |  | Iac2
7 | V3.00 | 0x0013 |  | U16 |  | RO
8 | Serial NO. 5 | 0x0017 | 03 | ASCII |  | RO
9 | Serial No. 4 | 0x0018 | 03 | U16 |  | RO
10 | Serial No. 3 | 0x0019 | 03 | U16 |  | RO
11 | Serial No. 2 | 0x001A | 03 | U16 |  | RO
12 | Serial No. 1 | 0x001B | 03 | U16 |  | RO
13 | Epv1 today L_ | 0x0031 | 04 | U16 | kWh 0.1 | RO
14 | Sys Min | 0x0031 | 03 | U16 |  | RO
15 | PFModel | 0x0063 | 03 | U16 |  | RO
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Epv1 today H_ | 0x0030 | 04 | U16 |  | RO
2 | Sys Hour | 0x0030 | 03 | U16 |  | RO
3 | Real value | 0x008D | 04 | U16 | V 0.1 | RO
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Epv1 total H_ | 0x0032 | 04 | U16 |  | RO
2 | Sys Sec | 0x0032 | 03 | U16 |  | RO
3 | Epv1 total L_ | 0x0033 | 04 | U16 | kWh 0.1 | RO
4 | Grid Faultrecord 4 - code | 0x0069 | 04 | U16 |  | RO
5 | Grid Faultrecord 4 - year¦month | 0x006A | 04 | U16 |  | RO
6 | L1_VOLTAGE | 0x006B | 04 | U16 |  | RO | r_voltage | Grid Faultrecord 4 - day¦hour
7 | Grid Faultrecord 5 - code | 0x006E | 04 | U16 |  | RO
8 | Grid Faultrecord 5 - year¦month | 0x006F | 04 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 19/21
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x000B | PV_POWER | U16 | W | 0.1
13 | cumulative_energy | PDF | O | 0x001C | CUMULATIVE_ENERGY | U16 | KWH | 0.1 | KWH→Wh (*1000)
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | X | - | - |  |  |  | Work State 미발견
16 | alarm1 | PDF | X | - | - |  |  |  | 알람 미발견
17 | alarm2 | PDF | - | - | - |  |  |  | 보조 알람 없음
18 | alarm3 | PDF | - | - | - |  |  |  | 보조 알람 없음
19 | mppt1_voltage | PDF | O | 0x0003 | Vpv1 | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x0004 | PV1Curr | U16 | A | 0.1
21 | mppt2_voltage | PDF | O | 0x0007 | Vpv2 | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x0008 | PV2Curr | U16 | A | 0.1
23 | string1_current | HANDLER | O | 0x0004 | PV1Curr | U16 | A | 0.1
24 | string2_current | HANDLER | O | 0x0008 | PV2Curr | U16 | A | 0.1

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 2ch / String 2ch
MPPT 채널 수 | 2
String 채널 수 | 2
String 모니터링 | No (MPPT당 1 String)
MPPT 채널 H01 매칭 (4개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x0003 | Vpv1 | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x0004 | PV1Curr | U16 | A | 0.1
3 | mppt2_voltage | PDF | O | 0x0007 | Vpv2 | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x0008 | PV2Curr | U16 | A | 0.1
String 채널 H01 매칭 (2개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | 0x0004 | PV1Curr | U16 | A | 0.1
2 | string2_current | HANDLER | O | 0x0008 | PV2Curr | U16 | A | 0.1
MONITORING 전체 (101개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Inverter Status | 0x0000 | 04 | U16 |  | RO | power_factor
2 | POWER_FACTOR | 0x0000 | 03 | U16 |  | RO | power_factor
3 | Ppv H | 0x0001 | 04 | U16 | W 0.1 | RO
4 | V1.00 | 0x0001 |  | U16 |  | RO
5 | Ppv L | 0x0002 | 04 | U16 | W 0.1 | RO
6 | V1.10 | 0x0002 |  | U16 |  | RO
7 | PF CMDmemorystate | 0x0002 | 03 | U16 |  | RO
8 | Vpv1 | 0x0003 | 04 | U16 | V 0.1 | RO | mppt1_voltage
9 | V2.01 | 0x0003 |  | U16 |  | RO
10 | Active PRate | 0x0003 | 03 | U16 |  | RO
11 | PV1Curr | 0x0004 | 04 | U16 | A 0.1 | RO | mppt1_current
12 | Reactive PRate | 0x0004 | 03 | U16 |  | RO
13 | PV1Watt H | 0x0005 | 04 | U16 | W 0.1 | RO | mppt1_power
14 | PV1Watt L | 0x0006 | 04 | U16 | W 0.1 | RO | mppt1_power
15 | Pmax H | 0x0006 | 03 | U16 | VA 0.1 | RO
16 | Vpv2 | 0x0007 | 04 | U16 | V 0.1 | RO | mppt2_voltage
17 | Pmax L | 0x0007 | 03 | U16 | VA 0.1 | RO
18 | PV2Curr | 0x0008 | 04 | U16 | A 0.1 | RO | mppt2_current
19 | Vnormal | 0x0008 | 03 | U16 | V 0.1 | RO
20 | PV2Watt H | 0x0009 | 04 | U16 | W 0.1 | RO | mppt2_power
21 | PV2Watt L | 0x000A | 04 | U16 | W 0.1 | RO | mppt2_power
22 | PV_POWER | 0x000B | 04 | U16 | W 0.1 | RO | pv_power
23 | PV_POWER | 0x000C | 04 | U16 | W 0.1 | RO | pv_power
24 | FREQUENCY | 0x000D | 04 | U16 | Hz 0.01 | RO | frequency
25 | L1_VOLTAGE | 0x000E | 04 | U16 | V 0.1 | RO | r_voltage
26 | L1_CURRENT | 0x000F | 04 | U16 | A 0.1 | RO | r_current
27 | FREQUENCY | 0x000F | 03 | U16 |  | RO | frequency
28 | PV_POWER | 0x0010 | 04 | U16 | VA 0.1 | RO | pv_power
29 | PV_POWER | 0x0011 | 04 | U16 | VA 0.1 | RO | pv_power
30 | L2_VOLTAGE | 0x0012 | 04 | U16 | V 0.1 | RO | s_voltage
31 | PV_POWER | 0x0014 | 04 | U16 | VA 0.1 | RO | pv_power
32 | V3.01 | 0x0014 |  | U16 |  | RO
33 | PV_POWER | 0x0015 | 04 | U16 | VA 0.1 | RO | pv_power
34 | V3.02 | 0x0015 |  | U16 |  | RO
35 | L3_VOLTAGE | 0x0016 | 04 | U16 | V 0.1 | RO | t_voltage
36 | V3.03 | 0x0016 |  | U16 |  | RO
37 | L3_CURRENT | 0x0017 | 04 | U16 | A 0.1 | RO | t_current
38 | V3.04 | 0x0017 |  | U16 |  | RO
39 | PV_POWER | 0x0018 | 04 | U16 | VA 0.1 | RO | pv_power
40 | PV_POWER | 0x0019 | 04 | U16 | VA 0.1 | RO | pv_power
41 | Energy today H | 0x001A | 04 | U16 | KWH 0.1 | RO
42 | Energy today L | 0x001B | 04 | U16 | KWH 0.1 | RO
43 | CUMULATIVE_ENERGY | 0x001C | 04 | U16 | KWH 0.1 | RO | cumulative_energy
44 | Moudle H | 0x001C | 03 | U16 |  | RO
45 | CUMULATIVE_ENERGY | 0x001D | 04 | U16 | KWH 0.1 | RO | cumulative_energy
46 | Moudle L | 0x001D | 03 | U16 |  | RO
47 | Time total H | 0x001E | 04 | U16 |  | RO
48 | ComAddress | 0x001E | 03 | U16 |  | RO
49 | DAILY_ENERGY | 0x001F | 04 | U16 |  | RO | daily_energy
50 | Temperature | 0x0020 | 04 | U16 |  | RO | temperature
51 | AutoTestStart | 0x0022 | 03 | U16 |  | RO
52 | Fault code | 0x0028 | 04 | U16 |  | RO
53 | IPMTemperature | 0x0029 | 04 | U16 |  | RO
54 | Sys Year | 0x002D | 03 | U16 |  | RO
55 | L3_VOLTAGE | 0x002E | 03 | U16 |  | RO | t_voltage
56 | L3_CURRENT | 0x002F | 03 | U16 |  | RO | t_current
57 | Epv2 today H_ | 0x0034 | 04 | U16 |  | RO
58 | Epv2 today L_ | 0x0035 | 04 | U16 | kWh 0.1 | RO
59 | Epv2 total H_ | 0x0036 | 04 | U16 |  | RO
60 | Epv2 total L_ | 0x0037 | 04 | U16 | kWh 0.1 | RO
61 | Epv total H_ | 0x0038 | 04 | U16 |  | RO
62 | Epv total L_ | 0x0039 | 04 | U16 | kWh 0.1 | RO
63 | WarningCode | 0x0040 | 04 | U16 |  | RO
64 | ModbusVersion | 0x0049 | 03 | U16 |  | RO
65 | FreqDerateStart | 0x0051 | 03 | U16 |  | RO
66 | Grid Faultrecord 1 - code | 0x005A | 04 | U16 |  | RO
67 | PFLineP1 L_P | 0x005A | 03 | U16 |  | RO
68 | Grid Faultrecord 1 - year¦month | 0x005B | 04 | U16 |  | RO
69 | L1_VOLTAGE | 0x005C | 04 | U16 |  | RO | r_voltage
70 | PFLineP2 L_P | 0x005C | 03 | U16 |  | RO
71 | L2_VOLTAGE | 0x005D | 04 | U16 |  | RO | s_voltage
72 | PFLineP2 P_F | 0x005D | 03 | U16 |  | RO
73 | L3_VOLTAGE | 0x005E | 04 | U16 |  | RO | t_voltage
74 | PFLineP3 L_P | 0x005E | 03 | U16 |  | RO
75 | Grid Faultrecord 2 - code | 0x005F | 04 | U16 |  | RO
76 | PFLineP3 P_F | 0x005F | 03 | U16 |  | RO
77 | PFLineP4 L_P | 0x0060 | 03 | U16 |  | RO
78 | L1_VOLTAGE | 0x0061 | 04 | U16 |  | RO | r_voltage
79 | PFLineP4 P_F | 0x0061 | 03 | U16 |  | RO
80 | L2_VOLTAGE | 0x0062 | 04 | U16 |  | RO | s_voltage
81 | L3_VOLTAGE | 0x0063 | 04 | U16 |  | RO | t_voltage
82 | Grid Faultrecord 3 - code | 0x0064 | 04 | U16 |  | RO
83 | FLrate | 0x0064 | 03 | U16 |  | RO
84 | Grid Faultrecord 3 - year¦month | 0x0065 | 04 | U16 |  | RO
85 | L1_VOLTAGE | 0x0066 | 04 | U16 |  | RO | r_voltage
86 | L2_VOLTAGE | 0x0067 | 04 | U16 |  | RO | s_voltage
87 | L3_VOLTAGE | 0x0068 | 04 | U16 |  | RO | t_voltage
88 | L2_VOLTAGE | 0x006C | 04 | U16 |  | RO | s_voltage
89 | L3_VOLTAGE | 0x006D | 04 | U16 |  | RO | t_voltage
90 | L1_VOLTAGE | 0x0070 | 04 | U16 |  | RO | r_voltage
91 | L2_VOLTAGE | 0x0071 | 04 | U16 |  | RO | s_voltage
92 | L3_VOLTAGE | 0x0072 | 04 | U16 |  | RO | t_voltage
93 | bTestProcess<<8 ¦bAutoTestStep | 0x0087 | 04 | U16 |  | RO
94 | wAutoTestResult | 0x0088 | 04 | U16 |  | RO
95 | cTestStepStop | 0x0089 | 04 | U16 |  | RO
96 | Value Limit | 0x008B | 04 | U16 | V 0.1 | RO
97 | Time Limit | 0x008C | 04 | U16 |  | RO
98 | Test value | 0x008E | 04 | U16 | V 0.1 | RO
99 | Test treat value | 0x008F | 04 | U16 | V 0.1 | RO
100 | Test treat time | 0x0090 | 04 | U16 |  | RO
101 | Powerfactor | 0x2710 | 03 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)