## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=4, STR=8)
제조사 | ABB-PV
용량 | -
MPPT | 4
String/MPPT | 2
Total Strings | 8
H01 매칭 | 22/27
DER 매칭 | 33/33
총 레지스터 | 222
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Interlock fail | 0x0031 | U16 |  | RO
2 | Inverter – Serial number (SN0) | 0x0068 | ASCII |  | WO
3 | Inverter – Serial number (SN1) | 0x0069 | ASCII |  | RO
4 | Inverter – Serial number (SN2) | 0x006A | ASCII |  | RO
5 | Inverter – Serial number (SN3) | 0x006B | ASCII |  | RO
6 | Inverter – Serial number (SN4) | 0x006C | ASCII |  | RO
7 | Inverter – Serial number (SN5) | 0x006D | ASCII |  | RO
8 | Inverter – Model identifier | 0x0074 | U16 |  | RO
9 | Inverter – States (Byte 4) – Alarm state | 0x0080 | U16 |  | RO
10 | Dynamic Mode – Active Powermanagement; set Active Powerexpressed as percentage ofNominal Power (P ) in 1% stepsNOM | 0x00D2 | U16 |  | RO
11 | Permanent Mode – Active Powermanagement; set Active Powerexpressed as percentage ofNominal Power (P ) in 1% stepsNOM | 0x00D4 | U16 |  | RO
12 | Permanent Mode – Reset ActivePower to 100% of Nominal Power(P )NOM | 0x00D7 | U16 |  | RO
13 | Dynamic Mode – Reactive Powermanagement; set fixed Q bypercentage of Nominal Power(P ) in 1% stepsNOM | 0x00E1 | U16 |  | RO
14 | Inverter – Serial number (SN0) | 0x00FE | ASCII |  | WO
15 | Inverter – Serial number (SN1) | 0x00FF | ASCII |  | RO
16 | Inverter – Serial number (SN2) | 0x0100 | ASCII |  | RO
17 | Inverter – Serial number (SN3) | 0x0101 | ASCII |  | RO
18 | Inverter – Serial number (SN4) | 0x0102 | ASCII |  | RO
19 | Inverter – Serial number (SN5) | 0x0103 | ASCII |  | RO
20 | Communication Board – Serial number (SN0) | 0x0114 | ASCII |  | WO
21 | Communication Board – Serial number (SN1) | 0x0115 | ASCII |  | RO
22 | Communication Board – Serial number (SN2) | 0x0116 | ASCII |  | RO
23 | Communication Board – Serial number (SN3) | 0x0117 | ASCII |  | RO
24 | Communication Board – Serial number (SN4) | 0x0118 | ASCII |  | RO
25 | Communication Board – Serial number (SN5) | 0x0119 | ASCII |  | RO
26 | Fuse Control Board – Serial number (SN0) | 0x0124 | U16 |  | WO
27 | Fuse Control Board – Serial number (SN1) | 0x0125 | U16 |  | RO
28 | Fuse Control Board – Serial number (SN2) | 0x0126 | U16 |  | RO
29 | Fuse Control Board – Serial number (SN3) | 0x0127 | U16 |  | RO
30 | Fuse Control Board – Serial number (SN4) | 0x0128 | U16 |  | RO
31 | Fuse Control Board – Serial number (SN5) | 0x0129 | U16 |  | RO
32 | Dynamic Mode – Reactive Powermanagement; set fixed Q bypercentage of Nominal Power(P ) in 1% stepsNOM | 0x01FB | U16 |  | RO
33 | Dynamic Mode – Active Powermanagement; set Active Powerexpressed as percentage ofNominal Power (P ) in 1% stepsNOM | 0x01FC | U16 |  | RO
34 | Permanent Mode – Active Powermanagement; set Active Powerexpressed as percentage ofNominal Power (P ) in 1% stepsNOM | 0x0200 | U16 |  | RO
H01 MONITORING (178개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | POWER_FACTOR | 0x0000 | U16 |  | RO | power_factor
2 | Wait Sun/Grid | 0x0001 | U16 |  | RO
3 | Checking Grid | 0x0002 | U16 |  | RO
4 | Measuring Riso | 0x0003 | U16 |  | RO
5 | DC/DC Start | 0x0004 | U16 |  | RO
6 | Inverter Start | 0x0005 | U16 |  | RO
7 | Bulk UV | 0x0006 | U16 |  | RO
8 | Recovery | 0x0007 | U16 |  | RO
9 | Pause | 0x0008 | U16 |  | RO
10 | Ground Fault | 0x0009 | U16 |  | RO
11 | OTH Fault | 0x000A | U16 |  | RO
12 | Address Setting | 0x000B | U16 |  | RO
13 | L1_VOLTAGE | 0x000C | U16 |  | RO | r_voltage
14 | L2_VOLTAGE | 0x000D | U16 |  | RO | s_voltage
15 | Leak Fault | 0x000F | U16 |  | RO | frequency
16 | Waiting for manual reset | 0x0010 | U16 |  | RO
17 | Internal Error E026 | 0x0011 | U16 |  | RO | s_voltage
18 | Internal Error E027 | 0x0012 | U16 |  | RO | s_voltage
19 | Internal Error E028 | 0x0013 | U16 |  | RO | s_voltage
20 | Internal Error E029 | 0x0014 | U16 |  | RO | s_voltage
21 | Internal Error E030 | 0x0015 | U16 |  | RO | s_voltage
22 | Sending Wind Table | 0x0016 | U16 |  | RO
23 | Failed Sending table | 0x0017 | U16 |  | RO
24 | UTH Fault | 0x0018 | U16 |  | RO
25 | Remote OFF | 0x0019 | U16 |  | RO
26 | Interlock Fail | 0x001A | U16 |  | RO
27 | Executing Autotest | 0x001B | U16 |  | RO
28 | Self-Test 3 | 0x001C | U16 |  | RO | r_voltage
29 | Self-Test 4 | 0x001D | U16 |  | RO | r_voltage
30 | Waiting Sun | 0x001E | U16 |  | RO
31 | Temperature Fault | 0x001F | U16 |  | RO | daily_energy
32 | TEMPERATURE | 0x0020 | U16 |  | RO | temperature
33 | Int. Com. Fault | 0x0021 | U16 |  | RO
34 | Slave Insertion | 0x0022 | U16 |  | RO
35 | DC Switch Open | 0x0023 | U16 |  | RO
36 | TRAS Switch Open | 0x0024 | U16 |  | RO
37 | FREQUENCY | 0x0025 | U16 |  | RO | frequency
38 | L1_VOLTAGE | 0x0026 | U16 |  | RO | r_voltage
39 | Vref Error | 0x0027 | U16 |  | RO | r_current
40 | Input UC | 0x0029 | U16 |  | RO
41 | L2_VOLTAGE | 0x002A | U16 |  | RO | s_voltage
42 | L2_CURRENT | 0x002B | U16 |  | RO | s_current
43 | Waiting Start | 0x002C | U16 |  | RO
44 | MPPT | 0x002D | U16 |  | RO
45 | L3_VOLTAGE | 0x002E | U16 |  | RO | t_voltage
46 | L3_CURRENT | 0x002F | U16 |  | RO | t_current
47 | Battery low | 0x0034 | U16 |  | RO
48 | Arc fault self-test fail | 0x0035 | U16 |  | RO
49 | Input UC | 0x0036 | U16 |  | RO
50 | L2_VOLTAGE | 0x0037 | U16 |  | RO | s_voltage
51 | Fan Stuck | 0x0038 | U16 |  | RO
52 | DC Switch Open | 0x0039 | U16 |  | RO
53 | Tras Switch Open | 0x003A | U16 |  | RO
54 | AC Switch Open | 0x003B | U16 |  | RO
55 | Bulk UV | 0x003C | U16 |  | RO
56 | Autoexclusion | 0x003D | U16 |  | RO
57 | Grid df/dt | 0x003E | U16 |  | RO
58 | Den switch Open | 0x003F | U16 |  | RO
59 | DC Door Open | 0x0041 | U16 |  | RO
60 | AC Door Open | 0x0042 | U16 |  | RO
61 | Arc fault | 0x004F | U16 |  | RO
62 | Arc fault self-test fail | 0x0052 | U16 |  | RO
63 | Communication loss with Communication Board | 0x0053 | U16 |  | RO
64 | Arc fault reset by user | 0x0054 | U16 |  | RO
65 | Arc fault wrong configuration | 0x0055 | U16 |  | RO
66 | Erasing Internal Eeprom | 0x0062 | U16 |  | RO
67 | Erasing External Eeprom | 0x0063 | U16 |  | RO
68 | Inverter – Map size | 0x0065 | U16 |  | RO
69 | Inverter address | 0x0067 | U16 |  | RO | s_voltage
70 | L1_VOLTAGE | 0x0070 | ASCII |  | RO | r_voltage
71 | L2_VOLTAGE | 0x0071 | ASCII |  | RO | s_voltage
72 | L3_VOLTAGE | 0x0072 | ASCII |  | RO | t_voltage
73 | L1_CURRENT | 0x0073 | ASCII |  | RO | r_current
74 | L3_CURRENT | 0x0075 | U16 |  | RO | t_current
75 | AC_POWER | 0x0076 | U16 |  | RO | ac_power
76 | Inverter – Inverter type | 0x0077 | U16 |  | RO
77 | POWER_FACTOR | 0x0078 | ASCII |  | RO | power_factor
78 | FREQUENCY | 0x0079 | ASCII |  | RO | frequency
79 | POWER_FACTOR | 0x007A | ASCII |  | RO | power_factor
80 | FREQUENCY | 0x007B | ASCII |  | RO | frequency
81 | Inverter – States (Byte 0) – Global state | 0x007C | U16 |  | RO
82 | Inverter – States (Byte 1) – Inverter state | 0x007D | U16 |  | RO
83 | Inverter – States (Byte 2) – DC/DC Channel 1 state | 0x007E | U16 |  | RO
84 | Inverter – States (Byte 3) – DC/DC Channel 2 state | 0x007F | U16 |  | RO
85 | Display Board – Presence – Indicates status of board toinverter | 0x0081 | U16 |  | RO
86 | DAILY_ENERGY | 0x0084 | U16 |  | RO | daily_energy
87 | CUMULATIVE_ENERGY | 0x0086 | U16 |  | RO | cumulative_energy
88 | Inverter – Partial Energy | 0x0088 | U16 |  | RO
89 | Inverter – Week Energy | 0x008A | U16 |  | RO
90 | Inverter – Monthly Energy | 0x008C | U16 |  | RO
91 | Inverter – Yearly Energy | 0x008E | U16 |  | RO
92 | Inverter – Grid Voltage | 0x0090 | U16 |  | RO
93 | Inverter – Grid Current | 0x0092 | U16 |  | RO
94 | REACTIVE_POWER | 0x0094 | U16 |  | RO | reactive_power
95 | Inverter – Frequency | 0x0096 | U16 |  | RO
96 | Inverter – Input 1 Power | 0x0098 | U16 |  | RO | mppt1_power
97 | Inverter – Input 1 Voltage | 0x009A | U16 |  | RO | mppt1_voltage
98 | Inverter – Input 1 Current | 0x009C | U16 |  | RO | mppt1_current
99 | Inverter – Input 2 Power | 0x009E | U16 |  | RO | mppt2_power
100 | Inverter – Input 2 Voltage | 0x00A0 | U16 |  | RO | mppt2_voltage
101 | Inverter – Input 2 Current | 0x00A2 | U16 |  | RO | mppt2_current
102 | TEMPERATURE | 0x00A4 | U16 |  | RO | temperature
103 | Inverter – Booster Temperature | 0x00A6 | U16 |  | RO
104 | Inverter – Isolation Resistance | 0x00A8 | U16 |  | RO
105 | Inverter – Wind Generator Frequency | 0x00AA | U16 |  | RO
106 | Inverter – Cos(φ) | 0x00AC | U16 |  | RO
107 | Inverter – Presence – Indicates status of board to inverter | 0x00AE | U16 |  | RO
108 | Set transient options | 0x00C6 | U16 |  | RO
109 | Dynamic Mode – Reactive Powermanagement by fixed PF | 0x00C8 | U16 |  | RO
110 | Permanent Mode – ReactivePower management by fixed PF | 0x00CA | U16 |  | RO
111 | Permanent Mode – Reset PF to 1 | 0x00CD | U16 |  | RO
112 | Permanent Mode – Reactive | 0x00E3 | U16 |  | RO
113 | Auxiliary Boards – Start register | 0x00FA | U16 |  | RO
114 | Auxiliary Board – Map size | 0x00FB | U16 |  | RO
115 | Communication Board – Part number (PN0) | 0x011A | ASCII |  | WO
116 | Communication Board – Part number (PN1) | 0x011B | ASCII |  | RO
117 | Communication Board – Part number (PN2) | 0x011C | ASCII |  | RO
118 | Communication Board – Part number (PN3) | 0x011D | ASCII |  | RO
119 | Communication Board – Part number (PN4) | 0x011E | ASCII |  | RO
120 | Communication Board – Part number (PN5) | 0x011F | ASCII |  | RO
121 | Communication Board – Week production – High byte | 0x0120 | ASCII |  | RO
122 | Communication Board – Week production – Low byte | 0x0121 | ASCII |  | RO
123 | Communication Board – Year production – High byte | 0x0122 | ASCII |  | RO
124 | Communication Board – Year production – Low byte | 0x0123 | ASCII |  | RO
125 | Transient options configurable | 0x012B | U16 |  | RO
126 | Heartbeat counter | 0x012C | U16 |  | RO
127 | REACTIVE_POWER | 0x012D | U16 |  | RO | reactive_power
128 | Fuse Control Board – Part number (PN4) | 0x012E | U16 |  | RO
129 | Inverter – Grid Voltage | 0x012F | U16 |  | RO
130 | Fuse Control Board – Week production – High byte | 0x0130 | U16 |  | RO
131 | Fuse Control Board – Year production – High byte | 0x0132 | U16 |  | RO
132 | Inverter – Grid Current | 0x0133 | U16 |  | RO
133 | Communication Board – States (Byte 4) | 0x0134 | U16 |  | RO
134 | Communication Board – States (Byte 5) | 0x0135 | U16 |  | RO
135 | Fuse Control Board – States (Byte 0) | 0x0136 | U16 |  | RO
136 | Fuse Control Board – States (Byte 1) | 0x0137 | U16 |  | RO
137 | Fuse Control Board – States (Byte 2) | 0x0138 | U16 |  | RO
138 | Fuse Control Board – States (Byte 3) | 0x0139 | U16 |  | RO
139 | Fuse Control Board – States (Byte 4) | 0x013A | U16 |  | RO
140 | Communication Board – PT100 | 0x013B | U16 |  | RO
141 | Communication Board – PT1000 | 0x013D | U16 |  | RO
142 | Communication Board – Analog Input 1 | 0x013F | U16 |  | RO
143 | Communication Board – Analog Input 2 | 0x0141 | U16 |  | RO
144 | Communication Board – NTC | 0x0143 | U16 |  | RO
145 | Fuse Control Board – Voltage 1A | 0x0145 | U16 |  | RO
146 | Fuse Control Board – Voltage 1B | 0x0147 | U16 |  | RO
147 | Fuse Control Board – Voltage 1C | 0x0149 | U16 |  | RO
148 | Fuse Control Board – Voltage 1D | 0x014B | U16 |  | RO
149 | Fuse Control Board – Voltage 1E | 0x014D | U16 |  | RO
150 | Fuse Control Board – Voltage 2A | 0x014F | U16 |  | RO
151 | Fuse Control Board – Voltage 2B | 0x0151 | U16 |  | RO
152 | Fuse Control Board – Voltage 2C | 0x0153 | U16 |  | RO
153 | Fuse Control Board – Voltage 2D | 0x0155 | U16 |  | RO
154 | Fuse Control Board – Voltage 2E | 0x0157 | U16 |  | RO
155 | Fuse Control Board – Voltage Ch1 | 0x0159 | U16 |  | RO
156 | Fuse Control Board – Voltage Ch2 | 0x015B | U16 |  | RO
157 | Fuse Control Board – Current 1A | 0x015D | U16 |  | RO
158 | Fuse Control Board – Current 1B | 0x015F | U16 |  | RO
159 | Fuse Control Board – Current 1C | 0x0161 | U16 |  | RO
160 | Fuse Control Board – Current 1D | 0x0163 | U16 |  | RO
161 | Fuse Control Board – Current 1E | 0x0165 | U16 |  | RO
162 | Fuse Control Board – Current 2A | 0x0167 | U16 |  | RO
163 | Fuse Control Board – Current 2B | 0x0169 | U16 |  | RO
164 | Fuse Control Board – Current 2C | 0x016B | U16 |  | RO
165 | Fuse Control Board – Current 2D | 0x016D | U16 |  | RO
166 | Fuse Control Board – Current 2E | 0x016F | U16 |  | RO
167 | Fuse Control Board – States (Byte 5) | 0x0171 | U16 |  | RO
168 | Set unit of registers 0507, 0508,0511 and 0512 (% or ‰). | 0x01F5 | U16 |  | RO
169 | Set active mode (permanent ordynamic) | 0x01F6 | U16 |  | RO
170 | Set transient options | 0x01F9 | U16 |  | RO
171 | Set reactive power control mode(Q fixed or PF fixed) | 0x01FA | U16 |  | RO
172 | Dynamic Mode – Reactive Powermanagement by fixed PF | 0x01FD | U16 |  | RO
173 | Reset Active Power management | 0x0203 | U16 |  | RO
174 | Reset Reactive Powermanagement | 0x0204 | U16 |  | RO
175 | Registers Map – Type | 0x0E42 | ASCII |  | RO
176 | Registers Map – Inverter family supported | 0x0E43 | ASCII |  | RO
177 | Registers Map – Major Version | 0x0E44 | ASCII |  | RO
178 | Registers Map – Minor Version | 0x0E45 | ASCII |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Permanent Mode – Reactive | 0x01FF | U16 |  | RO |  | Power management; set fixed Qby percentage of Nominal Power(P ) in 1% stepsNOM
2 | Permanent Mode – ReactivePower management by fixed PF | 0x0201 | U16 |  | RO
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | L3_VOLTAGE | 0x000E | U16 |  | RO | t_voltage | Sensor Test + Meas.Riso
2 | Forbidden State | 0x0028 | U16 |  | RO
3 | Remote Off | 0x0032 | U16 |  | RO
4 | Arc fault | 0x0033 | U16 |  | RO
5 | L1_VOLTAGE | 0x006E | ASCII |  | WO | r_voltage | Inverter – Part number (PN0)
6 | L1_VOLTAGE | 0x006F | ASCII |  | RO | r_voltage | Inverter – Part number (PN1)
7 | Remote on/off | 0x00B4 | U16 |  | RO
8 | Reset by-hand | 0x00B5 | U16 |  | RO

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | ABB-PV
용량 | -
MPPT | 4 (PDF max 4개)
String | 8 (2/MPPT)
H01 매칭 | 22/27
DER 매칭 | 33/33
총 레지스터 | 222
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 34
MONITORING | 178
STATUS | 2
ALARM | 8
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | HANDLER | O | - | -
13 | cumulative_energy | PDF | O | 0x0086 | CUMULATIVE_ENERGY
14 | cumulative_energy_low | PDF | - | - | -
15 | status | PDF | X | - | -
16 | alarm1 | PDF | O | 0x0033 | Arc fault
17 | alarm2 | PDF | - | - | -
18 | alarm3 | PDF | - | - | -
19 | mppt1_voltage | PDF | O | 0x009A | Inverter – Input 1 Voltage
20 | mppt1_current | PDF | O | 0x009C | Inverter – Input 1 Current
21 | mppt2_voltage | PDF | O | 0x00A0 | Inverter – Input 2 Voltage
22 | mppt2_current | PDF | O | 0x00A2 | Inverter – Input 2 Current
23 | mppt3_voltage | PDF | X | - | -
24 | mppt3_current | PDF | X | - | -
25 | mppt4_voltage | PDF | X | - | -
26 | mppt4_current | PDF | X | - | -
27 | string1_current | HANDLER | O | 0x009C | Inverter – Input 1 Current
28 | string2_current | HANDLER | O | 0x00A2 | Inverter – Input 2 Current
29 | string3_current | HANDLER | O | - | -
30 | string4_current | HANDLER | O | - | -