## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | CL-Series-Modbus-Interface-Guide
프로토콜 버전
설비 타입 | inverter
MPPT | 5
String | 10
String 모니터링 | Yes
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | CL-Series-Modbus-Interface-Guide_990-91443.pdf
추출 일시 | 2026-04-03 16:28
H01 매칭 | 36/37
DER 매칭 | 33/33
추출 레지스터 | 170
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | High transient DC bus voltage | 0x0013 | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically.If the problem persists, contact technical support.
2 | High DC bus voltage | 0x0014 | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically.If the problem persists, contact technical support.
3 | Module temperature is toohigh. | 0x0024 | 03 | U16 |  | RO | temperature | Verify that the DC input power is not greater than the DC:AC ratio of1.5. If it is, then reduce DC input power.Check whether the inverter is directly placed under the sun andintense sun exposure is causing the inverter’s module temperature torise. Install a proper shade to shield the inverter from direct sunlight.If the problem persists, contact technical support.
4 | Inverter insulation resistanceevent (ISO-flt) | 0x0027 | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically. Test for insulationdamages in the wiring.If the problem persists, contact technical support.
5 | PV configuration mode set onthe HMI does not match thedesign. | 0x002F | 03 | U16 |  | RO |  | Disconnect the inverter from all power sources.See the CL 30, CL 33, CL 50 Owner's Guide (document number: 990-91392) for more information under PV Array Connection to reconnectthe PV strings and reselect PV configuration mode.
6 | Phase-S current samplingchannel event | 0x0031 | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically.If the problem persists, contact technical support.
7 | Inverter insulation resistanceredundancy event is detected. | 0x0037 | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically.If the problem persists, contact technical support.
8 | Solar irradiation is notsufficient for inverter operation | 0x004B | 03 | U16 |  | RO |  | Wait for sufficient sunlight.If this event recurs when irradiation is sufficient, check the PV systemdesign and adjust the connection of PV inputs.
9 | Serial Number | 0x137D | 03 | U16 |  | RO |  | Data type :UTF-8Example: A912071368
10 | DEVICE_MODEL | 0x1387 | 03 | U16 |  | RO |  | Device type code ¦ Device code for CL 30 = 0x2C1BDevice code for CL 33 = 0x2C17Device code for CL 50 = 0x2C18
11 | Nominal activepower | 0x1388 | 03 | U16 | kW 0.1 | RO
12 | Output type | 0x1389 | 03 | U16 |  | RO
13 | Daily poweryields | 0x138A | 03 | U16 | kWh 0.1 | RO
14 | Total runningtime | 0x138D | 03 | U32 |  | RO
15 | Power limitation switch | 0x138E | 03 | U16 |  | RO
16 | Internaltemperature | 0x138F | 03 | S16 | ℃ 0.1 | RO
17 | Total apparentpower | 0x1390 | 03 | U32 | VA | RO
18 | Event/Alarmcode | 0x13B4 | 03 | U16 |  | RO
19 | Nominal reactivepower | 0x13B8 | 03 | U16 |  | RO
20 | Array insulationresistance | 0x13CE | 03 | U16 |  | RO
21 | Daily runningtime | 0x13F8 | 03 | U16 |  | RO
22 | MPPT 4 voltage | 0x13FA | 03 | U16 | V 0.1 | RO |  | Valid for inverters: CL 50
23 | Monthly powerYields | 0x1407 | 03 | U32 | kWh 0.1 | RO
24 | Bus voltage | 0x141A | 03 | U16 | V 0.1 | RO
25 | FREQUENCY | 0x141B | 03 | U16 | Hz 0.01 | RO |  | Grid frequency ¦ (Display accuracy increased to 0.01Hz)
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Phase-R current samplingchannel event | 0x0030 | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically.If the problem persists, contact technical support.
2 | AFD module abnormal | 0x0057 | 03 | U16 |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
3 | AFD module Disabled | 0x0059 | 03 | U16 |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
4 | Event/Alarmtime: Year | 0x13AE | 03 | U16 |  | RO
5 | PID work state | 0x141D | 03 | U16 |  | RO | inverter_status
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Average grid over-voltage (10minutes) | 0x000E | 03 | U16 |  | RO | t_voltage | This condition occurs when grid voltage exceeds the inverter’spermissible operating limit for an average of 10 minutes. Contact theutility company for suggestions.The inverter can recover automatically. Wait for a few minutes for theinverter to recover but if the event persists, contact technical support.
2 | Phase-T current samplingchannel event | 0x0032 | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically.If the problem persists, contact technical support.
3 | Main DSP data comparisonevent is detected. | 0x003C | 03 | U16 |  | RO |  | Wait for the inverter to recover automatically.If the problem persists, contact technical support.
4 | PV 2 power event warning | 0x004F | 03 | U16 |  | RO |  | Check the PV input terminals for loose connections. Tighten theconnections according to torque specifications found in the CL 30, CL33, CL 50 Owner's Guide (document number: 990-91392) for moreinformation.If the problem persists, contact technical support.
5 | String 1 reverse connectionevent | 0x01C0 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
6 | String 2 reverse connectionevent | 0x01C1 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
7 | String 3 reverse connectionevent | 0x01C2 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
8 | String 4 reverse connectionevent | 0x01C3 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
9 | String 5 reverse connectionevent | 0x01C4 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
10 | String 6 reverse connectionevent | 0x01C5 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
11 | String 7 reverse connectionevent | 0x01C6 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
12 | String 8 reverse connectionevent | 0x01C7 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
13 | String 9 reverse connectionevent | 0x01C8 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
14 | String 10 reverse connectionevent | 0x01C9 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
15 | String 1 reverse connectionalarm | 0x0214 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
16 | String 2 reverse connectionalarm | 0x0215 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
17 | String 3 reverse connectionalarm | 0x0216 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
18 | String 4 reverse connectionalarm | 0x0217 | 03 | STRINGING |  | RO |  | Refer Conext CL30/33/50 Owner’s Guide (document number: 975-xxxx-xx-xx for more information.If the problem persists, contact technical support
19 | String 5 reverse connectionalarm | 0x0218 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
20 | String 6 reverse connectionalarm | 0x0219 | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
21 | String 7 reverse connectionalarm | 0x021A | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
22 | String 8 reverse connectionalarm | 0x021B | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
23 | String 9 reverse connectionalarm | 0x021C | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
24 | String 10 reverse connectionalarm | 0x021D | 03 | STRINGING |  | RO |  | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
25 | String 8 abnormal alarm | 0x022B | 03 | STRINGING |  | RO | r_voltage | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
26 | String 9 abnormal alarm | 0x022C | 03 | STRINGING |  | RO | r_voltage | Refer to the CL 30, CL 33, CL 50 Owner's Guide (document number:990-91392) for more information.If the problem persists, contact technical support.
27 | String x output current anomaly | 0x0244 | 03 | STRINGING |  | RO
28 | Event/Alarmtime: Month | 0x13AF | 03 | U16 |  | RO
29 | Event/Alarmtime: Day | 0x13B0 | 03 | U16 |  | RO
30 | Event/Alarmtime: Hour | 0x13B1 | 03 | U16 |  | RO
31 | Event/Alarmtime: Minute | 0x13B2 | 03 | U16 |  | RO
32 | Event/Alarmtime: Second | 0x13B3 | 03 | U16 |  | RO
33 | Alarm run | 0x9100 | 03 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 36/37
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x1398 | PV_POWER | U32 | W
13 | cumulative_energy | PDF | O | 0x138B | CUMULATIVE_ENERGY | U32 | kWh |  | kWh→Wh (*1000)
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x141D | PID work state | U16 |  |  | 4608=Initial Standby, 4864=Key Stop, 5120=Standby, 5376=EmergencyStop, 5632=Starting, 21760=Event... (+4)
16 | alarm1 | PDF | O | 0x13AF | Event/Alarmtime: Month | U16 |  |  | 0=Great Britain, 1=Germany, 2=France, 3=Italy, 4=Spain, 5=Austria... (+22)
17 | alarm2 | PDF | O | 0x13B0 | Event/Alarmtime: Day | U16
18 | alarm3 | PDF | O | 0x13B1 | Event/Alarmtime: Hour | U16
19 | mppt1_voltage | PDF | O | 0x1392 | MPPT 1 voltage | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x1393 | MPPT 1 current | U16 | A | 0.1
21 | mppt2_voltage | PDF | O | 0x1394 | MPPT 2 voltage | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x1395 | MPPT 2 current | U16 | A | 0.1
23 | mppt3_voltage | PDF | O | 0x1396 | MPPT 3 voltage | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x1397 | MPPT 3 current | U16 | A | 0.1
25 | mppt4_voltage | PDF | X | - | -
26 | mppt4_current | PDF | O | 0x13FB | MPPT 4 current | U16 | A | 0.1
27 | mppt5_voltage | PDF | O | 0x13FC | MPPT 5 voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x13FD | MPPT 5 current | U16 | A | 0.1
29 | string1_current | PDF | O | 0x1B64 | String 1 current | U16 | A | 0.01
30 | string2_current | PDF | O | 0x1B65 | String 2 current | U16 | A | 0.01
31 | string3_current | PDF | O | 0x1B66 | String 3 current | U16 | A | 0.01
32 | string4_current | PDF | O | 0x1B67 | String 4 current | U16 | A | 0.01
33 | string5_current | PDF | O | 0x1B68 | String 5 current | U16 | A | 0.01
34 | string6_current | PDF | O | 0x1B69 | String 6 current | U16 | A | 0.01
35 | string7_current | PDF | O | 0x1B6A | String 7 current | U16 | A | 0.01
36 | string8_current | PDF | O | 0x1B6B | String 8 current | U16 | A | 0.01
37 | string9_current | PDF | O | 0x1B6C | String 9 current | U16 | A | 0.01
38 | string10_current | PDF | O | 0x1B6D | String 10 current | U16 | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 5ch / String 10ch
MPPT 채널 수 | 5
String 채널 수 | 10
String 모니터링 | Yes
MPPT 채널 H01 매칭 (10개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x1392 | MPPT 1 voltage | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x1393 | MPPT 1 current | U16 | A | 0.1
3 | mppt2_voltage | PDF | O | 0x1394 | MPPT 2 voltage | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x1395 | MPPT 2 current | U16 | A | 0.1
5 | mppt3_voltage | PDF | O | 0x1396 | MPPT 3 voltage | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x1397 | MPPT 3 current | U16 | A | 0.1
7 | mppt4_voltage | PDF | X | - | -
8 | mppt4_current | PDF | O | 0x13FB | MPPT 4 current | U16 | A | 0.1
9 | mppt5_voltage | PDF | O | 0x13FC | MPPT 5 voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x13FD | MPPT 5 current | U16 | A | 0.1
String 채널 H01 매칭 (10개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x1B64 | String 1 current | U16 | A | 0.01
2 | string2_current | PDF | O | 0x1B65 | String 2 current | U16 | A | 0.01
3 | string3_current | PDF | O | 0x1B66 | String 3 current | U16 | A | 0.01
4 | string4_current | PDF | O | 0x1B67 | String 4 current | U16 | A | 0.01
5 | string5_current | PDF | O | 0x1B68 | String 5 current | U16 | A | 0.01
6 | string6_current | PDF | O | 0x1B69 | String 6 current | U16 | A | 0.01
7 | string7_current | PDF | O | 0x1B6A | String 7 current | U16 | A | 0.01
8 | string8_current | PDF | O | 0x1B6B | String 8 current | U16 | A | 0.01
9 | string9_current | PDF | O | 0x1B6C | String 9 current | U16 | A | 0.01
10 | string10_current | PDF | O | 0x1B6D | String 10 current | U16 | A | 0.01
MONITORING 전체 (95개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | IllegalFunction | 0x0001 | 03 | U16 |  | RO
2 | IllegalAddress | 0x0002 | 03 | U16 |  | RO
3 | Illegal DataValue | 0x0003 | 03 | U16 |  | RO
4 | SlaveDeviceError | 0x0004 | 03 | U16 |  | RO
5 | The AC output currentexceeds the inverter’sprotection limit. | 0x0006 | 03 | U16 |  | RO
6 | Transient AC over current | 0x0007 | 03 | U16 |  | RO
7 | GR L_ | 0x000A | 03 | U16 |  | RO
8 | The DC component of the ACcurrent exceeds the inverter’slimit. | 0x000B | 03 | U16 |  | RO
9 | Residual current leakagedetected is high. | 0x000C | 03 | U16 |  | RO | r_voltage
10 | Grid overvoltage | 0x000F | 03 | U16 |  | RO | frequency
11 | Grid voltage imbalance | 0x0011 | 03 | U16 |  | RO
12 | PV input over current | 0x0015 | 03 | U16 |  | RO
13 | PV configuration mode haschanged during normaloperation. | 0x0017 | 03 | U16 |  | RO
14 | Voltage imbalance at neutralpoint | 0x0018 | 03 | U16 |  | RO
15 | Transient unbalance ofvoltage neutral point | 0x0019 | 03 | U16 |  | RO
16 | Clamp capacitance over-voltage event is detected. | 0x001E | 03 | U16 |  | RO
17 | Clamp capacitance under-voltage event is detected. | 0x001F | 03 | U16 |  | RO | daily_energy
18 | Clamp capacitance imbalanceevent is detected. | 0x0020 | 03 | U16 |  | RO | temperature
19 | Clamp capacitance pre-charge ground fault isdetected | 0x0021 | 03 | U16 |  | RO
20 | Internal ambient temperatureis too high. | 0x0025 | 03 | U16 |  | RO | frequency
21 | Line tie relay contacts havewelded or are open. | 0x0026 | 03 | U16 |  | RO | r_voltage
22 | AC (or DC) over-current or DCover- voltage event isdetected. | 0x0028 | 03 | U16 |  | RO
23 | Current leakage samplingchannel event | 0x0029 | 03 | U16 |  | RO
24 | AC current imbalance | 0x002A | 03 | U16 |  | RO | s_voltage
25 | The ambient temperature fallsbelow - 25 °C (-13 °F) | 0x002B | 03 | U16 |  | RO | s_current
26 | DC/AC inversion circuit event | 0x002C | 03 | U16 |  | RO
27 | Grid voltage redundancyevent is detected. | 0x0035 | 03 | U16 |  | RO
28 | Grid frequency redundancyevent is detected. | 0x0036 | 03 | U16 |  | RO
29 | Inverter leakage currentredundancy event is detected. | 0x0038 | 03 | STRINGING |  | RO
30 | Main DSP communicationredundancy event is detected. | 0x003B | 03 | U16 |  | RO
31 | JP 50Hz | 0x0046 | 03 | U16 |  | RO
32 | JP 60Hz | 0x0047 | 03 | U16 |  | RO
33 | DC side SPD event | 0x0048 | 03 | U16 |  | RO
34 | Communication event | 0x004A | 03 | U16 |  | RO
35 | PV overload condition | 0x004C | 03 | U16 |  | RO
36 | PV 1 power event warning | 0x004E | 03 | U16 |  | RO
37 | PV 3 power event warning | 0x0050 | 03 | U16 |  | RO | pv_power
38 | PV 4 power event warning | 0x0051 | 03 | U16 |  | RO
39 | Self test did not pass | 0x0069 | 03 | U16 |  | RO
40 | Grounding cable event | 0x006A | 03 | U16 |  | RO
41 | Electric arc event | 0x0088 | 03 | U16 |  | RO
42 | PV5 abnormal | 0x00DC | 03 | U16 |  | RO
43 | Device anomaly. | 0x0130 | 03 | U16 |  | RO
44 | Device anomaly. | 0x0150 | 03 | U16 |  | RO
45 | Device anomaly. | 0x0180 | 03 | U16 |  | RO
46 | String 1 abnormal alarm | 0x0224 | 03 | STRINGING |  | RO | r_voltage
47 | String 2 abnormal alarm | 0x0225 | 03 | STRINGING |  | RO | r_voltage
48 | String 3 abnormal alarm | 0x0226 | 03 | STRINGING |  | RO | mppt1_voltage
49 | String 4 abnormal alarm | 0x0227 | 03 | STRINGING |  | RO | mppt2_voltage
50 | String 5 abnormal alarm | 0x0228 | 03 | STRINGING |  | RO | mppt1_current
51 | String 6 abnormal alarm | 0x0229 | 03 | STRINGING |  | RO | mppt2_current
52 | String 7 abnormal alarm | 0x022A | 03 | STRINGING |  | RO | r_voltage
53 | String 10 abnormal alarm | 0x022D | 03 | STRINGING |  | RO | r_current
54 | String x reverse connection alarm | 0x0235 | 03 | STRINGING |  | RO
55 | Device anomaly | 0x0280 | 03 | U16 |  | RO
56 | Device anomaly | 0x0300 | 03 | U16 |  | RO
57 | Device anomaly | 0x0740 | 03 | U16 |  | RO
58 | CUMULATIVE_ENERGY | 0x138B | 03 | U32 | kWh | RO | cumulative_energy
59 | MPPT 1 voltage | 0x1392 | 03 | U16 | V 0.1 | RO | mppt1_voltage
60 | MPPT 1 current | 0x1393 | 03 | U16 | A 0.1 | RO | mppt1_current
61 | MPPT 2 voltage | 0x1394 | 03 | U16 | V 0.1 | RO | mppt2_voltage
62 | MPPT 2 current | 0x1395 | 03 | U16 | A 0.1 | RO | mppt2_current
63 | MPPT 3 voltage | 0x1396 | 03 | U16 | V 0.1 | RO | mppt3_voltage
64 | MPPT 3 current | 0x1397 | 03 | U16 | A 0.1 | RO | mppt3_current
65 | PV_POWER | 0x1398 | 03 | U32 | W | RO | pv_power
66 | A-B linevoltage/phase Avoltage | 0x139A | 03 | U16 | V 0.1 | RO | mppt1_voltage
67 | B-C lineVoltage/phase BVoltage | 0x139B | 03 | U16 | V 0.1 | RO | mppt1_current
68 | C-A lineVoltage/Phase Cvoltage | 0x139C | 03 | U16 | V 0.1 | RO | mppt2_voltage
69 | L1_CURRENT | 0x139D | 03 | U16 | A 0.1 | RO | r_current
70 | L2_CURRENT | 0x139E | 03 | U16 | A 0.1 | RO | s_current
71 | L3_CURRENT | 0x139F | 03 | U16 | A 0.1 | RO | t_current
72 | Total activepower | 0x13A6 | 03 | U32 | W | RO | s_current
73 | Total reactivepower | 0x13A8 | 03 | S32 |  | RO | ac_power
74 | Power factor | 0x13AA | 03 | S16 |  | RO | power_factor
75 | FREQUENCY | 0x13AB | 03 | U16 | Hz 0.1 | RO | frequency
76 | Reactive powerpercentage setting | 0x13AC | 03 | S16 |  | RO | power_factor
77 | Operating State | 0x13AD | 03 | U16 |  | RO | frequency
78 | MPPT 4 current | 0x13FB | 03 | U16 | A 0.1 | RO | mppt4_current
79 | MPPT 5 voltage | 0x13FC | 03 | U16 | V 0.1 | RO | mppt5_voltage
80 | MPPT 5 current | 0x13FD | 03 | U16 | A 0.1 | RO | mppt5_current
81 | CUMULATIVE_ENERGY | 0x1417 | 03 | U32 | kWh 0.1 | RO | cumulative_energy
82 | Negative voltageto the ground | 0x1419 | 03 | S16 | V 0.1 | RO
83 | PID alarm code | 0x141E | 03 | U16 |  | RO
84 | EmergencyStop | 0x1500 | 03 | U16 |  | RO
85 | String 1 current | 0x1B64 | 03 | U16 | A 0.01 | RO | string1_current
86 | String 2 current | 0x1B65 | 03 | U16 | A 0.01 | RO | string2_current
87 | String 3 current | 0x1B66 | 03 | U16 | A 0.01 | RO | string3_current
88 | String 4 current | 0x1B67 | 03 | U16 | A 0.01 | RO | string4_current
89 | String 5 current | 0x1B68 | 03 | U16 | A 0.01 | RO | string5_current
90 | String 6 current | 0x1B69 | 03 | U16 | A 0.01 | RO | string6_current
91 | String 7 current | 0x1B6A | 03 | U16 | A 0.01 | RO | string7_current
92 | String 8 current | 0x1B6B | 03 | U16 | A 0.01 | RO | string8_current
93 | String 9 current | 0x1B6C | 03 | U16 | A 0.01 | RO | string9_current
94 | String 10 current | 0x1B6D | 03 | U16 | A 0.01 | RO | string10_current
95 | Event | 0x5500 | 03 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)