## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Ekos
프로토콜 버전
설비 타입 | inverter
MPPT | 0
String | 2
String 모니터링 | Yes
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | Ekos_ModBus map-EK_20220209_통신테스트용.xlsx
추출 일시 | 2026-04-03 16:03
H01 매칭 | 20/20
DER 매칭 | 33/33
추출 레지스터 | 96
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | DEVICE_MODEL (PDF) | PDF |  | TEXT |  | RO |  | ModBus -EK 20220209 통신테스트용
2 | 시리얼번호 | 0x7539 |  | ASCII |  | RO
3 | 금일발전시간 (인버터 정상 가동시간) | 0x754E |  | U16 |  | RO
4 | 피상전력(종합) Reactive Power | 0x7561 |  | FLOAT32 | VA | RO
5 | 누적발전량 | 0x7569 |  | FLOAT32 | Wh | RO | cumulative_energy
6 | L1피상전력 | 0x757D |  | FLOAT32 | VA | RO
7 | L2피상전력 | 0x757F |  | FLOAT32 | VA | RO
8 | L3피상전력 | 0x7581 |  | FLOAT32 | VA | RO
9 | 방열판 온도 (인버터 내부온도) | 0x758B |  | FLOAT32 |  | RO
10 | 적산전력량 Total generation Energy | 0x758F |  | U32 | MWh | RO | cumulative_energy
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | 전체 상태 | 0x000F |  | U16 |  | RO
2 | 시스템동작상태 | 0x7549 |  | U16 |  | RO | inverter_status
3 | Inverter Status 상태 | 0x754B |  | U16 |  | RO | inverter_status
4 | PV Status Total(SUM) | 0x7593 |  | U16 |  | RO
5 | PV1 Status Total | 0x7594 |  | U16 |  | RO
6 | PV2 Status Total | 0x7595 |  | U16 |  | RO
7 | Inverter Status | 0x7596 |  | U16 |  | RO | inverter_status
8 | Converter Status | 0x7598 |  | U16 |  | RO
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | SPD 고장 | 0x000B |  | U16 |  | RO
2 | SW Fault Status Alarm 1 | 0x754C |  | U16 |  | RO
3 | HW Fault Status Alarm 2 | 0x754D |  | U16 |  | RO
4 | Grid Status Alarm3 | 0x7597 |  | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 20/20
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x7559 | 태양전지 전력 | FLOAT32 | W
13 | cumulative_energy | PDF | O | 0x7569 | 누적발전량 | FLOAT32 | Wh
14 | cumulative_energy_low | PDF | O | 0x7591 | 적산전력량 소수점 | U32 | Wh
15 | status | PDF | O | 0x7549 | 시스템동작상태 | U16
16 | alarm1 | PDF | O | 0x754C | SW Fault Status Alarm 1 | U16
17 | alarm2 | PDF | O | 0x754D | HW Fault Status Alarm 2 | U16
18 | alarm3 | PDF | O | 0x7597 | Grid Status Alarm3 | U16
19 | string1_current | PDF | O | 0x759B | 태양전지1 전류 String 1 Current | STRINGING | A
20 | string2_current | PDF | O | 0x75A1 | 태양전지2 전류 String 2 Current | STRINGING | A

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 0ch / String 2ch
MPPT 채널 수 | 0
String 채널 수 | 2
String 모니터링 | Yes
MPPT 채널 H01 매칭 (0개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
String 채널 H01 매칭 (2개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x759B | 태양전지1 전류 String 1 Current | STRINGING | A
2 | string2_current | PDF | O | 0x75A1 | 태양전지2 전류 String 2 Current | STRINGING | A
MONITORING 전체 (61개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | PV total(98)PV1(99)PV2(100) | 0x0000 |  | U16 |  | RO
2 | 컨버터 센서의 offset이상 | 0x0001 |  | U16 |  | RO
3 | 과전류 Trip | 0x0002 |  | U16 |  | RO
4 | 저주파수 | 0x0003 |  | U16 |  | RO
5 | 계통정전 | 0x0004 |  | U16 |  | RO
6 | 계통지락 | 0x0005 |  | U16 |  | RO
7 | 계통잔류전류 | 0x0006 |  | U16 |  | RO
8 | FLT INV OHR | 0x0007 |  | U16 |  | RO
9 | MC 이상 | 0x0008 |  | U16 |  | RO
10 | PWM 이상 | 0x000A |  | U16 |  | RO
11 | DC지락 | 0x000D |  | U16 |  | RO
12 | 비상 스위치ON | 0x000E |  | U16 |  | RO
13 | 인버터 버전 | 0x7541 |  | U16 |  | RO
14 | 인버터 용량 | 0x7542 |  | U16 | kW | RO
15 | 현재시각(Year) | 0x7543 |  | U16 |  | RO
16 | 현재시각(Month) | 0x7544 |  | U16 |  | RO
17 | 현재시각(Day) | 0x7545 |  | U16 |  | RO
18 | 현재시각(Hour) | 0x7546 |  | U16 |  | RO
19 | 현재시각(Minute) | 0x7547 |  | U16 |  | RO
20 | 현재시각(Second) | 0x7548 |  | U16 |  | RO
21 | 발전유무 | 0x754A |  | U16 |  | RO
22 | 금일발전시각시각 (Hour,Min) | 0x754F |  | U16 |  | RO
23 | 금일 최근 정지시각 (Hour, Min) | 0x7550 |  | U16 |  | RO
24 | 누적발전시간 | 0x7551 |  | U32 |  | RO
25 | 태양전지 전압 | 0x7553 |  | FLOAT32 | V | RO
26 | 인버터 DC전압 PV voltage | 0x7555 |  | FLOAT32 | V | RO
27 | 태양전지 전류 | 0x7557 |  | FLOAT32 | A | RO
28 | 태양전지 전력 | 0x7559 |  | FLOAT32 | W | RO | pv_power
29 | 전압(종합) | 0x755B |  | FLOAT32 | V | RO
30 | 전류(종합) | 0x755D |  | FLOAT32 | A | RO
31 | 유효전력(종합) Active Power | 0x755F |  | FLOAT32 | W | RO | ac_power
32 | 역률(종합) PF | 0x7563 |  | FLOAT32 |  | RO | power_factor
33 | 주파수 Frequency | 0x7565 |  | FLOAT32 | Hz | RO | frequency
34 | 일발전량 | 0x7567 |  | FLOAT32 | Wh | RO | daily_energy
35 | L1전압 | 0x756B |  | FLOAT32 | V | RO
36 | L2전압 | 0x756D |  | FLOAT32 | V | RO
37 | L1전류 | 0x7571 |  | FLOAT32 | A | RO
38 | L2전류 | 0x7573 |  | FLOAT32 | A | RO
39 | L3전류 | 0x7575 |  | FLOAT32 | A | RO
40 | L1유효전력 | 0x7577 |  | FLOAT32 | W | RO
41 | L2유효전력 | 0x7579 |  | FLOAT32 | W | RO
42 | L3유효전력 | 0x757B |  | FLOAT32 | W | RO
43 | L1역률 | 0x7583 |  | FLOAT32 |  | RO
44 | L2역률 | 0x7585 |  | FLOAT32 |  | RO
45 | L3역률 | 0x7587 |  | FLOAT32 |  | RO
46 | PV MPPPT온도 | 0x7589 |  | FLOAT32 |  | RO
47 | 적산전력량 소수점 | 0x7591 |  | U32 | Wh | RO | cumulative_energy_low
48 | 태양전지1 전압 String 1 Voltage | 0x7599 |  | STRINGING | V | RO | string1_voltage
49 | 태양전지1 전류 String 1 Current | 0x759B |  | STRINGING | A | RO | string1_current
50 | 태양전지1 전력 String 1 Power | 0x759D |  | STRINGING | W | RO
51 | 태양전지2 전압 String 2 Volrage | 0x759F |  | STRINGING | V | RO
52 | 태양전지2 전류 String 2 Current | 0x75A1 |  | STRINGING | A | RO | string2_current
53 | AD CH1(일사량 수평면) | 0x75A5 |  | U16 |  | RO
54 | AD CH2(일사량 경사면) | 0x75A6 |  | U16 |  | RO
55 | AD CH3(온도 외기) | 0x75A7 |  | U16 |  | RO
56 | AD CH4(온도 모듈) | 0x75A8 |  | U16 |  | RO
57 | CH1 Current(일체형 접속함 채널1 전류) | 0x75A9 |  | U16 | A 0.01 | RO
58 | CH2 Current(일체형 접속함 채널2 전류) | 0x75AA |  | U16 | A 0.01 | RO
59 | CH3 Current(일체형 접속함 채널3 전류) | 0x75AB |  | U16 | A 0.01 | RO
60 | CH4 Current(일체형 접속함 채널4 전류) | 0x75AC |  | U16 | A 0.01 | RO
61 | 인버터 용량 | 0xA411 |  | U16 | kW 1 | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)