## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | GoodWe
프로토콜 버전
설비 타입 | inverter
MPPT | 6
String | 20
String 모니터링 | Yes
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | GoodWe Modbus Protocol Customer Version.pdf
추출 일시 | 2026-04-03 16:03
H01 매칭 | 50/50
DER 매칭 | 33/33
추출 레지스터 | 156
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Device SerialNumber | 0x0200 |  | STRING | 1 | RO |  | ASCII code, 16 bytes
2 | Device Type | 0x0210 |  | STRING | 1 | RO |  | ASCII code, 16 bytes
3 | Inverter internaltemperature | 0x0235 |  | U16 | 10 | RO |  | Inverter internal temperature
4 | Inverter internaltemperature | 0x030F |  | U16 | 10 | RO |  | Inverter internal temperature
5 | FirmwareVersion | 0x0316 |  | U16 | 1 | RO |  | Firmware Version
6 | BUS Voltage | 0x031C |  | U16 | V 10 | RO |  | BUS Voltage
7 | NBUS Voltage | 0x031D |  | U16 | V 10 | RO |  | NBUS Voltage
8 | FirmwareVersion of ARM | 0x0354 |  | U16 |  | RO
9 | 1. Safety country of Inverter is set wrong.¦2. Grid voltageis not stable.¦3. AC (to grid) cable too small or too long | 0x20000 |  | U16 |  | RO
10 | 1. The Ground cable of panels is not connected or notconnected well.¦2. DC cable is broken.¦3. Neutral &ground cable are not connected well on AC side.¦4. TheISO failure happens on rainy days or early morning orsunset, when the humidity is comparatively heavy. | 0x40000 |  | U16 |  | RO
11 | 1. Cable between control board and power board (forDT) is not tight.¦2. Neutral & ground cable are notconnected well on AC side. ¦3. Control board problem. | 0x2000000 |  | U16 |  | RO
12 | 1. Safety country of Inverter is set wrong.¦2. Gridfrequency is not stable. | 0x20000000 |  | U16 |  | RO
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Battery ModeSwitch(Brazil) | 0x0133 |  | U16 | 1 | WO |  | 0-Off,1-On
2 | Shadow modeswitch | 0x0138 |  | U16 | 1 | RW |  | 0-Off,1-On
3 | Work Mode | 0x0234 |  | U16 | 1 | RO | inverter_status | 0:cWaitMode1:cNormalMode2:cFaultMode
4 | Work Mode | 0x030E |  | U16 | 1 | RO | inverter_status | 0:cWaitMode1:cNormalMode2:cFaultMode
5 | Function StatusBits | 0x0319 |  | U16 | A 1 | RO |  | Table 8-3
6 | High Byte of PVMode（SMTonly） | 0x0340 |  | U16 |  | RO
7 | Low Byte of PVMode（SMTonly） | 0x0341 |  | U16 |  | RO
8 | GPRS Burn-inMode | 0x0355 |  | U16 |  | RO
9 | PID&SPD Status | 0x036F |  | U16 | 1 | RO |  | Table 8-6
10 | Output controlstate | 0x0370 |  | U16 | 1 | RO |  | For Japanese models: 0-unprotected, 1-protected
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Error Message | 0x0220 |  | U32 | 1 | RO |  | Failure description for status‘failure’ Table8-2
2 | Error Message H | 0x0310 |  | U16 | 1 | RO |  | Failure description for status‘failure’ Table8-2
3 | Error Message L | 0x0311 |  | U16 | 1 | RO |  | Failure description for status‘failure’ Table8-2
4 | Warning Code | 0x0317 |  | U16 | 1 | RO |  | Warning Code
5 | 1. The device is abnormal | 0x8000000 |  | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 50/50
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x0233 | Pac L /Invertercurrent outputpower | U16 | W | 1
13 | cumulative_energy | PDF | O | 0x0222 | High Byte ofTotal FeedPower to grid/Total powergeneration | U16 | KWH | 10 | KWH→Wh (*1000)
14 | cumulative_energy_low | PDF | O | 0x0223 | Low Byte ofTotal FeedPower togrid/Total powergeneration | U16 | KWH | 10
15 | status | PDF | O | 0x0234 | Work Mode | U16 |  | 1 | 0=cWaitMode1, 2=cFaultMode
16 | alarm1 | PDF | O | 0x0220 | Error Message | U32 |  | 1 | 0=1. Try to resta, 1=1. Try to resta, 2=1. An occasiona, 3=The number of t, 4=Inverter suffer, 5=Please contact ... (+11)
17 | alarm2 | PDF | O | 0x0310 | Error Message H | U16 |  | 1 | 862=Istr4/PV String, 863=Istr5/PV String, 864=Istr6/PV String, 865=Istr7/PV String, 866=Istr8/PV String, 867=Istr9/PV String... (+18)
18 | alarm3 | PDF | O | 0x0311 | Error Message L | U16 |  | 1
19 | mppt1_voltage | PDF | O | 0x0226 | Vpv1 /PPV1input voltage | U16 | V | 10
20 | mppt1_current | PDF | O | 0x0228 | Ipv1 /PV1 inputcurrent | U16 | A | 10
21 | mppt2_voltage | PDF | O | 0x0227 | Vpv2 /PV2 inputvoltage | U16 | V | 10
22 | mppt2_current | PDF | O | 0x0229 | Ipv2 /PV2 inputcurrent | U16 | A | 10
23 | mppt3_voltage | PDF | O | 0x0357 | Vpv3 /PV3 inputvoltage | U16
24 | mppt3_current | PDF | O | 0x0359 | Ipv3 /PV3 inputcurrent | U16
25 | mppt4_voltage | PDF | O | 0x0358 | Vpv4 /PV4 inputvoltage | U16
26 | mppt4_current | PDF | O | 0x035A | Ipv4 /PV4 inputcurrent | U16
27 | mppt5_voltage | PDF | O | 0x0324 | Vpv5 /PV5 inputvoltage | U16
28 | mppt5_current | PDF | O | 0x0325 | Ipv5 /PV5 inputcurrent | U16
29 | mppt6_voltage | PDF | O | 0x0326 | Vpv6 /PV6 inputvoltage | U16
30 | mppt6_current | PDF | O | 0x0327 | Ipv6 /PV6 inputcurrent | U16
31 | string1_current | PDF | O | 0x035B | Istr1/PV String1Current | U16
32 | string2_current | PDF | O | 0x035C | Istr2/PV String2Current | U16
33 | string3_current | PDF | O | 0x035D | Istr3/PV String3Current | U16
34 | string4_current | PDF | O | 0x035E | Istr4/PV String4Current | U16 | A | 10
35 | string5_current | PDF | O | 0x035F | Istr5/PV String5Current | U16 | A | 10
36 | string6_current | PDF | O | 0x0360 | Istr6/PV String6Current | U16 | A | 10
37 | string7_current | PDF | O | 0x0361 | Istr7/PV String7Current | U16 | A | 10
38 | string8_current | PDF | O | 0x0362 | Istr8/PV String8Current | U16 | A | 10
39 | string9_current | PDF | O | 0x0363 | Istr9/PV String9Current | U16 | A | 10
40 | string10_current | PDF | O | 0x0364 | Istr10/PVString10 Current | U16 | A | 10
41 | string11_current | PDF | O | 0x0365 | Istr11/PVString11 Current | U16 | A | 10
42 | string12_current | PDF | O | 0x0366 | Istr12/PVString12 Current | U16 | A | 10
43 | string13_current | PDF | O | 0x0367 | Istr13/PVString13 Current | U16 | A | 10
44 | string14_current | PDF | O | 0x0368 | Istr14/PVString14 Current | U16 | A | 10
45 | string15_current | PDF | O | 0x0369 | Istr15/PVString15 Current | U16 | A | 10
46 | string16_current | PDF | O | 0x036A | Istr16/PVString16 Current | U16 | A | 10
47 | string17_current | PDF | O | 0x036B | Istr17/PVString17 Current | U16 | A | 10
48 | string18_current | PDF | O | 0x036C | Istr18/PVString18 Current | U16 | A | 10
49 | string19_current | PDF | O | 0x036D | Istr19/PVString19 Current | U16 | A | 10
50 | string20_current | PDF | O | 0x036E | Istr20/PVString20 Current | U16 | A | 10

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 6ch / String 20ch
MPPT 채널 수 | 6
String 채널 수 | 20
String 모니터링 | Yes
MPPT 채널 H01 매칭 (12개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x0226 | Vpv1 /PPV1input voltage | U16 | V | 10
2 | mppt1_current | PDF | O | 0x0228 | Ipv1 /PV1 inputcurrent | U16 | A | 10
3 | mppt2_voltage | PDF | O | 0x0227 | Vpv2 /PV2 inputvoltage | U16 | V | 10
4 | mppt2_current | PDF | O | 0x0229 | Ipv2 /PV2 inputcurrent | U16 | A | 10
5 | mppt3_voltage | PDF | O | 0x0357 | Vpv3 /PV3 inputvoltage | U16
6 | mppt3_current | PDF | O | 0x0359 | Ipv3 /PV3 inputcurrent | U16
7 | mppt4_voltage | PDF | O | 0x0358 | Vpv4 /PV4 inputvoltage | U16
8 | mppt4_current | PDF | O | 0x035A | Ipv4 /PV4 inputcurrent | U16
9 | mppt5_voltage | PDF | O | 0x0324 | Vpv5 /PV5 inputvoltage | U16
10 | mppt5_current | PDF | O | 0x0325 | Ipv5 /PV5 inputcurrent | U16
11 | mppt6_voltage | PDF | O | 0x0326 | Vpv6 /PV6 inputvoltage | U16
12 | mppt6_current | PDF | O | 0x0327 | Ipv6 /PV6 inputcurrent | U16
String 채널 H01 매칭 (20개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x035B | Istr1/PV String1Current | U16
2 | string2_current | PDF | O | 0x035C | Istr2/PV String2Current | U16
3 | string3_current | PDF | O | 0x035D | Istr3/PV String3Current | U16
4 | string4_current | PDF | O | 0x035E | Istr4/PV String4Current | U16 | A | 10
5 | string5_current | PDF | O | 0x035F | Istr5/PV String5Current | U16 | A | 10
6 | string6_current | PDF | O | 0x0360 | Istr6/PV String6Current | U16 | A | 10
7 | string7_current | PDF | O | 0x0361 | Istr7/PV String7Current | U16 | A | 10
8 | string8_current | PDF | O | 0x0362 | Istr8/PV String8Current | U16 | A | 10
9 | string9_current | PDF | O | 0x0363 | Istr9/PV String9Current | U16 | A | 10
10 | string10_current | PDF | O | 0x0364 | Istr10/PVString10 Current | U16 | A | 10
11 | string11_current | PDF | O | 0x0365 | Istr11/PVString11 Current | U16 | A | 10
12 | string12_current | PDF | O | 0x0366 | Istr12/PVString12 Current | U16 | A | 10
13 | string13_current | PDF | O | 0x0367 | Istr13/PVString13 Current | U16 | A | 10
14 | string14_current | PDF | O | 0x0368 | Istr14/PVString14 Current | U16 | A | 10
15 | string15_current | PDF | O | 0x0369 | Istr15/PVString15 Current | U16 | A | 10
16 | string16_current | PDF | O | 0x036A | Istr16/PVString16 Current | U16 | A | 10
17 | string17_current | PDF | O | 0x036B | Istr17/PVString17 Current | U16 | A | 10
18 | string18_current | PDF | O | 0x036C | Istr18/PVString18 Current | U16 | A | 10
19 | string19_current | PDF | O | 0x036D | Istr19/PVString19 Current | U16 | A | 10
20 | string20_current | PDF | O | 0x036E | Istr20/PVString20 Current | U16 | A | 10
MONITORING 전체 (114개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Power onvoltage | 0x0000 |  | U16 | V 10 | RW
2 | Lower limit ofgrid voltage | 0x0002 |  | U16 | V 10 | RW
3 | Upper limit ofgrid voltage | 0x0003 |  | U16 | V 10 | RW
4 | Lower limit ofgrid frequency | 0x0004 |  | U16 | Hz 100 | RW
5 | Upper limit ofgrid frequency | 0x0005 |  | U16 | Hz 100 | RW
6 | Bit3 | 0x0008 |  | U16 |  | RO
7 | Bit5 | 0x0020 |  | U16 |  | RO
8 | Bit6 | 0x0040 |  | U16 |  | RO
9 | Bit7 | 0x0080 |  | U16 |  | RO
10 | Active poweradjust | 0x0100 |  | U16 | 1 | RW
11 | PF reactivepower adjust | 0x0101 |  | U16 | 1 | RW
12 | Reactive poweradjust | 0x0102 |  | S32 | 1 | RW
13 | Max value ofreactive power | 0x0104 |  | U32 | 1 | RO
14 | Export PowerLimit AdjustRange | 0x0106 |  | S16 | 1 | WO
15 | Export powerlimitCommunicationOvertime set | 0x010B |  | U16 |  | RW
16 | Power On(Allowon grid self-test) | 0x0120 |  | U16 |  | WO
17 | Power Off(Notallow on gridself-test) | 0x0121 |  | U16 |  | WO
18 | AutomaticReactive powerAdjust | 0x0130 |  | U16 |  | WO
19 | AutomaticReactive powerAdjust ID | 0x0131 |  | U32 |  | WO
20 | Battery Voltageset(Brazil) | 0x0134 |  | U16 | V 10 | WO
21 | High Byte ofTotal FeedPower to grid/Total powergeneration | 0x0222 |  | U16 | KWH 10 | RO | cumulative_energy
22 | Low Byte ofTotal FeedPower togrid/Total powergeneration | 0x0223 |  | U16 | KWH 10 | RO | cumulative_energy_low
23 | High Byte ofTotal feedinghours/Hourlypowergeneration | 0x0224 |  | U16 | 1 | RO | cumulative_energy
24 | Low Byte ofTotal feedinghours/Hourlypowergeneration | 0x0225 |  | U16 | 1 | RO | cumulative_energy_low
25 | Vpv1 /PPV1input voltage | 0x0226 |  | U16 | V 10 | RO | mppt1_voltage
26 | Vpv2 /PV2 inputvoltage | 0x0227 |  | U16 | V 10 | RO | mppt2_voltage
27 | Ipv1 /PV1 inputcurrent | 0x0228 |  | U16 | A 10 | RO | mppt1_current
28 | Ipv2 /PV2 inputcurrent | 0x0229 |  | U16 | A 10 | RO | mppt2_current
29 | Vac1 /L1 Phasevoltage | 0x022A |  | U16 | V 10 | RO
30 | Vac2 /L2 Phasevoltage | 0x022B |  | U16 | V 10 | RO
31 | Vac3 /L3 Phasevoltage | 0x022C |  | U16 | V 10 | RO
32 | Iac1 /L1 Phasecurrent | 0x022D |  | U16 | A 10 | RO
33 | Iac2 /L2 Phasecurrent | 0x022E |  | U16 | A 10 | RO
34 | Iac3 /L3 Phasecurrent | 0x022F |  | U16 | A 10 | RO
35 | Fac1 /L1 Phasefrequency | 0x0230 |  | U16 | Hz 100 | RO
36 | Fac2 /L2 Phasefrequency | 0x0231 |  | U16 | Hz 100 | RO
37 | Fac3 /L3 Phasefrequency | 0x0232 |  | U16 | Hz 100 | RO
38 | Pac L /Invertercurrent outputpower | 0x0233 |  | U16 | W 1 | RO | pv_power
39 | E-Day /Dailypowergeneration | 0x0236 |  | U16 | KWH 10 | RO
40 | Vpv1 /PV1 inputvoltage | 0x0300 |  | U16 | V 10 | RO | mppt1_voltage
41 | Vpv2 /PV2 inputvoltage | 0x0301 |  | U16 | V 10 | RO | mppt2_voltage
42 | Ipv1 /PV1 inputcurrent | 0x0302 |  | U16 | A 10 | RO | mppt1_current
43 | Ipv2 /PV2 inputcurrent | 0x0303 |  | U16 | A 10 | RO | mppt2_current
44 | Vac1 /L1 Phasevoltage | 0x0304 |  | U16 | V 10 | RO
45 | Vac2 /L2 Phasevoltage | 0x0305 |  | U16 | V 10 | RO
46 | Vac3 /L3 Phasevoltage | 0x0306 |  | U16 | V 10 | RO
47 | Iac1 /L1 Phasecurrent | 0x0307 |  | U16 | A 10 | RO
48 | Iac2 /L2 Phasecurrent | 0x0308 |  | U16 | A 10 | RO
49 | Iac3 /L3 Phasecurrent | 0x0309 |  | U16 | A 10 | RO
50 | Fac1 /L1 Phasefrequency | 0x030A |  | U16 | Hz 100 | RO
51 | Fac2 /L2 Phasefrequency | 0x030B |  | U16 | Hz 100 | RO
52 | Fac3 /L3 Phasefrequency | 0x030C |  | U16 | Hz 100 | RO
53 | Pac L /Invertercurrent outputpower | 0x030D |  | U16 | W 1 | RO | pv_power
54 | High Byte ofTotal FeedPower togrid/Total powergeneration | 0x0312 |  | U16 | KWH 10 | RO | cumulative_energy
55 | Low Byte ofTotal FeedPower togrid/Total powergeneration | 0x0313 |  | U16 | KWH 10 | RO | cumulative_energy_low
56 | High Byte ofTotal feedinghours/Hourlypowergeneration | 0x0314 |  | U16 | 1 | RO | cumulative_energy
57 | Low Byte ofTotal feedinghours/Hourlypowergeneration | 0x0315 |  | U16 | 1 | RO | cumulative_energy_low
58 | RSVD | 0x0318 |  | U16 | V 10 | RO
59 | RSVD | 0x031A |  | U16 | V 10 | RO
60 | RSVD | 0x031B |  | U16 | V 10 | RO
61 | RSVD | 0x031E |  | U16 | Hz 100 | RO
62 | Safety Code | 0x031F |  | U16 | 1 | RO
63 | Feed Power togrid in today/Daily power | 0x0320 |  | U16 | KWH 10 | RO
64 | Vpv5 /PV5 inputvoltage | 0x0324 |  | U16 |  | RO | mppt5_voltage
65 | Ipv5 /PV5 inputcurrent | 0x0325 |  | U16 |  | RO | mppt5_current
66 | Vpv6 /PV6 inputvoltage | 0x0326 |  | U16 |  | RO | mppt6_voltage
67 | Ipv6 /PV6 inputcurrent | 0x0327 |  | U16 |  | RO | mppt6_current
68 | Year :Month | 0x033B |  | U16 |  | RO
69 | Date :Hour | 0x033C |  | U16 |  | RO
70 | Minute :Second | 0x033D |  | U16 |  | RO
71 | Manufacture ID | 0x033E |  | U16 |  | RO
72 | Wireless signalstrength | 0x033F |  | U16 |  | RO
73 | High Byte ofPower | 0x0352 |  | U16 |  | RO
74 | Low Byte ofPower | 0x0353 |  | U16 |  | RO
75 | Pac H /High Byteof Power | 0x0356 |  | U16 |  | RO | pv_power
76 | Vpv3 /PV3 inputvoltage | 0x0357 |  | U16 |  | RO | mppt3_voltage
77 | Vpv4 /PV4 inputvoltage | 0x0358 |  | U16 |  | RO | mppt4_voltage
78 | Ipv3 /PV3 inputcurrent | 0x0359 |  | U16 |  | RO | mppt3_current
79 | Ipv4 /PV4 inputcurrent | 0x035A |  | U16 |  | RO | mppt4_current
80 | Istr1/PV String1Current | 0x035B |  | U16 |  | RO | string1_current
81 | Istr2/PV String2Current | 0x035C |  | U16 |  | RO | string2_current
82 | Istr3/PV String3Current | 0x035D |  | U16 |  | RO | string3_current
83 | Istr4/PV String4Current | 0x035E |  | U16 | A 10 | RO | string4_current
84 | Istr5/PV String5Current | 0x035F |  | U16 | A 10 | RO | string5_current
85 | Istr6/PV String6Current | 0x0360 |  | U16 | A 10 | RO | string6_current
86 | Istr7/PV String7Current | 0x0361 |  | U16 | A 10 | RO | string7_current
87 | Istr8/PV String8Current | 0x0362 |  | U16 | A 10 | RO | string8_current
88 | Istr9/PV String9Current | 0x0363 |  | U16 | A 10 | RO | string9_current
89 | Istr10/PVString10 Current | 0x0364 |  | U16 | A 10 | RO | string10_current
90 | Istr11/PVString11 Current | 0x0365 |  | U16 | A 10 | RO | string11_current
91 | Istr12/PVString12 Current | 0x0366 |  | U16 | A 10 | RO | string12_current
92 | Istr13/PVString13 Current | 0x0367 |  | U16 | A 10 | RO | string13_current
93 | Istr14/PVString14 Current | 0x0368 |  | U16 | A 10 | RO | string14_current
94 | Istr15/PVString15 Current | 0x0369 |  | U16 | A 10 | RO | string15_current
95 | Istr16/PVString16 Current | 0x036A |  | U16 | A 10 | RO | string16_current
96 | Istr17/PVString17 Current | 0x036B |  | U16 | A 10 | RO | string17_current
97 | Istr18/PVString18 Current | 0x036C |  | U16 | A 10 | RO | string18_current
98 | Istr19/PVString19 Current | 0x036D |  | U16 | A 10 | RO | string19_current
99 | Istr20/PVString20 Current | 0x036E |  | U16 | A 10 | RO | string20_current
100 | Power Factor | 0x0376 |  | U16 | 1000 | RO | power_factor
101 | High Byte of ACreactive power | 0x037D |  | U16 | 1000 | RO
102 | Low Byte of ACreactive power | 0x037E |  | U16 | 1000 | RO
103 | Leak currentValue | 0x0380 |  | U16 | 1 | RO
104 | Bit10 | 0x0400 |  | U16 |  | RO
105 | Bit11 | 0x0800 |  | STRINGING |  | RO
106 | Bit12 | 0x1000 |  | U16 |  | RO
107 | Bit13 | 0x2000 |  | U16 |  | RO
108 | Bit14 | 0x4000 |  | U16 |  | RO
109 | Bit15 | 0x8000 |  | U16 |  | RO
110 | Bit16 | 0x10000 |  | U16 |  | RO
111 | Inverter detects a higher DC component in AC output. | 0x80000 |  | U16 |  | RO
112 | The cable inside for communication of LCD gets loosen. | 0x100000 |  | U16 |  | RO
113 | Some string current is too high. | 0x200000 |  | STRINGING |  | RO
114 | 1. PV string reverse connection | 0x400000 |  | STRINGING |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)