## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Huawei
프로토콜 버전
설비 타입 | inverter
MPPT | 8
String | 8
String 모니터링 | No (MPPT당 1 String)
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | Huawei_SUN2000MC_Modbus_Interface_Definitions.pdf
추출 일시 | 2026-04-03 16:03
H01 매칭 | 41/41
DER 매칭 | 33/33
추출 레지스터 | 1061
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Number of points | 0x0001 | 03 | U16 | A 1 | RO
2 | SERIAL_NUMBER | 0x0014 | 03 | U16 |  | RO |  | SN ¦ N/A
3 | FIRMWARE_VERSION | 0x001E | 03 | U16 |  | RO |  | Software version ¦ N/A
4 | Low Insulation Resistance | 0x080E | 03 | U16 |  | RO
5 | Model | 0x7530 |  | STRING |  | RO
6 | SERIAL_NUMBER | 0x753F |  | STRING |  | RO |  | SN
7 | FirmwareVersion | 0x7553 |  | STRING |  | RO
8 | Softwareversion | 0x7562 |  | STRING |  | RO
9 | Protocolversion[Modbus] | 0x7574 |  | U32 |  | RO
10 | Model ID | 0x7576 |  | U16 |  | RO
11 | NumberofMPPTs | 0x7578 |  | U16 | 1 | RO
12 | Ratedpower | 0x7579 |  | U32 | kW 1000 | RO
13 | ProductSoftwareVersionNumber | 0x759C |  | U16 |  | RO
14 | PowerGridStandardCodeProtocolVersion | 0x759D |  | U16 |  | RO
15 | [Third-partylabeling]SN | 0x75EF |  | STRING |  | RO
16 | [Third-partylabel]Manufacturermodel | 0x75F9 |  | U16 |  | RO
17 | MonitoringBoard SN | 0x7927 |  | STRING |  | RO
18 | Monitoringsoftwareversion | 0x7931 |  | STRING |  | RO
19 | DeviceSNfeaturecode | 0x7D0F |  | U16 |  | RO
20 | Internaltemperature | 0x7D57 |  | S16 | 10 | RO
21 | AlarmclearanceSN | 0x7D9B |  | U16 |  | RO
22 | Serialnumberofthelatestactivealarm. | 0x7DAC |  | U32 |  | RO
23 | LatestHistoricalAlarmSerialNumber | 0x7DAE |  | U32 |  | RO
24 | Totalbusvoltage | 0x7DB0 |  | S16 | V 10 | RO
25 | MPPT3DCTotalEnergyYield | 0x7DD8 |  | U32 | kWh 100 | RO
26 | Runningtimeofcapacitorbank | 0x88B8 |  | U32 | 10 | RO
27 | Internalfan1runningtime | 0x88BA |  | U32 | 10 | RO
28 | InternalTemperature1 | 0x88CD |  | S16 | 10 | RO
29 | InternalTemperature2 | 0x88CE |  | S16 | 10 | RO
30 | InternalTemperature3 | 0x88CF |  | S16 | 10 | RO
31 | InternalTemperature4 | 0x88D0 |  | S16 | 10 | RO
32 | InternalTemperature5 | 0x88D1 |  | S16 | 10 | RO
33 | InternalTemperature6 | 0x88D2 |  | S16 | 10 | RO
34 | Internaltemperature7 | 0x88D3 |  | S16 | 10 | RO
35 | Internaltemperature8 | 0x88D4 |  | S16 | 10 | RO
36 | Internaltemperature9 | 0x88D5 |  | S16 | 10 | RO
37 | Internaltemperature10 | 0x88D6 |  | S16 | 10 | RO
38 | Internaltemperature11 | 0x88D7 |  | S16 | 10 | RO
39 | Internaltemperature12 | 0x88D8 |  | S16 | 10 | RO
40 | Positivebusvoltage | 0x88E2 |  | S16 | V 10 | RO
41 | Negativebusvoltage | 0x88E3 |  | S16 | V 10 | RO
42 | BUSnegativevoltagetoground | 0x88E4 |  | S16 | V 10 | RO
43 | LicenseSN | 0x8949 |  | STRING | 1 | RO
44 | MeterModelCheckResult | 0x9112 |  | U16 |  | RO
45 | LayoutFileChangeSN | 0x915A |  | U16 | 1 | RO
46 | SERIAL_NUMBER | 0x9187 |  | STRING |  | RO |  | SN
47 | SERIAL_NUMBER | 0x9218 |  | STRING | 1 | RO |  | SN
48 | Softwareversion | 0x9267 |  | STRING |  | RO
49 | Replacethetargetmodel. | 0xA41C |  | U16 | 1 | RW
50 | Maximumapparentpower | 0xA425 |  | U32 | kVA 1000 | RW
51 | apparentpowerreference | 0xA429 |  | U32 | 1000 | RW
52 | ScienceandTechnologyJingkeProtocolVersion | 0xAC47 | 03 | U16 |  | RW
53 | Clear therunningtimeinformation. | 0xAFD3 | 03 | U16 |  | WO
54 | ESNvalidationcommand | 0xAFD7 | 03 | U16 | 1 | WO
55 | Metermodel | 0xB8C7 | 03 | U16 |  | RW
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | [Remotesignal]Runningstatus(monitoring) | 0x7D02 |  | U16 |  | RO
2 | [Remotesignal]Runningstatus(powerprocessing) | 0x7D03 |  | U32 | 1 | RO
3 | INVERTER_MODE | 0x7D59 |  | U16 |  | RO | inverter_status | DeviceStatus
4 | Built-inPIDrunningstatus | 0x7DBE |  | U16 |  | RO
5 | String 1accessstatus | 0x7E2C |  | STRINGING |  | RO
6 | String 2accessstatus | 0x7E2D |  | STRINGING |  | RO
7 | String 3accessstatus | 0x7E2E |  | STRINGING |  | RO
8 | String 4accessstatus | 0x7E2F |  | STRINGING |  | RO
9 | String 5accessstatus | 0x7E30 |  | STRINGING |  | RO
10 | Connectionstatus ofstring 6 | 0x7E31 |  | U16 |  | RO
11 | String 7accessstatus | 0x7E32 |  | STRINGING |  | RO
12 | String 8accessstatus | 0x7E33 |  | STRINGING |  | RO
13 | StentSystemStatus | 0x84D0 |  | U32 |  | RO
14 | Operatingmode | 0x84F4 |  | U16 |  | RO
15 | Supportaccessstatus | 0x84F6 |  | U32 | 1 | RO
16 | Workingmodemask | 0x84F8 |  | U32 | 1 | RO | inverter_status
17 | Support 1GeneralFaultStatus | 0x851B |  | U16 |  | RO
18 | Support 1user-definedfaultstatus | 0x851C |  | U16 | 1 | RO
19 | Support 2GeneralFaultStatus | 0x851D |  | U16 | 1 | RO
20 | Support 2CustomFaultStatus | 0x851E |  | U16 | 1 | RO
21 | Support 3GeneralFaultStatus | 0x851F |  | U16 | 1 | RO
22 | Support 3user-definedfaultstatus | 0x8520 |  | U16 | 1 | RO
23 | Support 4GeneralFaultStatus | 0x8521 |  | U16 | 1 | RO
24 | Support 4CustomFaultStatus | 0x8522 |  | U16 | 1 | RO
25 | Support 5GeneralFaultStatus | 0x8523 |  | U16 | 1 | RO
26 | Support 5CustomFaultStatus | 0x8524 |  | U16 | 1 | RO
27 | Support 6GeneralFaultStatus | 0x8525 |  | U16 | 1 | RO
28 | Support 6CustomFaultStatus | 0x8526 |  | U16 | 1 | RO
29 | Support 7GeneralFaultStatus | 0x8527 |  | U16 | 1 | RO
30 | Support 7CustomFaultStatus | 0x8528 |  | U16 | 1 | RO
31 | Support 8GeneralFaultStatus | 0x8529 |  | U16 | 1 | RO
32 | Support 8CustomFaultStatus | 0x852A |  | U16 | 1 | RO
33 | Support 9GeneralFaultStatus | 0x852B |  | U16 | 1 | RO
34 | Support 9CustomFaultStatus | 0x852C |  | U16 | 1 | RO
35 | Support10GeneralFaultStatus | 0x852D |  | U16 | 1 | RO
36 | Support10CustomFaultStatus | 0x852E |  | U16 | 1 | RO
37 | Support11GeneralFaultStatus | 0x852F |  | U16 | 1 | RO
38 | Support11CustomFaultStatus | 0x8530 |  | U16 | 1 | RO
39 | Support12GeneralFaultStatus | 0x8531 |  | U16 | 1 | RO
40 | Support12CustomFaultStatus | 0x8532 |  | U16 | 1 | RO
41 | Support13GeneralFaultStatus | 0x8533 |  | U16 | 1 | RO
42 | Support13CustomFaultStatus | 0x8534 |  | U16 | 1 | RO
43 | Support14GeneralFaultStatus | 0x8535 |  | U16 | 1 | RO
44 | Support14CustomFaultStatus | 0x8536 |  | U16 | 1 | RO
45 | Support15GeneralFaultStatus | 0x8537 |  | U16 | 1 | RO
46 | Support15CustomFaultStatus | 0x8538 |  | U16 | 1 | RO
47 | Support16GeneralFaultStatus | 0x8539 |  | U16 | 1 | RO
48 | Support16CustomFaultStatus | 0x853A |  | U16 | 1 | RO
49 | I-Vscanstatus | 0x8916 |  | U16 |  | RO
50 | [STA]WLANlistscanningstatus | 0x8921 |  | U16 |  | RO
51 | [NTP]LastNTPsynchronizationstatus. | 0x8928 |  | U16 | 1 | RO
52 | Deferredactivationstate | 0x892B |  | U16 |  | RO
53 | [4G]Trafficstatus | 0x8932 |  | U16 |  | RO
54 | [STA]Routerconnectionstatus | 0x8935 |  | U16 |  | RO
55 | [FE]Connectionstatus | 0x8936 |  | U16 | 1 | RO
56 | Smart I-V-V-Diagnosis(License)Status | 0x8942 |  | U16 | V | RO
57 | [Stringmonitoring]Licensestatus | 0x8995 |  | U16 |  | RO
58 | [4G]Modulestatus | 0x89B1 |  | U16 |  | RO
59 | [4G]PINcheckstatus | 0x89C2 |  | U16 |  | RO
60 | Activepoweradjustmentstatus | 0x89E4 |  | U16 |  | RO
61 | Reactivepoweradjustmentstatus | 0x89E8 |  | U16 |  | RO
62 | Upgradestatus ID. | 0x8CC1 |  | U16 |  | RO
63 | [Module1]Runningstatus ofthebattery | 0x9088 |  | U16 |  | RO
64 | MeterStatus | 0x90EC |  | U16 |  | RO
65 | Currentstatus ofthephysicallocation | 0x9156 |  | U16 |  | RO | inverter_status
66 | RelativePositioningStatus | 0x9158 |  | U16 |  | RO
67 | Disconnectedstatus | 0x915C |  | U16 |  | RO
68 | [DC-MBUS]Networkingstatus | 0x9182 |  | U16 |  | RO
69 | FastShutdownSelfTestStatus | 0x9185 |  | U16 |  | RO
70 | Runningstatus | 0x9186 |  | U16 |  | RO
71 | [Scheduleserver]Communicationstatus | 0x9263 |  | U16 |  | RO
72 | [Scheduleserver]Latestconnectionstatus | 0x9264 |  | U16 |  | RO
73 | UpgradeStatus | 0x9279 |  | U16 |  | RO
74 | Invertercomprehensivestatus | 0x928E |  | U16 |  | RO
75 | Inverterintegratedstatussupportflag | 0x928F |  | U16 | 1 | RO
76 | Q-Ucharacteristiccurvemode | 0x9C65 |  | U16 |  | RW
77 | Outputmode | 0xA411 |  | U16 |  | RW
78 | Of-fgridswitchovermode | 0xA43C |  | U16 |  | RW
79 | Off-gridmode | 0xA43D |  | U16 |  | RW
80 | PQmode | 0xA43E |  | U16 |  | RW
81 | Stringconnectionmode | 0xA441 |  | U16 |  | RW
82 | PowerQualityOptimizationMode | 0xA451 | 03 | U16 |  | RW
83 | Failureprotectionactivepowermode | 0xA45C | 03 | U16 |  | RW
84 | Failureprotectionreactivepowermode | 0xA45F | 03 | U16 |  | RW
85 | Gridfaultzerocurrentmode | 0xA47E | 03 | U16 |  | RW
86 | Built-inPIDmode | 0xA4C4 | 03 | U16 |  | RW
87 | Operatingmode | 0xA5A9 | 03 | U16 |  | RW
88 | [ManagementSystem]Portmode | 0xA85C | 03 | U16 |  | RW
89 | [STA]WirelessRoutingEncryptionMode | 0xA89C | 03 | U16 |  | RW
90 | Parallelcommunicationmode | 0xA961 | 03 | U16 |  | RW
91 | [4G]Networkmode | 0xA9A6 | 03 | U16 |  | RW | inverter_status
92 | [4G]APNmode | 0xA9A7 | 03 | U16 |  | RW
93 | Operatingmode | 0xABE1 | 03 | U16 |  | RW
94 | Operatingmode | 0xB79C | 03 | U16 |  | RW
95 | Securitymode | 0xB834 | 03 | U16 |  | RW
96 | Activepowercontrolmode | 0xB937 | 03 | U16 |  | RW
97 | Restrictionmode | 0xB93B | 03 | U16 |  | RW
98 | reactivepowercontrolmode | 0xB941 | 03 | U16 |  | RW
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Abnormal Grounding | 0x080D | 03 | U16 |  | RO
2 | Device Fault | 0x0810 | 03 | U16 |  | RO
3 | Faulty Power Collector[2] | 0x0813 | 03 | U16 |  | RO
4 | Battery abnormal | 0x0814 | 03 | U16 |  | RO
5 | Abnormal PV moduleconfiguration | 0x0820 | 03 | U16 |  | RO
6 | Optimizer fault[5] | 0x0821 | 03 | U16 |  | RO
7 | On-grid/Off-grid controllerabnormal[4] | 0x0822 | 03 | U16 |  | RO
8 | Built-in PID operationabnormal[6] | 0x0825 | 03 | U16 |  | RO
9 | External Fan Abnormal | 0x0826 | 03 | U16 |  | RO
10 | Internal Fan Abnormal | 0x0827 | 03 | U16 |  | RO
11 | DC Protection UnitAbnormal[8] | 0x0828 | 03 | U16 |  | RO
12 | [Remotesignal]Alarm 1 | 0x7D08 |  | U16 |  | RO
13 | [Remotesignal]Alarm 2 | 0x7D09 |  | U16 |  | RO
14 | [Remotesignal]Alarm 3 | 0x7D0A |  | U16 |  | RO
15 | [Remotesignal]Alarm 4 | 0x7D0B |  | U16 |  | RO
16 | [Remotesignal]Alarm 5 | 0x7D0C |  | U16 |  | RO
17 | [Remotesignal]Alarm 6 | 0x7D0D |  | U16 |  | RO
18 | FaultCode | 0x7D5A |  | U16 |  | RO
19 | Numberofcriticalalarms | 0x7D97 |  | U16 | 1 | RO
20 | Numberofmajoralarms | 0x7D98 |  | U16 | 1 | RO
21 | NumberofMinorAlarms | 0x7D99 |  | U16 | 1 | RO
22 | NumberofWarningAlarms | 0x7D9A |  | U16 | 1 | RO
23 | Monitoringalarm 1 | 0x7DFC |  | U16 |  | RO
24 | Monitoringalarm 2 | 0x7DFD |  | U16 |  | RO
25 | Monitoralarm 3 | 0x7DFE |  | U16 |  | RO
26 | [External]Poweralarm 1 | 0x7DFF |  | U16 |  | RO
27 | [External]Poweralarm 2 | 0x7E00 |  | U16 |  | RO
28 | [External]Poweralarm 3 | 0x7E01 |  | U16 |  | RO
29 | [External]Poweralarm 4 | 0x7E02 |  | U16 |  | RO
30 | [External]Poweralarm 5 | 0x7E03 |  | U16 |  | RO
31 | [External]Poweralarm 6 | 0x7E04 |  | U16 |  | RO
32 | [External]Poweralarm 7 | 0x7E05 |  | U16 |  | RO
33 | [External]Poweralarm 8 | 0x7E06 |  | U16 |  | RO
34 | [External]Poweralarm 9 | 0x7E07 |  | U16 |  | RO
35 | [External]Poweralarm10 | 0x7E08 |  | U16 |  | RO
36 | [External]Poweralarm11 | 0x7E09 |  | U16 |  | RO
37 | [External]Poweralarm12 | 0x7E0A |  | U16 |  | RO
38 | [External]Poweralarm13 | 0x7E0B |  | U16 |  | RO
39 | [External]Poweralarm14 | 0x7E0C |  | U16 |  | RO
40 | [External]Poweralarm15 | 0x7E0D |  | U16 |  | RO
41 | [External]Poweralarm16 | 0x7E0E |  | U16 |  | RO
42 | Monitoralarm 4 | 0x7E0F |  | U16 |  | RO
43 | Monitoralarm 5 | 0x7E10 |  | U16 |  | RO
44 | [External]Poweralarm17 | 0x7E11 |  | U16 |  | RO
45 | Internalalarm | 0x88C2 |  | U16 | V 1 | RO
46 | Audibleandvisualalarm | 0xA432 |  | U16 |  | RW
47 | Powergridfaultrecoveryautomaticstartup | 0xA44D | 03 | U16 |  | RW
48 | Abnormalgroundingshutdown | 0xA454 | 03 | U16 |  | RW
49 | Power-onsoftstarttimeduetopowergridfaults | 0xA474 | 03 | U16 | 1 | RW
50 | Powergridfaultrecoverytime | 0xA478 | 03 | U16 | 1 | RW
51 | [4G][Default]Identityauthenticationtype | 0xA9A9 | 03 | U16 |  | RW
52 | [4G][Default]APN | 0xA9AA | 03 | STRING | 1 | RW
53 | [4G][Default]APNusername | 0xA9CA | 03 | STRING | 1 | RW
54 | SupportFaultClearance | 0xAC32 | 03 | U16 | 1 | WO
55 | SupportFaultClearance | 0xAD10 | 03 | U16 |  | WO
56 | Clearingactivealarms | 0xAFC9 | 03 | U16 |  | WO
57 | Alarmsetting | 0xAFCB | 03 | U16 |  | WO
58 | Alarmclearance | 0xAFCD | 03 | U16 |  | WO
59 | Alarmmasking | 0xAFCE | 03 | U16 |  | WO
60 | Alarmportself-checkstart | 0xAFED | 03 | U16 | 1 | WO
61 | Audibleandvisualalarmconfirmation | 0xAFF0 | 03 | U16 | 1 | WO
62 | MaximumFeedGridPowerDefault | 0xBA3B | 03 | S32 | kW 1000 | RW
63 | Defaultactivepowerchangegradient | 0xBA3D | 03 | U32 | 1000 | RW
64 | Faulty Monitoring Unit | 0xF000 | 03 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 41/41
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x7D6C | TotalDCInputPower | U32 | kWh | 100
13 | cumulative_energy | PDF | O | 0x7D6A | Accumulatedpowergeneration | U32 | kWh | 100 | kWh→Wh (*1000)
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x7D59 | INVERTER_MODE | U16 |  |  | 0=Standby: initia, 1=Standby: detect, 2=Standby: detect, 3=Standby: drid, 512=On-grid, 768=Shutdown: fault... (+9)
16 | alarm1 | PDF | O | 0x7D5A | FaultCode | U16
17 | alarm2 | PDF | O | 0x7D08 | [Remotesignal]Alarm 1 | U16 |  |  | 0=input overvolta, 1=input undervolt, 2=output overvolt, 4=overtemperature, 6=output short ci, 7=EEPROM fault... (+15)
18 | alarm3 | PDF | O | 0x7D09 | [Remotesignal]Alarm 2 | U16 |  |  | 13=CEI0-21, 14=EN50438-CZ, 15=RD1699/661, 16=RD1699/661-MV48, 17=EN50438-NL, 18=C10/11... (+23)
19 | mppt1_voltage | PDF | O | 0x7D10 | PV1voltage | S16 | V | 10
20 | mppt1_current | PDF | O | 0x7D11 | PV1current | S16 | A | 100
21 | mppt2_voltage | PDF | O | 0x7D12 | PV2Voltage | S16 | V | 10
22 | mppt2_current | PDF | O | 0x7D13 | PV2current | S16 | A | 100
23 | mppt3_voltage | PDF | O | 0x7D14 | PV3Voltage | S16 | V | 10
24 | mppt3_current | PDF | O | 0x7D15 | PV3current | S16 | A | 100
25 | mppt4_voltage | PDF | O | 0x7D16 | PV4Voltage | S16 | V | 10
26 | mppt4_current | PDF | O | 0x7D17 | PV4current | S16 | A | 100
27 | mppt5_voltage | PDF | O | 0x7D18 | PV5voltage | S16 | V | 10
28 | mppt5_current | PDF | O | 0x7D19 | PV5current | S16 | A | 100
29 | mppt6_voltage | PDF | O | 0x7D1A | PV6voltage | S16 | V | 10
30 | mppt6_current | PDF | O | 0x7D1B | PV6current | S16 | A | 100
31 | mppt7_voltage | PDF | O | 0x7D1C | PV7Voltage | S16 | V | 10
32 | mppt7_current | PDF | O | 0x7D1D | PV7current | S16 | A | 100
33 | mppt8_voltage | PDF | O | 0x7D1E | PV8Voltage | S16 | V | 10
34 | mppt8_current | PDF | O | 0x7D1F | PV8current | S16 | A | 100
35 | string1_current | HANDLER | O | 0x7D11 | PV1current | S16 | A | 100
36 | string2_current | HANDLER | O | 0x7D13 | PV2current | S16 | A | 100
37 | string3_current | HANDLER | O | 0x7D15 | PV3current | S16 | A | 100
38 | string4_current | HANDLER | O | 0x7D17 | PV4current | S16 | A | 100
39 | string5_current | HANDLER | O | 0x7D19 | PV5current | S16 | A | 100
40 | string6_current | HANDLER | O | 0x7D1B | PV6current | S16 | A | 100
41 | string7_current | HANDLER | O | 0x7D1D | PV7current | S16 | A | 100
42 | string8_current | HANDLER | O | 0x7D1F | PV8current | S16 | A | 100

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 8ch / String 8ch
MPPT 채널 수 | 8
String 채널 수 | 8
String 모니터링 | No (MPPT당 1 String)
MPPT 채널 H01 매칭 (16개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x7D10 | PV1voltage | S16 | V | 10
2 | mppt1_current | PDF | O | 0x7D11 | PV1current | S16 | A | 100
3 | mppt2_voltage | PDF | O | 0x7D12 | PV2Voltage | S16 | V | 10
4 | mppt2_current | PDF | O | 0x7D13 | PV2current | S16 | A | 100
5 | mppt3_voltage | PDF | O | 0x7D14 | PV3Voltage | S16 | V | 10
6 | mppt3_current | PDF | O | 0x7D15 | PV3current | S16 | A | 100
7 | mppt4_voltage | PDF | O | 0x7D16 | PV4Voltage | S16 | V | 10
8 | mppt4_current | PDF | O | 0x7D17 | PV4current | S16 | A | 100
9 | mppt5_voltage | PDF | O | 0x7D18 | PV5voltage | S16 | V | 10
10 | mppt5_current | PDF | O | 0x7D19 | PV5current | S16 | A | 100
11 | mppt6_voltage | PDF | O | 0x7D1A | PV6voltage | S16 | V | 10
12 | mppt6_current | PDF | O | 0x7D1B | PV6current | S16 | A | 100
13 | mppt7_voltage | PDF | O | 0x7D1C | PV7Voltage | S16 | V | 10
14 | mppt7_current | PDF | O | 0x7D1D | PV7current | S16 | A | 100
15 | mppt8_voltage | PDF | O | 0x7D1E | PV8Voltage | S16 | V | 10
16 | mppt8_current | PDF | O | 0x7D1F | PV8current | S16 | A | 100
String 채널 H01 매칭 (8개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | 0x7D11 | PV1current | S16 | A | 100
2 | string2_current | HANDLER | O | 0x7D13 | PV2current | S16 | A | 100
3 | string3_current | HANDLER | O | 0x7D15 | PV3current | S16 | A | 100
4 | string4_current | HANDLER | O | 0x7D17 | PV4current | S16 | A | 100
5 | string5_current | HANDLER | O | 0x7D19 | PV5current | S16 | A | 100
6 | string6_current | HANDLER | O | 0x7D1B | PV6current | S16 | A | 100
7 | string7_current | HANDLER | O | 0x7D1D | PV7current | S16 | A | 100
8 | string8_current | HANDLER | O | 0x7D1F | PV8current | S16 | A | 100
MONITORING 전체 (562개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | VDE-AR-N-4105 | 0x0000 | 03 | U16 |  | RO
2 | Feature data sequencenumber | 0x0002 | 03 | U16 |  | RO
3 | UTE C 15-712-1(B) | 0x0003 | 03 | U16 |  | RO
4 | File version | 0x0004 | 03 | U16 |  | RO
5 | VDE 0126-1-1-BU | 0x0005 | 03 | U16 |  | RO
6 | VDE 0126-1-1-GR(A) | 0x0006 | 03 | U16 | A | RO
7 | VDE 0126-1-1-GR(B) | 0x0007 | 03 | U16 |  | RO
8 | BDEW-MV | 0x0008 | 03 | U16 |  | RO
9 | G59-England | 0x0009 | 03 | U16 |  | RO
10 | P/P value at point 1n | 0x000A | 03 | U16 | 10 | RO
11 | G83-England | 0x000B | 03 | U16 |  | RO
12 | G83-Scotland | 0x000C | 03 | U16 |  | RO
13 | CEI0-21 | 0x000D | 03 | U16 |  | RO
14 | 0x0E | 0x000E | 03 | U16 |  | RO
15 | RD1699/661 | 0x000F | 03 | U16 |  | RO
16 | RD1699/661-MV480 | 0x0010 | 03 | U16 |  | RO
17 | C10/11 | 0x0012 | 03 | U16 |  | RO
18 | AS4777 | 0x0013 | 03 | U16 |  | RO
19 | Custom (50 Hz) | 0x0015 | 03 | U16 | Hz | RO
20 | Custom (60 Hz) | 0x0016 | 03 | U16 | Hz | RO
21 | CEI0-16 | 0x0017 | 03 | U16 |  | RO
22 | Real-time data ofoptimizer 1 | 0x001A | 03 | U16 |  | RO
23 | TAI-MEA | 0x001B | 03 | U16 |  | RO
24 | BDEW-MV480 | 0x001C | 03 | U16 |  | RO
25 | Custom MV480 (50 Hz) | 0x001D | 03 | U16 | Hz | RO
26 | G59-England-MV480 | 0x001F | 03 | U16 |  | RO
27 | UTE C 15-712-1-MV480 | 0x0021 | 03 | U16 |  | RO
28 | TAI-PEA-MV480 | 0x0022 | 03 | U16 |  | RO
29 | TAI-MEA-MV480 | 0x0023 | 03 | U16 |  | RO
30 | C11/C10-MV480 | 0x0029 | 03 | U16 |  | RO
31 | 0x2B | 0x002B | 03 | U16 |  | RO
32 | NRS-097-2-1 | 0x002D | 03 | U16 |  | RO
33 | NRS-097-2-1-MV480 | 0x002E | 03 | U16 |  | RO
34 | IEEE 1547-MV480 | 0x0030 | 03 | U16 |  | RO
35 | ANRE | 0x0034 | 03 | U16 |  | RO
36 | ANRE-MV480 | 0x0035 | 03 | U16 |  | RO
37 | ELECTRIC RULE NO.21-MV480 | 0x0036 | 03 | U16 |  | RO
38 | HECO-MV480 | 0x0037 | 03 | U16 |  | RO
39 | PRC 024 Eastern-MV480_ _ | 0x0038 | 03 | U16 |  | RO
40 | PRC 024 Western-_ _MV480 | 0x0039 | 03 | U16 |  | RO
41 | PRC 024 Quebec-MV480_ _ | 0x003A | 03 | U16 |  | RO
42 | PRC 024 ERCOT-MV480_ _ | 0x003B | 03 | U16 |  | RO
43 | PO12.3-MV480 | 0x003C | 03 | U16 |  | RO
44 | EN50438 IE-MV480_ | 0x003D | 03 | U16 |  | RO
45 | EN50438 IE_ | 0x003E | 03 | U16 |  | RO
46 | IEEE 1547a-MV480 | 0x003F | 03 | U16 |  | RO
47 | 0x41 | 0x0041 | 03 | U16 |  | RO
48 | CEI0-16-MV480 | 0x0046 | 03 | U16 |  | RO
49 | PO12.3 | 0x0047 | 03 | U16 |  | RO
50 | CEI0-21-MV480 | 0x004A | 03 | U16 |  | RO
51 | IEEE 1547-MV600 | 0x004F | 03 | U16 |  | RO
52 | ELECTRIC RULE NO.21-MV600 | 0x0050 | 03 | U16 |  | RO
53 | HECO-MV600 | 0x0051 | 03 | U16 |  | RO
54 | PRC 024 Eastern-MV600_ _ | 0x0052 | 03 | U16 |  | RO
55 | PRC 024 Western-_ _MV600 | 0x0053 | 03 | U16 |  | RO
56 | PRC 024 Quebec-MV600_ _ | 0x0054 | 03 | U16 |  | RO
57 | PRC 024 ERCOT-MV600_ _ | 0x0055 | 03 | U16 |  | RO
58 | IEEE 1547a-MV600 | 0x0056 | 03 | U16 |  | RO
59 | Function code | 0x005A | 03 | U16 |  | RO
60 | NAMIBIA | 0x005B | 03 | U16 |  | RO
61 | ABNT NBR 16149 | 0x005C | 03 | U16 |  | RO
62 | ABNT NBR 16149-MV480 | 0x005D | 03 | U16 |  | RO
63 | SA RPPs_ | 0x005E | 03 | U16 |  | RO
64 | SA RPPs-MV480_ | 0x005F | 03 | U16 |  | RO
65 | ZAMBIA | 0x0062 | 03 | U16 |  | RO
66 | ZAMBIA-MV480 | 0x0063 | 03 | U16 |  | RO
67 | KENYA ETHIOPIA_ | 0x006B | 03 | U16 |  | RO
68 | Feature data of optimizer1 | 0x006C | 03 | U16 |  | RO
69 | G59-England-MV800 | 0x006D | 03 | U16 |  | RO
70 | NIGERIA | 0x006E | 03 | U16 |  | RO
71 | NIGERIA-MV480 | 0x006F | 03 | U16 |  | RO
72 | DUBAI | 0x0070 | 03 | U16 |  | RO
73 | DUBAI-MV480 | 0x0071 | 03 | U16 |  | RO
74 | Northern Ireland | 0x0072 | 03 | U16 |  | RO
75 | Northern Ireland-MV480 | 0x0073 | 03 | U16 |  | RO
76 | Cameroon | 0x0074 | 03 | U16 |  | RO
77 | Cameroon-MV480 | 0x0075 | 03 | U16 |  | RO
78 | Custom MV600-50 Hz | 0x0078 | 03 | U16 | Hz | RO
79 | BDEW-MV800 | 0x007C | 03 | U16 |  | RO
80 | ABNT NBR 16149-MV800 | 0x007D | 03 | U16 |  | RO
81 | UTE C 15-712-1-MV800 | 0x007E | 03 | U16 |  | RO
82 | No permission | 0x0080 | 03 | U16 |  | RO
83 | TAI-PEA-MV800 | 0x0082 | 03 | U16 |  | RO
84 | 0x83 | 0x0083 | 03 | U16 |  | RO
85 | NRS-097-2-1-MV800 | 0x0085 | 03 | U16 |  | RO
86 | SA RPPs-MV800_ | 0x0086 | 03 | U16 |  | RO
87 | 0x87 | 0x0087 | 03 | U16 |  | RO
88 | Description aboutthe first device | 0x0088 | 03 | ASCII |  | RO
89 | DUBAI-MV800 | 0x008A | 03 | U16 |  | RO
90 | EN50438 IE-MV800_ | 0x008C | 03 | U16 |  | RO
91 | Northern Ireland-MV800 | 0x008E | 03 | U16 |  | RO
92 | CEI0-21-MV800 | 0x008F | 03 | U16 |  | RO
93 | IEC 61727-MV800-60Hz | 0x0090 | 03 | U16 |  | RO
94 | NAMIBIA MV480_ | 0x0091 | 03 | U16 |  | RO
95 | Pakistan-MV800 | 0x0094 | 03 | U16 |  | RO
96 | BRASIL-ANEEL-MV800 | 0x0095 | 03 | U16 |  | RO
97 | CEI0-16-MV800 | 0x0097 | 03 | U16 |  | RO
98 | ZAMBIA-MV800 | 0x0098 | 03 | U16 |  | RO
99 | KENYA ETHIOPIA-_MV800 | 0x0099 | 03 | U16 |  | RO
100 | NAMIBIA MV800_ | 0x009A | 03 | U16 |  | RO
101 | Cameroon-MV800 | 0x009B | 03 | U16 |  | RO
102 | NIGERIA-MV800 | 0x009C | 03 | U16 |  | RO
103 | ABUDHABI-MV800 | 0x009D | 03 | U16 |  | RO
104 | LEBANON | 0x009E | 03 | U16 |  | RO
105 | LEBANON-MV480 | 0x009F | 03 | U16 |  | RO
106 | LEBANON-MV800 | 0x00A0 | 03 | U16 |  | RO
107 | TUNISIA | 0x00A6 | 03 | U16 |  | RO
108 | TUNISIA-MV480 | 0x00A7 | 03 | U16 |  | RO
109 | TUNISIA-MV800 | 0x00A8 | 03 | U16 |  | RO
110 | JAMAICA-MV800 | 0x00A9 | 03 | U16 |  | RO
111 | Ghana-MV480 | 0x00AF | 03 | U16 |  | RO
112 | VDE-AR-N4120-HV | 0x00B4 | 03 | U16 |  | RO
113 | VDE-AR-N4120-HV480 | 0x00B5 | 03 | U16 |  | RO
114 | VDE-AR-N4120-HV800 | 0x00B6 | 03 | U16 |  | RO
115 | IEEE 1547-MV800 | 0x00B7 | 03 | U16 |  | RO
116 | Nicaragua-MV800 | 0x00B8 | 03 | U16 |  | RO
117 | IEEE 1547a-MV800 | 0x00B9 | 03 | U16 |  | RO
118 | ELECTRIC RULE NO.21-MV800 | 0x00BA | 03 | U16 |  | RO
119 | HECO-MV800 | 0x00BB | 03 | U16 |  | RO
120 | PRC 024 Eastern-MV800_ _ | 0x00BC | 03 | U16 |  | RO
121 | PRC 024 Western-_ _MV800 | 0x00BD | 03 | U16 |  | RO
122 | PRC 024 Quebec-MV800_ _ | 0x00BE | 03 | U16 |  | RO
123 | PRC 024 ERCOT-MV800_ _ | 0x00BF | 03 | U16 |  | RO
124 | Custom-MV800-50Hz | 0x00C0 | 03 | U16 |  | RO
125 | RD1699/661-MV800 | 0x00C1 | 03 | U16 |  | RO
126 | PO12.3-MV800 | 0x00C2 | 03 | U16 |  | RO
127 | SVG-LV | 0x00C6 | 03 | U16 |  | RO
128 | Ghana-MV800 | 0x00CA | 03 | U16 |  | RO
129 | TAIPOWER | 0x00CB | 03 | U16 |  | RO
130 | TAIPOWER-MV480 | 0x00CC | 03 | U16 |  | RO
131 | TAIPOWER-MV800 | 0x00CD | 03 | U16 |  | RO
132 | IEEE 1547-LV208 | 0x00CE | 03 | U16 |  | RO
133 | IEEE 1547-LV240 | 0x00CF | 03 | U16 |  | RO
134 | IEEE 1547a-LV208 | 0x00D0 | 03 | U16 |  | RO
135 | IEEE 1547a-LV240 | 0x00D1 | 03 | U16 |  | RO
136 | ELECTRIC RULE NO.21-LV208 | 0x00D2 | 03 | U16 |  | RO
137 | ELECTRIC RULE NO.21-LV240 | 0x00D3 | 03 | U16 |  | RO
138 | HECO-O+M+H-LV208 | 0x00D4 | 03 | U16 |  | RO
139 | HECO-O+M+H-LV240 | 0x00D5 | 03 | U16 |  | RO
140 | PRC 024 Eastern-LV208_ _ | 0x00D6 | 03 | U16 |  | RO
141 | PRC 024 Eastern-LV240_ _ | 0x00D7 | 03 | U16 |  | RO
142 | PRC 024 Western-LV208_ _ | 0x00D8 | 03 | U16 |  | RO
143 | PRC 024 Western-LV240_ _ | 0x00D9 | 03 | U16 |  | RO
144 | PRC 024 ERCOT-LV208_ _ | 0x00DA | 03 | U16 |  | RO
145 | PRC 024 ERCOT-LV240_ _ | 0x00DB | 03 | U16 |  | RO
146 | PRC 024 Quebec-LV208_ _ | 0x00DC | 03 | U16 |  | RO
147 | PRC 024 Quebec-LV240_ _ | 0x00DD | 03 | U16 |  | RO
148 | Bangladesh | 0x00E5 | 03 | U16 |  | RO
149 | Bangladesh-MV480 | 0x00E6 | 03 | U16 |  | RO
150 | Bangladesh-MV800 | 0x00E7 | 03 | U16 |  | RO
151 | Bahrain | 0x00EA | 03 | U16 |  | RO
152 | Bahrain-MV480 | 0x00EB | 03 | U16 |  | RO
153 | Bahrain-MV800 | 0x00EC | 03 | U16 |  | RO
154 | KAZAKHSTAN-MV800 | 0x00F2 | 03 | U16 |  | RO
155 | Mauritius | 0x00F3 | 03 | U16 |  | RO
156 | TAI-MEA-MV800 | 0x00F8 | 03 | U16 |  | RO
157 | Pakistan | 0x00F9 | 03 | U16 |  | RO
158 | Pakistan-MV480 | 0x00FA | 03 | U16 |  | RO
159 | HECO-L+M-LV208 | 0x00FC | 03 | U16 |  | RO
160 | HECO-L+M-LV240 | 0x00FD | 03 | U16 |  | RO
161 | C10/11-MV800 | 0x00FE | 03 | U16 |  | RO
162 | Description aboutthe 120th device | 0x00FF | 03 | U16 |  | RO
163 | G99-TYPEA-LV | 0x0102 | 03 | U16 |  | RO
164 | G99-TYPEB-LV | 0x0103 | 03 | U16 |  | RO
165 | G99-TYPEB-HV | 0x0104 | 03 | U16 |  | RO
166 | G99-TYPEB-HV-MV480 | 0x0105 | 03 | U16 |  | RO
167 | G99-TYPEB-HV-MV800 | 0x0106 | 03 | U16 |  | RO
168 | G99-TYPEC-HV-MV800 | 0x0107 | 03 | U16 |  | RO
169 | G99-TYPED-MV800 | 0x0108 | 03 | U16 |  | RO
170 | G99-TYPEA-HV | 0x0109 | 03 | U16 |  | RO
171 | CEA-MV800 | 0x010A | 03 | U16 |  | RO
172 | VDE-AR-N4110 | 0x010C | 03 | U16 |  | RO
173 | VDE-AR-N4110-MV480 | 0x010D | 03 | U16 |  | RO
174 | VDE-AR-N4110-MV800 | 0x010E | 03 | U16 |  | RO
175 | Panama-MV800 | 0x010F | 03 | U16 |  | RO
176 | North Macedonia-MV800 | 0x0110 | 03 | U16 |  | RO
177 | NTS-MV480 | 0x0112 | 03 | U16 |  | RO
178 | NTS-MV800 | 0x0113 | 03 | U16 |  | RO
179 | String Reverse Connection | 0x07DB | 03 | STRINGING |  | RO
180 | String Current Backfeed | 0x07DC | 03 | STRINGING |  | RO
181 | Abnormal String Power | 0x07DD | 03 | STRINGING |  | RO
182 | High input string voltage toground. | 0x07DE | 03 | STRINGING |  | RO
183 | PV String Loss | 0x07DF | 03 | STRINGING |  | RO
184 | AFCI Self-Check Fail.[1] | 0x07E5 | 03 | U16 |  | RO
185 | Phase Wire Short-Circuitedto PE | 0x07EF | 03 | U16 |  | RO
186 | Grid Loss | 0x07F0 | 03 | U16 |  | RO
187 | Grid Undervoltage | 0x07F1 | 03 | U16 |  | RO
188 | Grid Overvoltage | 0x07F2 | 03 | U16 |  | RO
189 | Grid Volt. Imbalance | 0x07F3 | 03 | U16 |  | RO
190 | Grid Overfrequency | 0x07F4 | 03 | U16 |  | RO
191 | Grid Underfrequency | 0x07F5 | 03 | U16 |  | RO
192 | Unstable Grid Frequency | 0x07F6 | 03 | U16 |  | RO
193 | Output Overcurrent | 0x07F7 | 03 | U16 |  | RO
194 | Output DC ComponentOverhigh | 0x07F8 | 03 | U16 |  | RO
195 | Abnormal Residual Current | 0x0803 | 03 | U16 |  | RO
196 | Overtemperature | 0x080F | 03 | U16 |  | RO
197 | Upgrade Failed or VersionMismatch | 0x0811 | 03 | U16 |  | RO
198 | License Expired | 0x0812 | 03 | U16 |  | RO
199 | Battery ReverseConnection[7] | 0x0815 | 03 | U16 |  | RO
200 | Active Islanding | 0x0816 | 03 | U16 |  | RO
201 | Passive Islanding | 0x0817 | 03 | U16 |  | RO
202 | Transient AC Overvoltage | 0x0818 | 03 | U16 |  | RO
203 | Peripheral port shortcircuit[3] | 0x081B | 03 | U16 |  | RO
204 | NumberofPVstrings | 0x7577 |  | U16 | 1 | RO
205 | Maximumactivepower(Pmax) | 0x757B |  | U32 | kW 1000 | RO
206 | Maximumapparent(Smax) | 0x757D |  | U32 | kVA 1000 | RO
207 | Real-timemaximumreactivepower(Qmax,fedtothepowergrid) | 0x757F |  | S32 | 1000 | RO
208 | Real-timemaximumreactivepower (-Qmax,absorbedfromthepowergrid) | 0x7581 |  | S32 | 1000 | RO
209 | Maximumactivepower(Pmax r_eal) | 0x7583 |  | U32 | kW 1000 | RO
210 | Maximumapparentcapability(Smax r_eal) | 0x7585 |  | U32 | kVA 1000 | RO
211 | Productsalesarea | 0x7599 |  | STRING |  | RO
212 | ProductsoftwareID | 0x759B |  | U16 |  | RO
213 | UniqueID ofthesoftware. | 0x759E |  | U16 |  | RO
214 | Numberofupgradepackages | 0x759F |  | U16 | 1 | RO
215 | Informationaboutsubpackage 1 | 0x75A0 |  | U32 |  | RO
216 | Subpackage 2information | 0x75A2 |  | U32 |  | RO
217 | Informationaboutsubpackage 3 | 0x75A4 |  | U32 |  | RO
218 | Subpackage 4information | 0x75A6 |  | U32 |  | RO
219 | Subpackage 5information | 0x75A8 |  | U32 |  | RO
220 | Informationaboutsubpackage 6 | 0x75AA |  | U32 |  | RO
221 | Subpackage 7information | 0x75AC |  | U32 |  | RO
222 | Subpackage 8information | 0x75AE |  | U32 |  | RO
223 | Subpackage 9information | 0x75B0 |  | U32 |  | RO
224 | Informationaboutsubpackage10 | 0x75B2 |  | U32 |  | RO
225 | SubdeviceSupportID | 0x75FF |  | U32 |  | RO
226 | Subdevicepresenceflag. | 0x7601 |  | U32 |  | RO
227 | NumberofuniquesouthboundsoftwareIDs | 0x7724 |  | U16 | 1 | RO
228 | UniqueID 1ofthesouthboundsoftware. | 0x7725 |  | U16 |  | RO
229 | UniqueID 2ofthesouthboundsoftware | 0x7726 |  | U16 |  | RO
230 | Numberofupgradepackagesforsouthbounddevice 1 | 0x772A |  | U16 | 1 | RO
231 | Informationaboutsubpackage 1ofsouthbounddevice 1 | 0x772B |  | U32 |  | RO
232 | Informationaboutsubpackage 2ofsouthbounddevice 1 | 0x772D |  | U32 |  | RO
233 | Informationaboutsubpackage 3ofsouthbounddevice 1 | 0x772F |  | U32 |  | RO
234 | Numberofupgradepackagesforsouthbounddevice 2 | 0x7735 |  | U16 | 1 | RO
235 | Informationaboutsubpackage 1ofsouthbounddevice 2 | 0x7736 |  | U32 |  | RO
236 | Informationaboutsubpackage 2ofsouthbounddevice 2 | 0x7738 |  | U32 |  | RO
237 | Informationaboutsubpackage 3ofsouthbounddevice 2 | 0x773A |  | U32 |  | RO
238 | Informationaboutsubpackage 4ofsouthbounddevice 2 | 0x773C |  | U32 |  | RO
239 | Ofefringname ofsouthbounddevice 1 | 0x7761 |  | STRING |  | RO
240 | Offeringname ofsouthbounddevice 2 | 0x7770 |  | STRING |  | RO
241 | Ofefringname ofsouthbounddevice 3. | 0x777F |  | STRING |  | RO
242 | Hardwareversion | 0x7918 |  | STRING | 1 | RO
243 | MainDSPversion | 0x7940 |  | STRING |  | RO
244 | CPLDversionnumber | 0x795E |  | STRING |  | RO
245 | AFCIversionnumber | 0x796D |  | STRING |  | RO
246 | DC-MBUSversionnumber | 0x798B |  | STRING |  | RO
247 | Registrationcode | 0x79E0 |  | STRING | 1 | RO
248 | [Remotecommunication]Single-noderemotecommunication | 0x7D00 |  | U16 |  | RO
249 | PV1voltage | 0x7D10 |  | S16 | V 10 | RO | mppt1_voltage
250 | PV1current | 0x7D11 |  | S16 | A 100 | RO | mppt1_current
251 | PV2Voltage | 0x7D12 |  | S16 | V 10 | RO | mppt2_voltage
252 | PV2current | 0x7D13 |  | S16 | A 100 | RO | mppt2_current
253 | PV3Voltage | 0x7D14 |  | S16 | V 10 | RO | mppt3_voltage
254 | PV3current | 0x7D15 |  | S16 | A 100 | RO | mppt3_current
255 | PV4Voltage | 0x7D16 |  | S16 | V 10 | RO | mppt4_voltage
256 | PV4current | 0x7D17 |  | S16 | A 100 | RO | mppt4_current
257 | PV5voltage | 0x7D18 |  | S16 | V 10 | RO | mppt5_voltage
258 | PV5current | 0x7D19 |  | S16 | A 100 | RO | mppt5_current
259 | PV6voltage | 0x7D1A |  | S16 | V 10 | RO | mppt6_voltage
260 | PV6current | 0x7D1B |  | S16 | A 100 | RO | mppt6_current
261 | PV7Voltage | 0x7D1C |  | S16 | V 10 | RO | mppt7_voltage
262 | PV7current | 0x7D1D |  | S16 | A 100 | RO | mppt7_current
263 | PV8Voltage | 0x7D1E |  | S16 | V 10 | RO | mppt8_voltage
264 | PV8current | 0x7D1F |  | S16 | A 100 | RO | mppt8_current
265 | DCpower | 0x7D40 |  | S32 | kW 1000 | RO
266 | PowergridlineAandBvoltage | 0x7D42 |  | U16 | V 10 | RO
267 | PowergridB/Clinevoltage | 0x7D43 |  | U16 | V 10 | RO
268 | PowergridCAlinevoltage | 0x7D44 |  | U16 | V 10 | RO
269 | Powergridphase Avoltage | 0x7D45 |  | U16 | V 10 | RO
270 | Powergridphase Bvoltage | 0x7D46 |  | U16 | V 10 | RO
271 | Powergridphase Cvoltage | 0x7D47 |  | U16 | V 10 | RO
272 | Powergridphase Acurrent | 0x7D48 |  | S32 | A 1000 | RO
273 | Powergridphase Bcurrent | 0x7D4A |  | S32 | A 1000 | RO
274 | Powergridphase Ccurrent | 0x7D4C |  | S32 | A 1000 | RO
275 | Peakactivepower ofthecurrentday | 0x7D4E |  | S32 | kW 1000 | RO
276 | Activepower | 0x7D50 |  | S32 | kW 1000 | RO
277 | reactivepower | 0x7D52 |  | S32 | 1000 | RO
278 | Powerfactor | 0x7D54 |  | S16 | 1000 | RO
279 | Gridfrequency | 0x7D55 |  | U16 | Hz 100 | RO
280 | Inverterefficiency | 0x7D56 |  | U16 | 100 | RO
281 | Insulationimpedance | 0x7D58 |  | U16 | 1000 | RO
282 | Start-uptime | 0x7D5B |  | U16 | 1 | RO
283 | Shutdowntime | 0x7D5D |  | U16 | 1 | RO
284 | Activepower[fast] | 0x7D5F |  | S32 | kW 1000 | RO
285 | Accumulatedpowergeneration | 0x7D6A |  | U32 | kWh 100 | RO | cumulative_energy
286 | TotalDCInputPower | 0x7D6C |  | U32 | kWh 100 | RO | pv_power
287 | Statisticaltimeofthecurrentenergyyield. | 0x7D6E |  | U16 | 1 | RO
288 | CurrentHourElectricity | 0x7D70 |  | U32 | kWh 100 | RO
289 | Current-daypowergeneration | 0x7D72 |  | U32 | kWh 100 | RO
290 | Electricitygenerated inthecurrentmonth | 0x7D74 |  | U32 | kWh 100 | RO
291 | Electricitygenerated inthecurrentyear | 0x7D76 |  | U32 | kWh 100 | RO
292 | LastHourPowerStatisticsTime | 0x7D9C |  | U16 | 1 | RO
293 | Electricitygenerated intheprevioushour | 0x7D9E |  | U32 | kWh 100 | RO
294 | Electricitystatisticstimeofthepreviousday | 0x7DA0 |  | U16 | 1 | RO
295 | Electricitygenerated inthepreviousday | 0x7DA2 |  | U32 | kWh 100 | RO
296 | Statisticaltimeofthepreviousmonth. | 0x7DA4 |  | U16 | 1 | RO
297 | Electricitygenerated inthepreviousmonth | 0x7DA6 |  | U32 | kWh 100 | RO
298 | Electricitystatisticstimeofthepreviousyear | 0x7DA8 |  | U16 | 1 | RO
299 | Electricitygenerated inthepreviousyear | 0x7DAA |  | U32 | kWh 100 | RO
300 | MaximumPVvoltage | 0x7DB1 |  | S16 | V 10 | RO
301 | MinimumPVvoltage | 0x7DB2 |  | S16 | V 10 | RO
302 | AveragePVnegative-to-groundvoltage | 0x7DB3 |  | S16 | V 10 | RO
303 | MaximumPVpositive-to-groundvoltage | 0x7DB4 |  | S16 | V 10 | RO
304 | MinimumPVnegative-to-groundvoltage | 0x7DB5 |  | S16 | V 10 | RO
305 | Inverter-to-PEwithstandvoltage | 0x7DB6 |  | U16 | V 1 | RO
306 | ISOfeatureinformation | 0x7DB7 |  | U16 | 1 | RO
307 | PVnegative-to-groundvoltage | 0x7DBF |  | S16 | V 10 | RO
308 | Directionofthebuilt-inPIDcompensation | 0x7DC0 |  | U16 |  | RO
309 | TotalDCenergyyieldofMPPT1 | 0x7DD4 |  | U32 | kWh 100 | RO
310 | TotalDCenergyyieldofMPPT2 | 0x7DD6 |  | U32 | kWh 100 | RO
311 | MPPT4DCAccumulatedEnergyYield | 0x7DDA |  | U32 | kWh 100 | RO | cumulative_energy
312 | Tiltangle 1sampling | 0x84D2 |  | S16 | 100 | RO
313 | Azimuth1sampling | 0x84D3 |  | S16 | 100 | RO
314 | Tiltangle 2sampling | 0x84D4 |  | S16 | 100 | RO
315 | Azimuth2sampling | 0x84D5 |  | S16 | 100 | RO
316 | Tiltangle 3sampling | 0x84D6 |  | S16 | 100 | RO
317 | Azimuth3sampling | 0x84D7 |  | S16 | 100 | RO
318 | Tiltangle 4sampling | 0x84D8 |  | S16 | 100 | RO
319 | Azimuth4sampling | 0x84D9 |  | S16 | 100 | RO
320 | Tiltangle 5sampling | 0x84DA |  | S16 | 100 | RO
321 | Azimuth5sampling | 0x84DB |  | S16 | 100 | RO
322 | Tiltangle 6sampling | 0x84DC |  | S16 | 100 | RO
323 | Azimuth6sampling | 0x84DD |  | S16 | 100 | RO
324 | Tiltangle 7sampling | 0x84DE |  | S16 | 100 | RO
325 | Azimuth7sampling | 0x84DF |  | S16 | 100 | RO
326 | Tiltangle 8sampling | 0x84E0 |  | S16 | 100 | RO
327 | Azimuth8sampling | 0x84E1 |  | S16 | 100 | RO
328 | Tiltangle 9sampling | 0x84E2 |  | S16 | 100 | RO
329 | Azimuth9sampling | 0x84E3 |  | S16 | 100 | RO
330 | Tiltangle 10sampling | 0x84E4 |  | S16 | 100 | RO
331 | Azimuth10sampling | 0x84E5 |  | S16 | 100 | RO
332 | Tiltangle 11sampling | 0x84E6 |  | S16 | 100 | RO
333 | Azimuth11sampling | 0x84E7 |  | S16 | 100 | RO
334 | Tiltangle 12sampling | 0x84E8 |  | S16 | 100 | RO
335 | Azimuth12sampling | 0x84E9 |  | S16 | 100 | RO
336 | Tiltangle 13sampling | 0x84EA |  | S16 | 100 | RO
337 | Bearing13sampling | 0x84EB |  | S16 | 100 | RO
338 | Tiltangle 14sampling | 0x84EC |  | S16 | 100 | RO
339 | Azimuth14sampling | 0x84ED |  | S16 | 100 | RO
340 | Tiltangle 15sampling | 0x84EE |  | S16 | 100 | RO
341 | Bearingangle 15sampling | 0x84EF |  | S16 | 100 | RO
342 | Tiltangle 16sampling | 0x84F0 |  | S16 | 100 | RO
343 | Bearing16sampling | 0x84F1 |  | S16 | 100 | RO
344 | Trackingsystemcontroller | 0x84F2 |  | U16 |  | RO
345 | SupportSystemType | 0x84F3 |  | U16 |  | RO
346 | Totalnumberofstents | 0x84F5 |  | U16 | 1 | RO
347 | Phase ADCcomponentDCI | 0x88DE |  | S16 | A 1000 | RO
348 | Phase BDCcomponentDCI | 0x88DF |  | S16 | A 1000 | RO
349 | Phase CDCcomponentDCI | 0x88E0 |  | S16 | A 1000 | RO
350 | LeakagecurrentRCD | 0x88E1 |  | S16 | 1 | RO
351 | I-Vscanningcapability | 0x8917 |  | U16 |  | RO
352 | [ManagementSystem]NMSIPaddress | 0x891E |  | U32 | 1 | RO
353 | [STA]WirelessRoutingAccessSignalStrength | 0x8920 |  | U16 |  | RO
354 | [NTP]NTPLastSynchronizationTime | 0x8929 |  | U32 | 1 | RO
355 | [4G]Monthlyusedtraffic | 0x892C |  | U32 | 100 | RO
356 | [4G]MonthlyRemainingTraffic | 0x892E |  | U32 | 100 | RO
357 | [4G]Averagedailytrafficusage | 0x8930 |  | U32 | 100 | RO
358 | [STA]Routerconnectiontime | 0x8934 |  | U16 | 1 | RO
359 | [Smart I-V-V-Diagnosis]AuthorizationFunction | 0x8940 |  | U32 | V 1 | RO
360 | [Smart I-V-V-Diagnosis]Licenseexpirationdate | 0x8943 |  | U16 | V 1 | RO
361 | Licenseloadingtime | 0x8945 |  | U16 | 1 | RO
362 | LicenseDeregistrationTime | 0x8947 |  | U16 | 1 | RO
363 | Invalidationcode. | 0x8953 |  | STRING | 1 | RO
364 | AuthorizationFeatureSignature | 0x8993 |  | U16 |  | RO
365 | [StringMonitoring]LicenseExpirationTime | 0x8996 |  | U16 | 1 | RO
366 | [4G]IPaddress | 0x89B2 |  | U32 | 1 | RO
367 | [4G]SubnetMask | 0x89B4 |  | U32 | 1 | RO
368 | [4G]IMEI | 0x89B6 |  | STRING | 1 | RO
369 | [4G]signalstrength | 0x89C0 |  | U16 | 1 | RO
370 | [4G]PINnumberinputtimes | 0x89C1 |  | U16 | 1 | RO
371 | Gridvoltage(phase Avoltage) | 0x90ED |  | S32 | V 10 | RO
372 | Phase Bvoltage | 0x90EF |  | S32 | V 10 | RO
373 | Phase Cvoltage | 0x90F1 |  | S32 | V 10 | RO
374 | Gridcurrent(phase Acurrent) | 0x90F3 |  | S32 | A 100 | RO
375 | Phase Bcurrent | 0x90F5 |  | S32 | A 100 | RO
376 | Phase Ccurrent | 0x90F7 |  | S32 | A 100 | RO
377 | Activepower | 0x90F9 |  | S32 | W 1 | RO
378 | reactivepower | 0x90FB |  | S32 | 1 | RO
379 | Powerfactor | 0x90FD |  | S16 | 1000 | RO
380 | Gridfrequency | 0x90FE |  | S16 | Hz 100 | RO
381 | Positiveactivepower | 0x90FF |  | S32 | kWh 100 | RO
382 | Reverseactivepower | 0x9101 |  | S32 | kWh 100 | RO
383 | Accumulatedreactivepower | 0x9103 |  | S32 | 100 | RO
384 | MeterType | 0x9105 |  | U16 |  | RO
385 | A-Blinevoltage | 0x9106 |  | S32 | V 10 | RO
386 | BClinevoltage | 0x9108 |  | S32 | V 10 | RO
387 | CAlinevoltage | 0x910A |  | S32 | V 10 | RO
388 | Phase Aactivepower | 0x910C |  | S32 | W 1 | RO
389 | Phase Bactivepower | 0x910E |  | S32 | W 1 | RO
390 | Phase Cactivepower | 0x9110 |  | S32 | W 1 | RO
391 | Totalnumberofoptimizers | 0x9150 |  | U16 | 1 | RO
392 | Numberofonlineoptimizers | 0x9151 |  | U16 | 1 | RO
393 | Featuredatasequencenumber | 0x9152 |  | U16 | 1 | RO
394 | PhysicalLocationLocatingProgress | 0x9153 |  | U16 |  | RO
395 | Logexportprogress | 0x9154 |  | U16 |  | RO
396 | Real-timedataqueryprogress | 0x9155 |  | U16 |  | RO
397 | NumberofSearchedOptimizers | 0x9157 |  | U16 | 1 | RO
398 | LayoutFileStorageProgress | 0x9159 |  | U16 | 1 | RO
399 | NumberofNetworkedNetworks | 0x9183 |  | U16 |  | RO
400 | Numberofneighboringnetworks | 0x9184 |  | U16 |  | RO
401 | Type | 0x9222 |  | U16 |  | RO
402 | Maximumnumberofconnecteddevices | 0x9235 |  | U16 | 1 | RO
403 | Carriers | 0x9240 |  | STRING | 1 | RO
404 | Totalratedcapacityofgrid-tiedinverters | 0x925E |  | U32 | kW 1000 | RO
405 | Conversionfactor | 0x9260 |  | U32 | 1000 | RO
406 | CurrentPercentage | 0x9262 |  | U16 | 10 | RO
407 | [Scheduleserver]Latestconnectiontime | 0x9265 |  | U32 |  | RO
408 | Numberofconnecteddevices | 0x9276 |  | U16 |  | RO
409 | Silenceflag | 0x9278 |  | U16 |  | RO
410 | Q-USchedulingTriggerPowerPercentage | 0x9C66 |  | S16 | 1 | RW
411 | Powerfactor | 0x9CBA |  | S16 | 1000 | RW
412 | Reactivepowercompensation(Q/S)[lowprecision] | 0x9CBB |  | S16 | 1000 | RW
413 | Reactivepoweradjustmenttime | 0x9CBC |  | U16 | 1 | RW
414 | Activepowerpercentagederating(lowprecision) | 0x9CBD |  | S16 | 10 | RW
415 | Nightreactivepowercompensation(Q/S) | 0x9CC0 |  | S16 | 1000 | RW
416 | Fixedvalue ofreactivepower atnight | 0x9CC1 |  | S32 | 1000 | RW
417 | PF-Ucharacteristiccurve | 0x9CEF |  | U16 |  | RW
418 | [Characteristiccurve]Reactivepoweradjustmenttime | 0x9D04 |  | U16 | 1 | RW
419 | Q-USchedulingExitPowerPercentage | 0x9D06 |  | S16 | 1 | RW
420 | Activepowerpercentagecontrol[lowprecision] | 0x9D07 |  | S16 | 10 | RW
421 | Quickpower-onandpower-off | 0x9D0A |  | U16 |  | WO
422 | Q-Ucharacteristiccurveminimum PFlimit | 0x9DB7 |  | U16 | 1000 | RW
423 | Powergridstandardcode | 0xA410 |  | U16 | 1 | RW
424 | Voltagelevel | 0xA412 |  | U16 | V 1 | RW
425 | FrequencyClass | 0xA413 |  | U16 | Hz 1 | RW
426 | Remotepowerscheduling | 0xA41E |  | U16 |  | RW
427 | reactivepowergradient | 0xA41F |  | U32 | 1000 | RW
428 | Activepowerchangegradient | 0xA421 |  | U32 | 1000 | RW
429 | Maximumactivepower | 0xA427 |  | U32 | kW 1000 | RW
430 | Activepowerreference | 0xA42B |  | U32 | kW 1000 | RW
431 | Plantactivepowergradient | 0xA42D |  | U16 | 1 | RW
432 | FrequencyActivePowerDeratingRecoveryDelayTime | 0xA438 |  | U16 | 1 | RW
433 | FrequencyActivePowerDeratingEffectiveDelayTime | 0xA439 |  | U16 | 1 | RW
434 | Frequencymodulationcontrolresponsedeadband | 0xA43B |  | U16 | Hz 1000 | RW
435 | Frequencymodulationcontrolpowerchangegradient | 0xA443 |  | U16 | 1 | RW
436 | Frequencymodulationcontrolpowerchangelimitingamplitude | 0xA444 |  | U16 | 10 | RW
437 | PredictedMPPTpower | 0xA448 |  | U32 | kW 1000 | RO
438 | Powerlimit0%shutdown | 0xA44E | 03 | U16 | % | RW
439 | Automaticpower-offwhencommunication isdisconnected | 0xA44F | 03 | U16 |  | RW
440 | Automaticpower-onaftercommunicationrecovery | 0xA450 | 03 | U16 |  | RW
441 | Nightreactivepower | 0xA453 | 03 | U16 |  | RW
442 | Nightreactivepowerparameterstakeeffect | 0xA456 | 03 | U16 |  | RW
443 | ActivePowerLimitforFailureProtection[kW][LowPrecision] | 0xA45D | 03 | U32 | kW 10 | RW
444 | Frequencyrateprotection | 0xA460 | 03 | U16 |  | RW
445 | Frequencychangerateprotectionpoint | 0xA461 | 03 | U16 | Hz 10 | RW
446 | Frequencychangerateprotectiontime | 0xA462 | 03 | U16 | 10 | RW
447 | Reactivepowerlimitforfailureprotection[Q/S][lowprecision] | 0xA463 | 03 | S16 | 1000 | RW
448 | Power-onvoltageupperlimitforgridconnection | 0xA464 | 03 | U16 | V 10 | RW
449 | Power-onvoltagelowerlimitforgridconnection | 0xA465 | 03 | U16 | V 10 | RW
450 | Power-onfrequencyupperlimitforgridconnection | 0xA466 | 03 | U16 | Hz 100 | RW
451 | Power-onfrequencylowerlimitforgridconnection | 0xA467 | 03 | U16 | Hz 100 | RW
452 | Powergridreconnectionvoltageupperlimit | 0xA468 | 03 | U16 | V 10 | RW
453 | PowerGridReconnectionVoltageLowerThreshold | 0xA469 | 03 | U16 | V 10 | RW
454 | Powergridreconnectionfrequencyupperlimit | 0xA46A | 03 | U16 | Hz 100 | RW
455 | Powergridreconnectionfrequencylowerlimit | 0xA46B | 03 | U16 | Hz 100 | RW
456 | AutomaticPowerGridReconnectionTime | 0xA46C | 03 | U16 | 1 | RW
457 | Voltageunbalanceprotectionthreshold | 0xA472 | 03 | U16 | 10 | RW
458 | Cos?-P/Pntriggervoltage | 0xA475 | 03 | U16 | 1 | RW
459 | Cos?-P/Pnexitvoltage | 0xA476 | 03 | U16 | 1 | RW
460 | Timefordeterminingshort-termpowergridinterruption | 0xA479 | 03 | U32 | 1 | RW
461 | Gridvoltagejumptriggerthreshold | 0xA47F | 03 | U16 | 10 | RW
462 | Short-termpowergridinterruptionandquickstartup | 0xA484 | 03 | U16 |  | RW
463 | PowergridvoltageprotectionshieldduringVRT | 0xA489 | 03 | U16 |  | RW
464 | VRTactivecurrentlimitingpercentage | 0xA48C | 03 | U16 | 1 | RW
465 | VRTactivepowerrecoverygradient | 0xA48D | 03 | U16 | 1 | RW
466 | RCDcurrentlimit | 0xA498 | 03 | U16 | 10 | RW
467 | Voltagerisesuppression | 0xA49A | 03 | U16 |  | RW
468 | Voltagerisesuppressionreactivepoweradjustmentpoint | 0xA49B | 03 | U16 | 10 | RW
469 | Voltagerisesuppressionactivederatingthreshold | 0xA49C | 03 | U16 | 10 | RW
470 | frequencymodulationcontrol | 0xA49D | 03 | U16 |  | RW
471 | frequencymodulationcontroldifferentialmodulationrate | 0xA49E | 03 | U16 | 1 | RW
472 | Overfrequencyderating | 0xA49F | 03 | U16 |  | RW
473 | Overfrequencyderatingcutofffrequency | 0xA4A0 | 03 | U16 | Hz 100 | RW
474 | Overfrequencyderatingcut-offpower | 0xA4A1 | 03 | U16 | 1 | RW
475 | Triggeringfrequency ofoverfrequencyderating | 0xA4A2 | 03 | U16 | Hz 100 | RW
476 | Overfrequencyderatingexitfrequency | 0xA4A3 | 03 | U16 | Hz 100 | RW
477 | Overfrequencyderatingpowerrecoverygradient | 0xA4A4 | 03 | U16 | 1 | RW
478 | UnderfrequencyPowerIncrease | 0xA4A7 | 03 | U16 |  | RW
479 | UnderfrequencyPowerIncreaseRecoveryGradient | 0xA4A8 | 03 | U16 | 1 | RW
480 | Cutofffrequency ofunderfrequencypowerincrease | 0xA4C0 | 03 | U16 | Hz 100 | RW
481 | Cut-offpowerforunderfrequencypowerincrease | 0xA4C1 | 03 | U16 | 1 | RW
482 | UnderfrequencyPowerIncreaseTriggeringFrequency | 0xA4C2 | 03 | U16 | Hz 100 | RW
483 | UnderfrequencyPowerIncreaseExitFrequency | 0xA4C3 | 03 | U16 | Hz 100 | RW
484 | PIDoutputvoltage | 0xA4C5 | 03 | S16 | V 10 | RW
485 | Activepowerchangegradient | 0xA4D0 | 03 | U32 | 1000 | RW
486 | Undervoltageprotectionthresholdfor10minutes | 0xA52F | 03 | U16 | V 10 | RW
487 | Ten-minuteundervoltageprotectiontime | 0xA530 | 03 | U32 | 1 | RW
488 | Ten-minuteovervoltageprotectionthreshold | 0xA532 | 03 | U16 | V 10 | RW
489 | Ten-minuteovervoltageprotectiontime | 0xA533 | 03 | U32 | 1 | RW
490 | Level-1overvoltageprotectionthreshold | 0xA535 | 03 | U16 | V 10 | RW
491 | Level-1overvoltageprotectiontime | 0xA536 | 03 | U32 | 1 | RW
492 | Level-2overvoltageprotectionthreshold | 0xA538 | 03 | U16 | V 10 | RW
493 | Level 2OvervoltageProtectionTime | 0xA539 | 03 | U32 | 1 | RW
494 | Level-3overvoltageprotectionthreshold | 0xA53B | 03 | U16 | V 10 | RW
495 | Level-3overvoltageprotectiontime | 0xA53C | 03 | U32 | 1 | RW
496 | Level-4overvoltageprotectionthreshold | 0xA53E | 03 | U16 | V 10 | RW
497 | Level-4overvoltageprotectiontime | 0xA53F | 03 | U32 | 1 | RW
498 | Level-5overvoltageprotectionthreshold | 0xA541 | 03 | U16 | V 10 | RW
499 | Level-5overvoltageprotectiontime | 0xA542 | 03 | U32 | 1 | RW
500 | Level-6overvoltageprotectionthreshold | 0xA544 | 03 | U16 | V 10 | RW
501 | Level-6overvoltageprotectiontime | 0xA545 | 03 | U32 | 1 | RW
502 | Level-1undervoltageprotectionthreshold | 0xA547 | 03 | U16 | V 10 | RW
503 | Level-1UndervoltageProtectionTime | 0xA548 | 03 | U32 | 1 | RW
504 | Level-2undervoltageprotectionthreshold | 0xA54A | 03 | U16 | V 10 | RW
505 | Level 2UndervoltageProtectionTime | 0xA54B | 03 | U32 | 1 | RW
506 | Level-3undervoltageprotectionthreshold | 0xA54D | 03 | U16 | V 10 | RW
507 | Level-3UndervoltageProtectionTime | 0xA54E | 03 | U32 | 1 | RW
508 | Level-4undervoltageprotectionthreshold | 0xA550 | 03 | U16 | V 10 | RW
509 | Level-4UndervoltageProtectionTime | 0xA551 | 03 | U32 | 1 | RW
510 | Level-5undervoltageprotectionthreshold | 0xA553 | 03 | U16 | V 10 | RW
511 | Level-5UndervoltageProtectionTime | 0xA554 | 03 | U32 | 1 | RW
512 | Level-6undervoltageprotectionthreshold | 0xA556 | 03 | U16 | V 10 | RW
513 | Level-6UndervoltageProtectionTime | 0xA557 | 03 | U32 | 1 | RW
514 | Level-1overfrequencyprotectionthreshold | 0xA559 | 03 | U16 | Hz 100 | RW
515 | Level-1OverfrequencyProtectionTime | 0xA55A | 03 | U32 | 1 | RW
516 | Level-2overfrequencyprotectionthreshold | 0xA55C | 03 | U16 | Hz 100 | RW
517 | Level-2overfrequencyprotectiontime | 0xA55D | 03 | U32 | 1 | RW
518 | Level-3overfrequencyprotectionthreshold | 0xA55F | 03 | U16 | Hz 100 | RW
519 | Level-3overfrequencyprotectiontime | 0xA560 | 03 | U32 | 1 | RW
520 | Level-4overfrequencyprotectionthreshold | 0xA562 | 03 | U16 | Hz 100 | RW
521 | Level-4overfrequencyprotectiontime | 0xA563 | 03 | U32 | 1 | RW
522 | Level-5overfrequencyprotectionthreshold | 0xA565 | 03 | U16 | Hz 100 | RW
523 | Level-5overfrequencyprotectiontime | 0xA566 | 03 | U32 | 1 | RW
524 | Level-6overfrequencyprotectionthreshold | 0xA568 | 03 | U16 | Hz 100 | RW
525 | Six-leveloverfrequencyprotectiontime | 0xA569 | 03 | U32 | 1 | RW
526 | Level-1underfrequencyprotectionthreshold | 0xA56B | 03 | U16 | Hz 100 | RW
527 | Level-1UnderfrequencyProtectionTime | 0xA56C | 03 | U32 | 1 | RW
528 | Level-2underfrequencyprotectionthreshold | 0xA56E | 03 | U16 | Hz 100 | RW
529 | Level-2underfrequencyprotectiontime | 0xA56F | 03 | U32 | 1 | RW
530 | Level-3underfrequencyprotectionthreshold | 0xA571 | 03 | U16 | Hz 100 | RW
531 | Level-3underfrequencyprotectiontime | 0xA572 | 03 | U32 | 1 | RW
532 | Level-4underfrequencyprotectionthreshold | 0xA574 | 03 | U16 | Hz 100 | RW
533 | Level-4UnderfrequencyProtectionTime | 0xA575 | 03 | U32 | 1 | RW
534 | Level-5underfrequencyprotectionthreshold | 0xA577 | 03 | U16 | Hz 100 | RW
535 | Level-5UnderfrequencyProtectionTime | 0xA578 | 03 | U32 | 1 | RW
536 | Level-6underfrequencyprotectionthreshold | 0xA57A | 03 | U16 | Hz 100 | RW
537 | Level-6UnderfrequencyProtectionTime | 0xA57B | 03 | U32 | 1 | RW
538 | Outputimpedanceenhancementfrequencypoint | 0xA5A4 | 03 | U16 | Hz 10 | RW
539 | UnderfrequencyPowerIncreaseEffectiveDelayTime | 0xA5BD | 03 | U16 | 1 | RW
540 | Powersettings | 0xA82C | 03 | U16 | 1 | RW
541 | [ManagementSystem]TCPFrameLength | 0xA837 | 03 | U16 | 1 | RW
542 | [App]Initialpower-onflag | 0xA95F | 03 | U16 |  | RW
543 | Start-upcurrent | 0xAA71 | 03 | U16 | A 100 | RW
544 | Temperature1 | 0xAD78 | 03 | S16 | 10 | WO
545 | Restorefactorysettings. | 0xAFC8 | 03 | U16 |  | WO
546 | Accumulatedenergyyieldcorrection | 0xAFD0 | 03 | U32 | kWh 100 | WO | cumulative_energy
547 | Powerlimitforgrid-tiedsites | 0xB7E7 | 03 | S32 | W 1 | RW
548 | SettingtheAccumulatedEnergyYield | 0xB829 | 03 | U16 |  | WO | cumulative_energy
549 | Networkfrequencyband | 0xB830 | 03 | U16 |  | RW
550 | Fastpower-downenable | 0xB835 | 03 | U16 |  | RW
551 | Forwardpower | 0xB8C4 | 03 | U16 |  | RW
552 | CTratedcurrent | 0xB8C6 | 03 | U16 | A 1 | RW
553 | Maximumpowerfedtothegrid(kW) | 0xB938 | 03 | S32 | kW 1000 | RW
554 | MaximumFeedGridPower(%) | 0xB93A | 03 | S16 | 10 | RW
555 | Powerdecreaseadjustmentperiod | 0xB93C | 03 | U16 | 10 | RW
556 | PowerIncreaseThreshold | 0xB93E | 03 | U32 | kW 1000 | RW
557 | Activepowerlimitforfailprotection[%][lowprecision] | 0xB940 | 03 | S16 | 10 | RW
558 | targetpowerfactor | 0xB944 | 03 | S16 | 1000 | RW
559 | Reactivepoweradjustmentperiod | 0xB945 | 03 | U16 | 10 | RW
560 | Failureprotectionreactivepowerlimit[PF] | 0xB948 | 03 | S16 | 1000 | RW
561 | Powerplant DCcapacity | 0xB94B | 03 | U32 | kW 1000 | RW
562 | Feedingpowerover-thresholdprotectionshutdown | 0xBB4E | 03 | U16 |  | RW

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)