## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Senergy
프로토콜 버전
설비 타입 | inverter
MPPT | 9
String | 24
String 모니터링 | Yes
IV Scan | Yes
IV Data Points | 64
IV Trackers | 9
원본 파일 | Senergy Modbus Protocol Map(260402).xlsx
추출 일시 | 2026-04-03 16:03
H01 매칭 | 60/60
DER 매칭 | 33/33
추출 레지스터 | 317
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Flash / Update (펌웨어 업데이트 중) | 0x0006 |  | U16 |  | RO
2 | INNER_TEMP | 0x101C |  | S16 | 1 | RO | temperature | Inner Temperature
3 | Total Energy | 0x1021 |  | U32 | kWh | RO | cumulative_energy
4 | Total generation time | 0x1023 |  | U32 |  | RO
5 | Decimals of total energy | 0x104C |  | U16 | Wh | RO | cumulative_energy_low | Relate to 0x1021, if total energy is 220.836kWh, then 0x104C is 836Wh
6 | Device Model name | 0x1A00 |  | STRINGING |  | RO |  | Ex.：PV 30KTL
7 | Device Serial number | 0x1A10 |  | STRINGING |  | RO |  | Ex.：1234-123456789
8 | Master firmware version | 0x1A1C |  | STRINGING |  | RO |  | Ex.：123456
9 | Slave firmware version | 0x1A26 |  | STRINGING |  | RO |  | Ex.：123456
10 | MPPT_COUNT | 0x1A3B |  | U16 |  | RO |  | MPPT Number ¦ Ex.：1=1 MPPT
11 | Nominal Voltage | 0x1A44 |  | U16 | V 0.1 | RO |  | Ex.：2200 = 220VFor CN (NB/T 32004) regulation code (0x5101=0x0E), the unit is 10ms. Other regulation codes use 1ms.
12 | Nominal Frequency | 0x1A45 |  | U16 | Hz 0.01 | RO |  | Ex.：5000 = 50HzOnly support for 3 phase model (0x1A48 = 3).
13 | Nominal Active Power (Low word) | 0x1A46 |  | U16 | W 1 | RO |  | Ex.：1500 = 1500W
14 | Grid Phase Number | 0x1A48 |  | U16 |  | RO |  | 1=single phase2=split phase3=three phases
15 | Nominal Active Power (High word) | 0x1A4E |  | U16 | W 1 | RO |  | Ex.：1 = (1*65536)W
16 | EMS Firmware Version | 0x1A60 |  | STRINGING |  | RO |  | Ex.：123456
17 | LCD firmware version | 0x1A8E |  | STRINGING |  | RO |  | Ex.：123456
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Off-Grid (독립 운전) | 0x0004 |  | U16 |  | RO
2 | Derating (출력 제한 운전 중) | 0x0007 |  | U16 |  | RO
3 | Shutdown mode | 0x0009 |  | U16 |  | RO
4 | Inverter Mode | 0x101D |  | U16 |  | RO | inverter_status | Inverter Mode Table
5 | DER-AVM digital meter connect status | 0x1210 |  | U16 |  | RO |  | 0: disconnected1: connected
6 | DER-AVM mode | 0x1211 |  | U16 |  | RW |  | 0: self control1: DER-AVM control
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Fault / Alarm (고장 발생) | 0x0005 |  | U16 |  | RO
2 | Error Code1 | 0x101E |  | U16 |  | RO | alarm1 | Error Code Table 1
3 | Error Code2 | 0x101F |  | U16 |  | RO | alarm2 | Error Code Table 2
4 | Error Code3 | 0x1020 |  | U16 |  | RO | alarm3 | Error Code Table 3
5 | EEPROM default | 0x6006 |  | U16 |  | RW |  | [0, 1]0: EEPROM setting NOT to default1: EEPROM setting to default

## 2_H01
H01 모니터링 매칭 — 60/60
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x1048 | PV total input power | U32 | W | 0.1
13 | cumulative_energy | PDF | O | 0x1306 | Accumulated energy of import | U32 | Wh | 10
14 | cumulative_energy_low | PDF | O | 0x104C | Decimals of total energy | U16 | Wh
15 | status | PDF | O | 0x101D | Inverter Mode | U16 |  |  | 1=L1 Voltage, 10=L3 Current, 11=L3 Power, 12=L3 Frequency, 13=MPPT1 Voltage, 14=MPPT1 Current... (+28)
16 | alarm1 | PDF | O | 0x101E | Error Code1 | U16
17 | alarm2 | PDF | O | 0x101F | Error Code2 | U16
18 | alarm3 | PDF | O | 0x1020 | Error Code3 | U16
19 | mppt1_voltage | PDF | O | 0x1010 | MPPT1 Voltage | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x1011 | MPPT1 Current | S16 | A | 0.01
21 | mppt2_voltage | PDF | O | 0x1014 | MPPT2 Voltage | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x1015 | MPPT2 Current | S16 | A | 0.01
23 | mppt3_voltage | PDF | O | 0x1018 | MPPT3 Voltage | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x1019 | MPPT3 Current | S16 | A | 0.01
25 | mppt4_voltage | PDF | O | 0x103E | MPPT4 Voltage | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x103F | MPPT4 Current | S16 | A | 0.01
27 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
29 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
31 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
33 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
35 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
36 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
37 | string1_current | PDF | O | 0x1051 | String1 input current | S16 | A | 0.01
38 | string2_current | PDF | O | 0x1053 | String2 input current | S16 | A | 0.01
39 | string3_current | PDF | O | 0x1055 | String3 input current | S16 | A | 0.01
40 | string4_current | PDF | O | 0x1057 | String4 input current | S16 | A | 0.01
41 | string5_current | PDF | O | 0x1059 | String5 input current | S16 | A | 0.01
42 | string6_current | PDF | O | 0x105B | String6 input current | S16 | A | 0.01
43 | string7_current | PDF | O | 0x105D | String7 input current | S16 | A | 0.01
44 | string8_current | PDF | O | 0x105F | String8 input current | S16 | A | 0.01
45 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
46 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
47 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
48 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
49 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
50 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
51 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
52 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
53 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
54 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
55 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
56 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
57 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
58 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
59 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
60 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 9ch / String 24ch
MPPT 채널 수 | 9
String 채널 수 | 24
String 모니터링 | Yes
MPPT 채널 H01 매칭 (18개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x1010 | MPPT1 Voltage | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x1011 | MPPT1 Current | S16 | A | 0.01
3 | mppt2_voltage | PDF | O | 0x1014 | MPPT2 Voltage | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x1015 | MPPT2 Current | S16 | A | 0.01
5 | mppt3_voltage | PDF | O | 0x1018 | MPPT3 Voltage | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x1019 | MPPT3 Current | S16 | A | 0.01
7 | mppt4_voltage | PDF | O | 0x103E | MPPT4 Voltage | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x103F | MPPT4 Current | S16 | A | 0.01
9 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
11 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
13 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
15 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
17 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
18 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
String 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x1051 | String1 input current | S16 | A | 0.01
2 | string2_current | PDF | O | 0x1053 | String2 input current | S16 | A | 0.01
3 | string3_current | PDF | O | 0x1055 | String3 input current | S16 | A | 0.01
4 | string4_current | PDF | O | 0x1057 | String4 input current | S16 | A | 0.01
5 | string5_current | PDF | O | 0x1059 | String5 input current | S16 | A | 0.01
6 | string6_current | PDF | O | 0x105B | String6 input current | S16 | A | 0.01
7 | string7_current | PDF | O | 0x105D | String7 input current | S16 | A | 0.01
8 | string8_current | PDF | O | 0x105F | String8 input current | S16 | A | 0.01
9 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
10 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
11 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
12 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
13 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
14 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
15 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
16 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
17 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
18 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
19 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
20 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
21 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
22 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
23 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
24 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01
MONITORING 전체 (185개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Wait / Initial (대기/초기화) | 0x0000 |  | U16 |  | RO
2 | Standby (스탠바이) | 0x0001 |  | U16 |  | RO
3 | Initialization (초기화 중) | 0x0002 |  | U16 |  | RO
4 | On-Grid / Normal (정상 발전 / 계통 연계) | 0x0003 |  | U16 |  | RO
5 | Grid over current, [0,1] | 0x0008 |  | U16 |  | RO
6 | EN50438 (유럽 공통) | 0x000A |  | U16 |  | RO
7 | Self control(outage), [0,1] | 0x000B |  | U16 |  | RO
8 | Leakage current abnormal, [0,1] | 0x000C |  | U16 |  | RO
9 | Register value | 0x0026 |  | U16 |  | RO
10 | L1 Voltage | 0x1001 |  | U16 | V 0.1 | RO | r_voltage
11 | L1 Current | 0x1002 |  | U16 | A 0.01 | RO | r_current
12 | L1 Power | 0x1003 |  | S32 | W 0.1 | RO
13 | L1 Frequency | 0x1005 |  | U16 | Hz 0.01 | RO | frequency
14 | L2 Voltage | 0x1006 |  | U16 | V 0.1 | RO | s_voltage
15 | L2 Current | 0x1007 |  | U16 | A 0.01 | RO | s_current
16 | L2 Power | 0x1008 |  | S32 | W 0.1 | RO
17 | L2 Frequency | 0x100A |  | U16 | Hz 0.01 | RO | frequency
18 | L3 Voltage | 0x100B |  | U16 | V 0.1 | RO | t_voltage
19 | L3 Current | 0x100C |  | U16 | A 0.01 | RO | t_current
20 | L3 Power | 0x100D |  | S32 | W 0.1 | RO
21 | L3 Frequency | 0x100F |  | U16 | Hz 0.01 | RO | frequency
22 | MPPT1 Voltage | 0x1010 |  | U16 | V 0.1 | RO | mppt1_voltage
23 | MPPT1 Current | 0x1011 |  | S16 | A 0.01 | RO | mppt1_current
24 | MPPT1 Power | 0x1012 |  | U32 | W 0.1 | RO | mppt1_power
25 | MPPT2 Voltage | 0x1014 |  | U16 | V 0.1 | RO | mppt2_voltage
26 | MPPT2 Current | 0x1015 |  | S16 | A 0.01 | RO | mppt2_current
27 | MPPT2 Power | 0x1016 |  | U32 | W 0.1 | RO | mppt2_power
28 | MPPT3 Voltage | 0x1018 |  | U16 | V 0.1 | RO | mppt3_voltage
29 | MPPT3 Current | 0x1019 |  | S16 | A 0.01 | RO | mppt3_current
30 | MPPT3 Power | 0x101A |  | U32 | W 0.1 | RO | mppt3_power
31 | DAILY_ENERGY | 0x1027 |  | U32 | Wh | RO | daily_energy
32 | Grid total Active Power | 0x1037 |  | S32 | W 0.1 | RO | ac_power
33 | Grid total Reactive Power | 0x1039 |  | S32 | 0.1 | RO | ac_power
34 | PV Today Peak Power | 0x103B |  | S32 | W 0.1 | RO
35 | Power Factor | 0x103D |  | S16 | 0.001 | RO | power_factor
36 | MPPT4 Voltage | 0x103E |  | U16 | V 0.1 | RO | mppt4_voltage
37 | MPPT4 Current | 0x103F |  | S16 | A 0.01 | RO | mppt4_current
38 | MPPT4 Power | 0x1040 |  | U32 | W 0.1 | RO | mppt4_power
39 | PV total input power | 0x1048 |  | U32 | W 0.1 | RO | pv_power
40 | String1 input voltage | 0x1050 |  | U16 | V 0.1 | RO | string1_voltage
41 | String1 input current | 0x1051 |  | S16 | A 0.01 | RO | string1_current
42 | String2 input voltage | 0x1052 |  | U16 | V 0.1 | RO | string2_voltage
43 | String2 input current | 0x1053 |  | S16 | A 0.01 | RO | string2_current
44 | String3 input voltage | 0x1054 |  | U16 | V 0.1 | RO | string3_voltage
45 | String3 input current | 0x1055 |  | S16 | A 0.01 | RO | string3_current
46 | String4 input voltage | 0x1056 |  | U16 | V 0.1 | RO | string4_voltage
47 | String4 input current | 0x1057 |  | S16 | A 0.01 | RO | string4_current
48 | String5 input voltage | 0x1058 |  | U16 | V 0.1 | RO | string5_voltage
49 | String5 input current | 0x1059 |  | S16 | A 0.01 | RO | string5_current
50 | String6 input voltage | 0x105A |  | U16 | V 0.1 | RO | string6_voltage
51 | String6 input current | 0x105B |  | S16 | A 0.01 | RO | string6_current
52 | String7 input voltage | 0x105C |  | U16 | V 0.1 | RO | string7_voltage
53 | String7 input current | 0x105D |  | S16 | A 0.01 | RO | string7_current
54 | String8 input voltage | 0x105E |  | U16 | V 0.1 | RO | string8_voltage
55 | String8 input current | 0x105F |  | S16 | A 0.01 | RO | string8_current
56 | String9 input voltage | 0x1060 |  | U16 | V 0.1 | RO | string9_voltage
57 | String9 input current | 0x1061 |  | S16 | A 0.01 | RO | string9_current
58 | String10 input voltage | 0x1062 |  | U16 | V 0.1 | RO | string10_voltage
59 | String10 input current | 0x1063 |  | S16 | A 0.01 | RO | string10_current
60 | String11 input voltage | 0x1064 |  | U16 | V 0.1 | RO | string11_voltage
61 | String11 input current | 0x1065 |  | S16 | A 0.01 | RO | string11_current
62 | String12 input voltage | 0x1066 |  | U16 | V 0.1 | RO | string12_voltage
63 | String12 input current | 0x1067 |  | S16 | A 0.01 | RO | string12_current
64 | String13 input voltage | 0x1068 |  | U16 | V 0.1 | RO | string13_voltage
65 | String13 input current | 0x1069 |  | S16 | A 0.01 | RO | string13_current
66 | String14 input voltage | 0x106A |  | U16 | V 0.1 | RO | string14_voltage
67 | String14 input current | 0x106B |  | S16 | A 0.01 | RO | string14_current
68 | String15 input voltage | 0x106C |  | U16 | V 0.1 | RO | string15_voltage
69 | String15 input current | 0x106D |  | S16 | A 0.01 | RO | string15_current
70 | String16 input voltage | 0x106E |  | U16 | V 0.1 | RO | string16_voltage
71 | String16 input current | 0x106F |  | S16 | A 0.01 | RO | string16_current
72 | String17 input voltage | 0x1070 |  | U16 | V 0.1 | RO | string17_voltage
73 | String17 input current | 0x1071 |  | S16 | A 0.01 | RO | string17_current
74 | String18 input voltage | 0x1072 |  | U16 | V 0.1 | RO | string18_voltage
75 | String18 input current | 0x1073 |  | S16 | A 0.01 | RO | string18_current
76 | String19 input voltage | 0x1074 |  | U16 | V 0.1 | RO | string19_voltage
77 | String19 input current | 0x1075 |  | S16 | A 0.01 | RO | string19_current
78 | String20 input voltage | 0x1076 |  | U16 | V 0.1 | RO | string20_voltage
79 | String20 input current | 0x1077 |  | S16 | A 0.01 | RO | string20_current
80 | String21 input voltage | 0x1078 |  | U16 | V 0.1 | RO | string21_voltage
81 | String21 input current | 0x1079 |  | S16 | A 0.01 | RO | string21_current
82 | String22 input voltage | 0x107A |  | U16 | V 0.1 | RO | string22_voltage
83 | String22 input current | 0x107B |  | S16 | A 0.01 | RO | string22_current
84 | String23 input voltage | 0x107C |  | U16 | V 0.1 | RO | string23_voltage
85 | String23 input current | 0x107D |  | S16 | A 0.01 | RO | string23_current
86 | String24 input voltage | 0x107E |  | U16 | V 0.1 | RO | string24_voltage
87 | String24 input current | 0x107F |  | S16 | A 0.01 | RO | string24_current
88 | MPPT5 Voltage | 0x1080 |  | U16 | V 0.1 | RO | mppt5_voltage
89 | MPPT5 Current | 0x1081 |  | S16 | A 0.01 | RO | mppt5_current
90 | MPPT5 Power | 0x1082 |  | U32 | W 0.1 | RO | mppt5_power
91 | MPPT6 Voltage | 0x1084 |  | U16 | V 0.1 | RO | mppt6_voltage
92 | MPPT6 Current | 0x1085 |  | S16 | A 0.01 | RO | mppt6_current
93 | MPPT6 Power | 0x1086 |  | U32 | W 0.1 | RO | mppt6_power
94 | MPPT7 Voltage | 0x1088 |  | U16 | V 0.1 | RO | mppt7_voltage
95 | MPPT7 Current | 0x1089 |  | S16 | A 0.01 | RO | mppt7_current
96 | MPPT7 Power | 0x108A |  | U32 | W 0.1 | RO | mppt7_power
97 | MPPT8 Voltage | 0x108C |  | U16 | V 0.1 | RO | mppt8_voltage
98 | MPPT8 Current | 0x108D |  | S16 | A 0.01 | RO | mppt8_current
99 | MPPT8 Power | 0x108E |  | U32 | W 0.1 | RO | mppt8_power
100 | MPPT9 Voltage | 0x1090 |  | U16 | V 0.1 | RO | mppt9_voltage
101 | MPPT9 Current | 0x1091 |  | S16 | A 0.01 | RO | mppt9_current
102 | MPPT9 Power | 0x1092 |  | U32 | W 0.1 | RO | mppt9_power
103 | External fan speed duty percentage | 0x120C |  | U16 | 1 | RO
104 | L1-N phase voltage (AC) | 0x1220 |  | U16 | V 0.1 | RO
105 | L2-N phase voltage (AC) | 0x1221 |  | U16 | V 0.1 | RO
106 | L3-N phase voltage (AC) | 0x1222 |  | U16 | V 0.1 | RO
107 | L1-L2 phase voltage (AC) | 0x1223 |  | U16 | V 0.1 | RO
108 | L2-L3 phase voltage (AC) | 0x1224 |  | U16 | V 0.1 | RO
109 | L3-L1 phase voltage (AC) | 0x1225 |  | U16 | V 0.1 | RO
110 | Q (Reference Output reactive power) | 0x1226 |  | S16 | 0.1 | RO
111 | L1 watt of grid | 0x1300 |  | S32 | W 0.1 | RO
112 | L2 watt of grid | 0x1302 |  | S32 | W 0.1 | RO
113 | L3 watt of grid | 0x1304 |  | S32 | W 0.1 | RO
114 | Accumulated energy of import | 0x1306 |  | U32 | Wh 10 | RO | cumulative_energy
115 | Accumulated energy of export | 0x1308 |  | U32 | Wh 10 | RO | cumulative_energy
116 | L1 watt of load | 0x130A |  | U32 | W 0.1 | RO
117 | L2 watt of load | 0x130C |  | U32 | W 0.1 | RO
118 | L3 watt of load | 0x130E |  | U32 | W 0.1 | RO
119 | Accumulated energy of load | 0x1310 |  | U32 | Wh 10 | RO | cumulative_energy
120 | L1-N phase voltage of grid | 0x131A |  | U16 | V 0.1 | RO
121 | L2-N phase voltage of grid | 0x131B |  | U16 | V 0.1 | RO
122 | L3-N phase voltage of grid | 0x131C |  | U16 | V 0.1 | RO
123 | L1 current of grid | 0x131D |  | S32 | A 0.01 | RO
124 | L2 current of grid | 0x131F |  | S32 | A 0.01 | RO
125 | L3 current of grid | 0x1321 |  | S32 | A 0.01 | RO
126 | L1-N phase voltage of load | 0x1323 |  | U16 | V 0.1 | RO
127 | L2-N phase voltage of load | 0x1324 |  | U16 | V 0.1 | RO
128 | L3-N phase voltage of load | 0x1325 |  | U16 | V 0.1 | RO
129 | L1 current of load | 0x1326 |  | S32 | A 0.01 | RO
130 | L2 current of load | 0x1328 |  | S32 | A 0.01 | RO
131 | L3 current of load | 0x132A |  | S32 | A 0.01 | RO
132 | Today import Energy | 0x1332 |  | U32 | Wh 10 | RO
133 | Today export Energy | 0x1334 |  | U32 | Wh 10 | RO
134 | Today load Energy | 0x1336 |  | U32 | Wh 10 | RO
135 | Frequency of grid | 0x1338 |  | U16 | Hz 0.01 | RO
136 | Power flow direction | 0x30B2 |  | U16 |  | RW
137 | Maximum feed in grid power | 0x30B9 |  | U32 | W | RW
138 | Clear the EEPROM history energy record | 0x6009 |  | U16 |  | RW
139 | Tracker 1 voltage | 0x8000 |  | U16 | V 0.1 | RO
140 | String 1-1 current | 0x8040 |  | S16 | A 0.01 | RO | string_current
141 | String 1-2 current | 0x8080 |  | S16 | A 0.01 | RO | string_current
142 | String 1-3 current | 0x80C0 |  | S16 | A 0.01 | RO | string_current
143 | String 1-4 current | 0x8100 |  | S16 | A 0.01 | RO | string_current
144 | Tracker 2 voltage | 0x8140 |  | U16 | V 0.1 | RO
145 | String 2-1 current | 0x8180 |  | S16 | A 0.01 | RO | string_current
146 | String 2-2 current | 0x81C0 |  | S16 | A 0.01 | RO | string_current
147 | String 2-3 current | 0x8200 |  | S16 | A 0.01 | RO | string_current
148 | String 2-4 current | 0x8240 |  | S16 | A 0.01 | RO | string_current
149 | Tracker 3 voltage | 0x8280 |  | U16 | V 0.1 | RO
150 | String 3-1 current | 0x82C0 |  | S16 | A 0.01 | RO | string_current
151 | String 3-2 current | 0x8300 |  | S16 | A 0.01 | RO | string_current
152 | String 3-3 current | 0x8340 |  | S16 | A 0.01 | RO | string_current
153 | String 3-4 current | 0x8380 |  | S16 | A 0.01 | RO | string_current
154 | Tracker 4 voltage | 0x83C0 |  | U16 | V 0.1 | RO
155 | String 4-1 current | 0x8400 |  | S16 | A 0.01 | RO | string_current
156 | String 4-2 current | 0x8440 |  | S16 | A 0.01 | RO | string_current
157 | String 4-3 current | 0x8480 |  | S16 | A 0.01 | RO | string_current
158 | String 4-4 current | 0x84C0 |  | S16 | A 0.01 | RO | string_current
159 | Tracker 5 voltage | 0x8500 |  | U16 | V 0.1 | RO
160 | String 5-1 current | 0x8540 |  | S16 | A 0.01 | RO | string_current
161 | String 5-2 current | 0x8580 |  | S16 | A 0.01 | RO | string_current
162 | String 5-3 current | 0x85C0 |  | S16 | A 0.01 | RO | string_current
163 | String 5-4 current | 0x8600 |  | S16 | A 0.01 | RO | string_current
164 | Tracker 6 voltage | 0x8640 |  | U16 | V 0.1 | RO
165 | String 6-1 current | 0x8680 |  | S16 | A 0.01 | RO | string_current
166 | String 6-2 current | 0x86C0 |  | S16 | A 0.01 | RO | string_current
167 | String 6-3 current | 0x8700 |  | S16 | A 0.01 | RO | string_current
168 | String 6-4 current | 0x8740 |  | S16 | A 0.01 | RO | string_current
169 | Tracker 7 voltage | 0x8780 |  | U16 | V 0.1 | RO
170 | String 7-1 current | 0x87C0 |  | S16 | A 0.01 | RO | string_current
171 | String 7-2 current | 0x8800 |  | S16 | A 0.01 | RO | string_current
172 | String 7-3 current | 0x8840 |  | S16 | A 0.01 | RO | string_current
173 | String 7-4 current | 0x8880 |  | S16 | A 0.01 | RO | string_current
174 | Tracker 8 voltage | 0x88C0 |  | U16 | V 0.1 | RO
175 | String 8-1 current | 0x8900 |  | S16 | A 0.01 | RO | string_current
176 | String 8-2 current | 0x8940 |  | S16 | A 0.01 | RO | string_current
177 | String 8-3 current | 0x8980 |  | S16 | A 0.01 | RO | string_current
178 | String 8-4 current | 0x89C0 |  | S16 | A 0.01 | RO | string_current
179 | Tracker 9 voltage | 0x8A00 |  | U16 | V 0.1 | RO
180 | String 9-1 current | 0x8A40 |  | S16 | A 0.01 | RO | string_current
181 | String 9-2 current | 0x8A80 |  | S16 | A 0.01 | RO | string_current
182 | String 9-3 current | 0x8AC0 |  | S16 | A 0.01 | RO | string_current
183 | String 9-4 current | 0x8B00 |  | S16 | A 0.01 | RO | string_current
184 | history log 0 | 0xB600 |  | U16 |  | RO
185 | history log 127 | 0xB77D |  | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## 5_IV
IV Scan 매핑 — data_points=64
IV Scan Command | 0x600D
Data Points | 64
Trackers | 9
Strings/Tracker | 4
IV Scan Command
Name | Address | Type | R/W | Description
IV_CURVE_SCAN | 0x600D | U16 | RW | W: 0=Stop, 1=Start / R: 0=Idle, 1=Running, 2=Finished
IV Data 레지스터 매핑
No | Type | Name | Address | Regs | Data Type | Scale
1 | Tracker Voltage | Tracker 1 voltage | 0x8000 | 64 | U16 | 0.1V
2 | String Current | String 1-1 current | 0x8040 | 64 | S16 | 0.01A
3 | String Current | String 1-2 current | 0x8080 | 64 | S16 | 0.01A
4 | String Current | String 1-3 current | 0x80C0 | 64 | S16 | 0.01A
5 | String Current | String 1-4 current | 0x8100 | 64 | S16 | 0.01A
6 | Tracker Voltage | Tracker 2 voltage | 0x8140 | 64 | U16 | 0.1V
7 | String Current | String 2-1 current | 0x8180 | 64 | S16 | 0.01A
8 | String Current | String 2-2 current | 0x81C0 | 64 | S16 | 0.01A
9 | String Current | String 2-3 current | 0x8200 | 64 | S16 | 0.01A
10 | String Current | String 2-4 current | 0x8240 | 64 | S16 | 0.01A
11 | Tracker Voltage | Tracker 3 voltage | 0x8280 | 64 | U16 | 0.1V
12 | String Current | String 3-1 current | 0x82C0 | 64 | S16 | 0.01A
13 | String Current | String 3-2 current | 0x8300 | 64 | S16 | 0.01A
14 | String Current | String 3-3 current | 0x8340 | 64 | S16 | 0.01A
15 | String Current | String 3-4 current | 0x8380 | 64 | S16 | 0.01A
16 | Tracker Voltage | Tracker 4 voltage | 0x83C0 | 64 | U16 | 0.1V
17 | String Current | String 4-1 current | 0x8400 | 64 | S16 | 0.01A
18 | String Current | String 4-2 current | 0x8440 | 64 | S16 | 0.01A
19 | String Current | String 4-3 current | 0x8480 | 64 | S16 | 0.01A
20 | String Current | String 4-4 current | 0x84C0 | 64 | S16 | 0.01A
21 | Tracker Voltage | Tracker 5 voltage | 0x8500 | 64 | U16 | 0.1V
22 | String Current | String 5-1 current | 0x8540 | 64 | S16 | 0.01A
23 | String Current | String 5-2 current | 0x8580 | 64 | S16 | 0.01A
24 | String Current | String 5-3 current | 0x85C0 | 64 | S16 | 0.01A
25 | String Current | String 5-4 current | 0x8600 | 64 | S16 | 0.01A
26 | Tracker Voltage | Tracker 6 voltage | 0x8640 | 64 | U16 | 0.1V
27 | String Current | String 6-1 current | 0x8680 | 64 | S16 | 0.01A
28 | String Current | String 6-2 current | 0x86C0 | 64 | S16 | 0.01A
29 | String Current | String 6-3 current | 0x8700 | 64 | S16 | 0.01A
30 | String Current | String 6-4 current | 0x8740 | 64 | S16 | 0.01A
31 | Tracker Voltage | Tracker 7 voltage | 0x8780 | 64 | U16 | 0.1V
32 | String Current | String 7-1 current | 0x87C0 | 64 | S16 | 0.01A
33 | String Current | String 7-2 current | 0x8800 | 64 | S16 | 0.01A
34 | String Current | String 7-3 current | 0x8840 | 64 | S16 | 0.01A
35 | String Current | String 7-4 current | 0x8880 | 64 | S16 | 0.01A
36 | Tracker Voltage | Tracker 8 voltage | 0x88C0 | 64 | U16 | 0.1V
37 | String Current | String 8-1 current | 0x8900 | 64 | S16 | 0.01A
38 | String Current | String 8-2 current | 0x8940 | 64 | S16 | 0.01A
39 | String Current | String 8-3 current | 0x8980 | 64 | S16 | 0.01A
40 | String Current | String 8-4 current | 0x89C0 | 64 | S16 | 0.01A
41 | Tracker Voltage | Tracker 9 voltage | 0x8A00 | 64 | U16 | 0.1V
42 | String Current | String 9-1 current | 0x8A40 | 64 | S16 | 0.01A
43 | String Current | String 9-2 current | 0x8A80 | 64 | S16 | 0.01A
44 | String Current | String 9-3 current | 0x8AC0 | 64 | S16 | 0.01A
45 | String Current | String 9-4 current | 0x8B00 | 64 | S16 | 0.01A