## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Solarize
프로토콜 버전
설비 타입 | inverter
MPPT | 9
String | 24
String 모니터링 | Yes
IV Scan | Yes
IV Data Points | 64
IV Trackers | 9
원본 파일 | Solarize Modbus Protocol-Korea-V1.2.4.pdf
추출 일시 | 2026-04-03 16:03
H01 매칭 | 60/60
DER 매칭 | 33/33
추출 레지스터 | 315
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INNER_TEMP | 0x101C | 03 | S16 | °C 1 | RO | temperature | Inner Temperature
2 | Total Energy | 0x1021 | 03 | U32 | kWh | RO | cumulative_energy
3 | Total generation time | 0x1023 | 03 | U32 |  | RO
4 | Decimals of total energy | 0x104C | 03 | U16 |  | RO | cumulative_energy_low | Wh
5 | Device Model name | 0x1A00 | 03 | STRINGING |  | RO |  | Ex.：PV 30KTL
6 | Device Serial number | 0x1A10 | 03 | STRINGING |  | RO |  | Ex.：1234-123456789
7 | Master firmware version | 0x1A1C | 03 | STRINGING |  | RO |  | Ex.：123456
8 | Slave firmware version | 0x1A26 | 03 | STRINGING |  | RO |  | Ex.：123456
9 | MPPT_COUNT | 0x1A3B | 03 | U16 |  | RO |  | MPPT Number ¦ Ex.：1=1 MPPT
10 | Nominal Voltage | 0x1A44 | 03 | U16 |  | RO |  | Ex.：2200 = 220V
11 | Nominal Frequency | 0x1A45 | 03 | U16 |  | RO |  | Ex.：5000 = 50Hz
12 | Nominal Active Power(Low word) | 0x1A46 | 03 | U16 | W 1 | RO |  | Ex.：1500 = 1500W
13 | Grid Phase Number | 0x1A48 | 03 | U16 |  | RO |  | 1=single phase2=split phase3=three phases
14 | Nominal Active Power(High word) | 0x1A4E | 03 | U16 | W 1 | RO |  | Ex.：1 = (1*65536)W
15 | EMS Firmware Version | 0x1A60 | 03 | STRINGING |  | RO |  | Ex.：123456
16 | LCD firmware version | 0x1A8E | 03 | STRINGING |  | RO |  | Ex.：123456
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Inverter Mode | 0x101D | 03 | U16 |  | RO | inverter_status | Inverter Mode Table
2 | DER-AVM digital meterconnect status | 0x1210 | 03 | U16 |  | RO
3 | DER-AVM mode | 0x1211 | 03 | U16 |  | RW |  | 0: self control1: DER-AVM control
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | GFCI abnormal | 0x0004 | 03 | U16 |  | RO
2 | Internal communication error | 0x000A | 03 | U16 |  | RO
3 | Internal storage error | 0x000C | 03 | U16 |  | RO
4 | Inverter abnormal | 0x000E | 03 | U16 |  | RO
5 | Boost abnormal | 0x000F | 03 | U16 |  | RO
6 | Error Code1 | 0x101E | 03 | U16 |  | RO | alarm1 | Error Code Table 1
7 | Error Code2 | 0x101F | 03 | U16 |  | RO | alarm2 | Error Code Table 2
8 | Error Code3 | 0x1020 | 03 | U16 |  | RO | alarm3 | Error Code Table 3
9 | EEPROM default | 0x6006 | 03 | U16 |  | RW

## 2_H01
H01 모니터링 매칭 — 60/60
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x1048 | PV total input power | U32 | W | 0.1
13 | cumulative_energy | PDF | O | 0x1306 | Accumulated energy ofimport | U32 | Wh | 10
14 | cumulative_energy_low | PDF | O | 0x104C | Decimals of total energy | U16
15 | status | PDF | O | 0x101D | Inverter Mode | U16 |  |  | 6=PV6 fuse open d, 7=PV7 fuse open d, 8=PV8 fuse open d
16 | alarm1 | PDF | O | 0x101E | Error Code1 | U16 |  |  | 0=Inverter over d, 1=Inverter relay , 2=Remote off, 3=Inverter over t, 4=GFCI abnormal, 5=PV string rever... (+10)
17 | alarm2 | PDF | O | 0x101F | Error Code2 | U16 |  |  | 136=String 1-2 curr, 137=String 1-3 curr, 138=String 1-4 curr, 139=Tracker 2 volta, 140=String 2-1 curr, 141=String 2-2 curr... (+33)
18 | alarm3 | PDF | O | 0x1020 | Error Code3 | U16
19 | mppt1_voltage | PDF | O | 0x1010 | MPPT1 Voltage | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x1011 | MPPT1 Current | S16 | A | 0.01
21 | mppt2_voltage | PDF | O | 0x1014 | MPPT2 Voltage | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x1015 | MPPT2 Current | S16 | A | 0.01
23 | mppt3_voltage | PDF | O | 0x1018 | MPPT3 Voltage | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x1019 | MPPT3 Current | S16 | A | 0.01
25 | mppt4_voltage | PDF | O | 0x103E | MPPT4 Voltage | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x103F | MPPT4 Current | S16 | A | 0.01
27 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
29 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
31 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
33 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
35 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
36 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
37 | string1_current | PDF | O | 0x1051 | String1 input current | S16 | A | 0.01
38 | string2_current | PDF | O | 0x1053 | String2 input current | S16 | A | 0.01
39 | string3_current | PDF | O | 0x1055 | String3 input current | S16 | A | 0.01
40 | string4_current | PDF | O | 0x1057 | String4 input current | S16 | A | 0.01
41 | string5_current | PDF | O | 0x1059 | String5 input current | S16 | A | 0.01
42 | string6_current | PDF | O | 0x105B | String6 input current | S16 | A | 0.01
43 | string7_current | PDF | O | 0x105D | String7 input current | S16 | A | 0.01
44 | string8_current | PDF | O | 0x105F | String8 input current | S16 | A | 0.01
45 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
46 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
47 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
48 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
49 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
50 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
51 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
52 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
53 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
54 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
55 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
56 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
57 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
58 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
59 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
60 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 9ch / String 24ch
MPPT 채널 수 | 9
String 채널 수 | 24
String 모니터링 | Yes
MPPT 채널 H01 매칭 (18개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x1010 | MPPT1 Voltage | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x1011 | MPPT1 Current | S16 | A | 0.01
3 | mppt2_voltage | PDF | O | 0x1014 | MPPT2 Voltage | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x1015 | MPPT2 Current | S16 | A | 0.01
5 | mppt3_voltage | PDF | O | 0x1018 | MPPT3 Voltage | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x1019 | MPPT3 Current | S16 | A | 0.01
7 | mppt4_voltage | PDF | O | 0x103E | MPPT4 Voltage | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x103F | MPPT4 Current | S16 | A | 0.01
9 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current | S16 | A | 0.01
11 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current | S16 | A | 0.01
13 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current | S16 | A | 0.01
15 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x108D | MPPT8 Current | S16 | A | 0.01
17 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage | U16 | V | 0.1
18 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current | S16 | A | 0.01
String 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x1051 | String1 input current | S16 | A | 0.01
2 | string2_current | PDF | O | 0x1053 | String2 input current | S16 | A | 0.01
3 | string3_current | PDF | O | 0x1055 | String3 input current | S16 | A | 0.01
4 | string4_current | PDF | O | 0x1057 | String4 input current | S16 | A | 0.01
5 | string5_current | PDF | O | 0x1059 | String5 input current | S16 | A | 0.01
6 | string6_current | PDF | O | 0x105B | String6 input current | S16 | A | 0.01
7 | string7_current | PDF | O | 0x105D | String7 input current | S16 | A | 0.01
8 | string8_current | PDF | O | 0x105F | String8 input current | S16 | A | 0.01
9 | string9_current | PDF | O | 0x1061 | String9 input current | S16 | A | 0.01
10 | string10_current | PDF | O | 0x1063 | String10 input current | S16 | A | 0.01
11 | string11_current | PDF | O | 0x1065 | String11 input current | S16 | A | 0.01
12 | string12_current | PDF | O | 0x1067 | String12 input current | S16 | A | 0.01
13 | string13_current | PDF | O | 0x1069 | String13 input current | S16 | A | 0.01
14 | string14_current | PDF | O | 0x106B | String14 input current | S16 | A | 0.01
15 | string15_current | PDF | O | 0x106D | String15 input current | S16 | A | 0.01
16 | string16_current | PDF | O | 0x106F | String16 input current | S16 | A | 0.01
17 | string17_current | PDF | O | 0x1071 | String17 input current | S16 | A | 0.01
18 | string18_current | PDF | O | 0x1073 | String18 input current | S16 | A | 0.01
19 | string19_current | PDF | O | 0x1075 | String19 input current | S16 | A | 0.01
20 | string20_current | PDF | O | 0x1077 | String20 input current | S16 | A | 0.01
21 | string21_current | PDF | O | 0x1079 | String21 input current | S16 | A | 0.01
22 | string22_current | PDF | O | 0x107B | String22 input current | S16 | A | 0.01
23 | string23_current | PDF | O | 0x107D | String23 input current | S16 | A | 0.01
24 | string24_current | PDF | O | 0x107F | String24 input current | S16 | A | 0.01
MONITORING 전체 (180개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Broadcast address | 0x0000 | 03 | U16 |  | RO
2 | Start bit | 0x0001 | 03 | U16 |  | RO
3 | Register number | 0x0002 | 03 | U16 |  | RO
4 | Read register address | 0x0003 | 03 | U16 |  | RO
5 | PV string reverse | 0x0005 | 03 | STRINGING |  | RO
6 | 0x07 | 0x0007 | 03 | U16 |  | RO
7 | Dc-link over voltage | 0x0009 | 03 | U16 |  | RO
8 | Software incompatibility | 0x000B | 03 | U16 |  | RO
9 | Data inconsistency | 0x000D | 03 | U16 |  | RO
10 | Byte number | 0x0026 | 03 | U16 |  | RO
11 | L1 Voltage | 0x1001 | 03 | U16 | V 0.1 | RO | r_voltage
12 | L1 Current | 0x1002 | 03 | U16 | A 0.01 | RO | r_current
13 | L1 Power | 0x1003 | 03 | S32 | W 0.1 | RO
14 | L1 Frequency | 0x1005 | 03 | U16 | Hz 0.01 | RO | frequency
15 | L2 Voltage | 0x1006 | 03 | U16 | V 0.1 | RO | s_voltage
16 | L2 Current | 0x1007 | 03 | U16 | A 0.01 | RO | s_current
17 | L2 Power | 0x1008 | 03 | S32 | W 0.1 | RO
18 | L2 Frequency | 0x100A | 03 | U16 | Hz 0.01 | RO | frequency
19 | L3 Voltage | 0x100B | 03 | U16 | V 0.1 | RO | t_voltage
20 | L3 Current | 0x100C | 03 | U16 | A 0.01 | RO | t_current
21 | L3 Power | 0x100D | 03 | S32 | W 0.1 | RO
22 | L3 Frequency | 0x100F | 03 | U16 | Hz 0.01 | RO | frequency
23 | MPPT1 Voltage | 0x1010 | 03 | U16 | V 0.1 | RO | mppt1_voltage
24 | MPPT1 Current | 0x1011 | 03 | S16 | A 0.01 | RO | mppt1_current
25 | MPPT1 Power | 0x1012 | 03 | U32 | W 0.1 | RO | mppt1_power
26 | MPPT2 Voltage | 0x1014 | 03 | U16 | V 0.1 | RO | mppt2_voltage
27 | MPPT2 Current | 0x1015 | 03 | S16 | A 0.01 | RO | mppt2_current
28 | MPPT2 Power | 0x1016 | 03 | U32 | W 0.1 | RO | mppt2_power
29 | MPPT3 Voltage | 0x1018 | 03 | U16 | V 0.1 | RO | mppt3_voltage
30 | MPPT3 Current | 0x1019 | 03 | S16 | A 0.01 | RO | mppt3_current
31 | MPPT3 Power | 0x101A | 03 | U32 | W 0.1 | RO | mppt3_power
32 | DAILY_ENERGY | 0x1027 | 03 | U32 | Wh | RO | daily_energy
33 | Grid total Active Power | 0x1037 | 03 | S32 | W 0.1 | RO | ac_power
34 | Grid total Reactive Power | 0x1039 | 03 | S32 |  | RO | ac_power
35 | PV Today Peak Power | 0x103B | 03 | S32 | W 0.1 | RO
36 | Power Factor | 0x103D | 03 | S16 |  | RO | power_factor
37 | MPPT4 Voltage | 0x103E | 03 | U16 | V 0.1 | RO | mppt4_voltage
38 | MPPT4 Current | 0x103F | 03 | S16 | A 0.01 | RO | mppt4_current
39 | MPPT4 Power | 0x1040 | 03 | U32 | W 0.1 | RO | mppt4_power
40 | PV total input power | 0x1048 | 03 | U32 | W 0.1 | RO | pv_power
41 | String1 input voltage | 0x1050 | 03 | U16 | V 0.1 | RO | string1_voltage
42 | String1 input current | 0x1051 | 03 | S16 | A 0.01 | RO | string1_current
43 | String2 input voltage | 0x1052 | 03 | U16 | V 0.1 | RO | string2_voltage
44 | String2 input current | 0x1053 | 03 | S16 | A 0.01 | RO | string2_current
45 | String3 input voltage | 0x1054 | 03 | U16 | V 0.1 | RO | string3_voltage
46 | String3 input current | 0x1055 | 03 | S16 | A 0.01 | RO | string3_current
47 | String4 input voltage | 0x1056 | 03 | U16 | V 0.1 | RO | string4_voltage
48 | String4 input current | 0x1057 | 03 | S16 | A 0.01 | RO | string4_current
49 | String5 input voltage | 0x1058 | 03 | U16 | V 0.1 | RO | string5_voltage
50 | String5 input current | 0x1059 | 03 | S16 | A 0.01 | RO | string5_current
51 | String6 input voltage | 0x105A | 03 | U16 | V 0.1 | RO | string6_voltage
52 | String6 input current | 0x105B | 03 | S16 | A 0.01 | RO | string6_current
53 | String7 input voltage | 0x105C | 03 | U16 | V 0.1 | RO | string7_voltage
54 | String7 input current | 0x105D | 03 | S16 | A 0.01 | RO | string7_current
55 | String8 input voltage | 0x105E | 03 | U16 | V 0.1 | RO | string8_voltage
56 | String8 input current | 0x105F | 03 | S16 | A 0.01 | RO | string8_current
57 | String9 input voltage | 0x1060 | 03 | U16 | V 0.1 | RO | string9_voltage
58 | String9 input current | 0x1061 | 03 | S16 | A 0.01 | RO | string9_current
59 | String10 input voltage | 0x1062 | 03 | U16 | V 0.1 | RO | string10_voltage
60 | String10 input current | 0x1063 | 03 | S16 | A 0.01 | RO | string10_current
61 | String11 input voltage | 0x1064 | 03 | U16 | V 0.1 | RO | string11_voltage
62 | String11 input current | 0x1065 | 03 | S16 | A 0.01 | RO | string11_current
63 | String12 input voltage | 0x1066 | 03 | U16 | V 0.1 | RO | string12_voltage
64 | String12 input current | 0x1067 | 03 | S16 | A 0.01 | RO | string12_current
65 | String13 input voltage | 0x1068 | 03 | U16 | V 0.1 | RO | string13_voltage
66 | String13 input current | 0x1069 | 03 | S16 | A 0.01 | RO | string13_current
67 | String14 input voltage | 0x106A | 03 | U16 | V 0.1 | RO | string14_voltage
68 | String14 input current | 0x106B | 03 | S16 | A 0.01 | RO | string14_current
69 | String15 input voltage | 0x106C | 03 | U16 | V 0.1 | RO | string15_voltage
70 | String15 input current | 0x106D | 03 | S16 | A 0.01 | RO | string15_current
71 | String16 input voltage | 0x106E | 03 | U16 | V 0.1 | RO | string16_voltage
72 | String16 input current | 0x106F | 03 | S16 | A 0.01 | RO | string16_current
73 | String17 input voltage | 0x1070 | 03 | U16 | V 0.1 | RO | string17_voltage
74 | String17 input current | 0x1071 | 03 | S16 | A 0.01 | RO | string17_current
75 | String18 input voltage | 0x1072 | 03 | U16 | V 0.1 | RO | string18_voltage
76 | String18 input current | 0x1073 | 03 | S16 | A 0.01 | RO | string18_current
77 | String19 input voltage | 0x1074 | 03 | U16 | V 0.1 | RO | string19_voltage
78 | String19 input current | 0x1075 | 03 | S16 | A 0.01 | RO | string19_current
79 | String20 input voltage | 0x1076 | 03 | U16 | V 0.1 | RO | string20_voltage
80 | String20 input current | 0x1077 | 03 | S16 | A 0.01 | RO | string20_current
81 | String21 input voltage | 0x1078 | 03 | U16 | V 0.1 | RO | string21_voltage
82 | String21 input current | 0x1079 | 03 | S16 | A 0.01 | RO | string21_current
83 | String22 input voltage | 0x107A | 03 | U16 | V 0.1 | RO | string22_voltage
84 | String22 input current | 0x107B | 03 | S16 | A 0.01 | RO | string22_current
85 | String23 input voltage | 0x107C | 03 | U16 | V 0.1 | RO | string23_voltage
86 | String23 input current | 0x107D | 03 | S16 | A 0.01 | RO | string23_current
87 | String24 input voltage | 0x107E | 03 | U16 | V 0.1 | RO | string24_voltage
88 | String24 input current | 0x107F | 03 | S16 | A 0.01 | RO | string24_current
89 | MPPT5 Voltage | 0x1080 | 03 | U16 | V 0.1 | RO | mppt5_voltage
90 | MPPT5 Current | 0x1081 | 03 | S16 | A 0.01 | RO | mppt5_current
91 | MPPT5 Power | 0x1082 | 03 | U32 | W 0.1 | RO | mppt5_power
92 | MPPT6 Voltage | 0x1084 | 03 | U16 | V 0.1 | RO | mppt6_voltage
93 | MPPT6 Current | 0x1085 | 03 | S16 | A 0.01 | RO | mppt6_current
94 | MPPT6 Power | 0x1086 | 03 | U32 | W 0.1 | RO | mppt6_power
95 | MPPT7 Voltage | 0x1088 | 03 | U16 | V 0.1 | RO | mppt7_voltage
96 | MPPT7 Current | 0x1089 | 03 | S16 | A 0.01 | RO | mppt7_current
97 | MPPT7 Power | 0x108A | 03 | U32 | W 0.1 | RO | mppt7_power
98 | MPPT8 Voltage | 0x108C | 03 | U16 | V 0.1 | RO | mppt8_voltage
99 | MPPT8 Current | 0x108D | 03 | S16 | A 0.01 | RO | mppt8_current
100 | MPPT8 Power | 0x108E | 03 | U32 | W 0.1 | RO | mppt8_power
101 | MPPT9 Voltage | 0x1090 | 03 | U16 | V 0.1 | RO | mppt9_voltage
102 | MPPT9 Current | 0x1091 | 03 | S16 | A 0.01 | RO | mppt9_current
103 | MPPT9 Power | 0x1092 | 03 | U32 | W 0.1 | RO | mppt9_power
104 | External fan speed dutypercentage | 0x120C | 03 | U16 |  | RO
105 | Q (Reference Output reactivepower) | 0x1226 | 03 | S16 |  | RO
106 | L1 watt of grid | 0x1300 | 03 | S32 | W 0.1 | RO
107 | L2 watt of grid | 0x1302 | 03 | S32 | W 0.1 | RO
108 | L3 watt of grid | 0x1304 | 03 | S32 | W 0.1 | RO
109 | Accumulated energy ofimport | 0x1306 | 03 | U32 | Wh 10 | RO | cumulative_energy
110 | Accumulated energy ofexport | 0x1308 | 03 | U32 | Wh 10 | RO | cumulative_energy
111 | L1 watt of load | 0x130A | 03 | U32 | W 0.1 | RO
112 | L2 watt of load | 0x130C | 03 | U32 | W 0.1 | RO
113 | L3 watt of load | 0x130E | 03 | U32 | W 0.1 | RO
114 | Accumulated energy of load | 0x1310 | 03 | U32 | Wh 10 | RO | cumulative_energy
115 | L1-N phase voltage of grid | 0x131A | 03 | U16 | V 0.1 | RO
116 | L2-N phase voltage of grid | 0x131B | 03 | U16 | V 0.1 | RO
117 | L3-N phase voltage of grid | 0x131C | 03 | U16 | V 0.1 | RO
118 | L1 current of grid | 0x131D | 03 | S32 | A 0.01 | RO
119 | L2 current of grid | 0x131F | 03 | S32 | A 0.01 | RO
120 | L3 current of grid | 0x1321 | 03 | S32 | A 0.01 | RO
121 | L1-N phase voltage of load | 0x1323 | 03 | U16 | V 0.1 | RO
122 | L2-N phase voltage of load | 0x1324 | 03 | U16 | V 0.1 | RO
123 | L3-N phase voltage of load | 0x1325 | 03 | U16 | V 0.1 | RO
124 | L1 current of load | 0x1326 | 03 | S32 | A 0.01 | RO
125 | L2 current of load | 0x1328 | 03 | S32 | A 0.01 | RO
126 | L3 current of load | 0x132A | 03 | S32 | A 0.01 | RO
127 | Today import Energy | 0x1332 | 03 | U32 | Wh 10 | RO
128 | Today export Energy | 0x1334 | 03 | U32 | Wh 10 | RO
129 | Today load Energy | 0x1336 | 03 | U32 | Wh 10 | RO
130 | Frequency of grid | 0x1338 | 03 | U16 | Hz 0.01 | RO
131 | Power flow direction | 0x30B2 | 03 | U16 |  | RW
132 | Maximum feed in grid power | 0x30B9 | 03 | U32 |  | RW
133 | Clear the EEPROM historyenergy record | 0x6009 | 03 | U16 |  | RW
134 | Tracker 1 voltage | 0x8000 | 03 | U16 | V 0.1 | RO
135 | String 1-1 current | 0x8040 | 03 | S16 | A 0.01 | RO | string_current
136 | String 1-2 current | 0x8080 | 03 | STRINGING | A 0.01 | RO | string_current
137 | String 1-3 current | 0x80C0 | 03 | STRINGING | A 0.01 | RO | string_current
138 | String 1-4 current | 0x8100 | 03 | STRINGING | A 0.01 | RO | string_current
139 | Tracker 2 voltage | 0x8140 | 03 | U16 | V 0.1 | RO
140 | String 2-1 current | 0x8180 | 03 | STRINGING | A 0.01 | RO | string_current
141 | String 2-2 current | 0x81C0 | 03 | STRINGING | A 0.01 | RO | string_current
142 | String 2-3 current | 0x8200 | 03 | STRINGING | A 0.01 | RO | string_current
143 | String 2-4 current | 0x8240 | 03 | STRINGING | A 0.01 | RO | string_current
144 | Tracker 3 voltage | 0x8280 | 03 | U16 | V 0.1 | RO
145 | String 3-1 current | 0x82C0 | 03 | STRINGING | A 0.01 | RO | string_current
146 | String 3-2 current | 0x8300 | 03 | STRINGING | A 0.01 | RO | string_current
147 | String 3-3 current | 0x8340 | 03 | STRINGING | A 0.01 | RO | string_current
148 | String 3-4 current | 0x8380 | 03 | STRINGING | A 0.01 | RO | string_current
149 | Tracker 4 voltage | 0x83C0 | 03 | U16 | V 0.1 | RO
150 | String 4-1 current | 0x8400 | 03 | STRINGING | A 0.01 | RO | string_current
151 | String 4-2 current | 0x8440 | 03 | STRINGING | A 0.01 | RO | string_current
152 | String 4-3 current | 0x8480 | 03 | STRINGING | A 0.01 | RO | string_current
153 | String 4-4 current | 0x84C0 | 03 | STRINGING | A 0.01 | RO | string_current
154 | Tracker 5 voltage | 0x8500 | 03 | U16 | V 0.1 | RO
155 | String 5-1 current | 0x8540 | 03 | STRINGING | A 0.01 | RO | string_current
156 | String 5-2 current | 0x8580 | 03 | STRINGING | A 0.01 | RO | string_current
157 | String 5-3 current | 0x85C0 | 03 | STRINGING | A 0.01 | RO | string_current
158 | String 5-4 current | 0x8600 | 03 | STRINGING | A 0.01 | RO | string_current
159 | Tracker 6 voltage | 0x8640 | 03 | U16 | V 0.1 | RO
160 | String 6-1 current | 0x8680 | 03 | STRINGING | A 0.01 | RO | string_current
161 | String 6-2 current | 0x86C0 | 03 | STRINGING | A 0.01 | RO | string_current
162 | String 6-3 current | 0x8700 | 03 | STRINGING | A 0.01 | RO | string_current
163 | String 6-4 current | 0x8740 | 03 | STRINGING | A 0.01 | RO | string_current
164 | Tracker 7 voltage | 0x8780 | 03 | U16 | V 0.1 | RO
165 | String 7-1 current | 0x87C0 | 03 | STRINGING | A 0.01 | RO | string_current
166 | String 7-2 current | 0x8800 | 03 | STRINGING | A 0.01 | RO | string_current
167 | String 7-3 current | 0x8840 | 03 | STRINGING | A 0.01 | RO | string_current
168 | String 7-4 current | 0x8880 | 03 | STRINGING | A 0.01 | RO | string_current
169 | Tracker 8 voltage | 0x88C0 | 03 | U16 | V 0.1 | RO
170 | String 8-1 current | 0x8900 | 03 | STRINGING | A 0.01 | RO | string_current
171 | String 8-2 current | 0x8940 | 03 | STRINGING | A 0.01 | RO | string_current
172 | String 8-3 current | 0x8980 | 03 | STRINGING | A 0.01 | RO | string_current
173 | String 8-4 current | 0x89C0 | 03 | STRINGING | A 0.01 | RO | string_current
174 | Tracker 9 voltage | 0x8A00 | 03 | U16 | V 0.1 | RO
175 | String 9-1 current | 0x8A40 | 03 | STRINGING | A 0.01 | RO | string_current
176 | String 9-2 current | 0x8A80 | 03 | STRINGING | A 0.01 | RO | string_current
177 | String 9-3 current | 0x8AC0 | 03 | STRINGING | A 0.01 | RO | string_current
178 | String 9-4 current | 0x8B00 | 03 | STRINGING | A 0.01 | RO | string_current
179 | history log 0 | 0xB600 | 03 | U16 |  | RO
180 | history log 127 | 0xB77D | 03 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)

## 5_IV
IV Scan 매핑 — data_points=64
IV Scan Command | 0x600D
Data Points | 64
Trackers | 9
Strings/Tracker | 4
IV Scan Command
Name | Address | Type | R/W | Description
IV_CURVE_SCAN | 0x600D | U16 | RW | W: 0=Stop, 1=Start / R: 0=Idle, 1=Running, 2=Finished
IV Data 레지스터 매핑
No | Type | Name | Address | Regs | Data Type | Scale
1 | Tracker Voltage | Tracker 1 voltage | 0x8000 | 64 | U16 | 0.1V
2 | String Current | String 1-1 current | 0x8040 | 64 | S16 | 0.01A
3 | String Current | String 1-2 current | 0x8080 | 64 | S16 | 0.01A
4 | String Current | String 1-3 current | 0x80C0 | 64 | S16 | 0.01A
5 | String Current | String 1-4 current | 0x8100 | 64 | S16 | 0.01A
6 | Tracker Voltage | Tracker 2 voltage | 0x8140 | 64 | U16 | 0.1V
7 | String Current | String 2-1 current | 0x8180 | 64 | S16 | 0.01A
8 | String Current | String 2-2 current | 0x81C0 | 64 | S16 | 0.01A
9 | String Current | String 2-3 current | 0x8200 | 64 | S16 | 0.01A
10 | String Current | String 2-4 current | 0x8240 | 64 | S16 | 0.01A
11 | Tracker Voltage | Tracker 3 voltage | 0x8280 | 64 | U16 | 0.1V
12 | String Current | String 3-1 current | 0x82C0 | 64 | S16 | 0.01A
13 | String Current | String 3-2 current | 0x8300 | 64 | S16 | 0.01A
14 | String Current | String 3-3 current | 0x8340 | 64 | S16 | 0.01A
15 | String Current | String 3-4 current | 0x8380 | 64 | S16 | 0.01A
16 | Tracker Voltage | Tracker 4 voltage | 0x83C0 | 64 | U16 | 0.1V
17 | String Current | String 4-1 current | 0x8400 | 64 | S16 | 0.01A
18 | String Current | String 4-2 current | 0x8440 | 64 | S16 | 0.01A
19 | String Current | String 4-3 current | 0x8480 | 64 | S16 | 0.01A
20 | String Current | String 4-4 current | 0x84C0 | 64 | S16 | 0.01A
21 | Tracker Voltage | Tracker 5 voltage | 0x8500 | 64 | U16 | 0.1V
22 | String Current | String 5-1 current | 0x8540 | 64 | S16 | 0.01A
23 | String Current | String 5-2 current | 0x8580 | 64 | S16 | 0.01A
24 | String Current | String 5-3 current | 0x85C0 | 64 | S16 | 0.01A
25 | String Current | String 5-4 current | 0x8600 | 64 | S16 | 0.01A
26 | Tracker Voltage | Tracker 6 voltage | 0x8640 | 64 | U16 | 0.1V
27 | String Current | String 6-1 current | 0x8680 | 64 | S16 | 0.01A
28 | String Current | String 6-2 current | 0x86C0 | 64 | S16 | 0.01A
29 | String Current | String 6-3 current | 0x8700 | 64 | S16 | 0.01A
30 | String Current | String 6-4 current | 0x8740 | 64 | S16 | 0.01A
31 | Tracker Voltage | Tracker 7 voltage | 0x8780 | 64 | U16 | 0.1V
32 | String Current | String 7-1 current | 0x87C0 | 64 | S16 | 0.01A
33 | String Current | String 7-2 current | 0x8800 | 64 | S16 | 0.01A
34 | String Current | String 7-3 current | 0x8840 | 64 | S16 | 0.01A
35 | String Current | String 7-4 current | 0x8880 | 64 | S16 | 0.01A
36 | Tracker Voltage | Tracker 8 voltage | 0x88C0 | 64 | U16 | 0.1V
37 | String Current | String 8-1 current | 0x8900 | 64 | S16 | 0.01A
38 | String Current | String 8-2 current | 0x8940 | 64 | S16 | 0.01A
39 | String Current | String 8-3 current | 0x8980 | 64 | S16 | 0.01A
40 | String Current | String 8-4 current | 0x89C0 | 64 | S16 | 0.01A
41 | Tracker Voltage | Tracker 9 voltage | 0x8A00 | 64 | U16 | 0.1V
42 | String Current | String 9-1 current | 0x8A40 | 64 | S16 | 0.01A
43 | String Current | String 9-2 current | 0x8A80 | 64 | S16 | 0.01A
44 | String Current | String 9-3 current | 0x8AC0 | 64 | S16 | 0.01A
45 | String Current | String 9-4 current | 0x8B00 | 64 | S16 | 0.01A