## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Sungrow
프로토콜 버전 | V1.1.37
설비 타입 | inverter
MPPT | 12
String | 24
String 모니터링 | Yes
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | Sungrow_StringInverter_Modbus_Protocol_v1137.pdf
추출 일시 | 2026-04-03 16:03
H01 매칭 | 65/65
DER 매칭 | 33/33
추출 레지스터 | 286
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Excessively high module temperature | 0x0024 | 03 | U16 |  | RO | temperature
2 | Low system insulation resistance | 0x0027 | 03 | U16 |  | RO
3 | SERIAL_NUMBER | 0x137E | 03 | U16 |  | RO |  | SN ¦ Data type :UTF-8
4 | Device type code | 0x1388 | 03 | U16 |  | RO |  | See Appendix 6
5 | Nominal activepower | 0x1389 | 03 | U16 | kW 0.1 | RO
6 | Output type | 0x138A | 03 | U16 |  | RO
7 | Daily power yields | 0x138B | 03 | U16 | kWh 0.1 | RO | daily_energy
8 | Total power yields | 0x138C | 03 | U32 | kWh | RO | cumulative_energy
9 | Total running time | 0x138E | 03 | U32 |  | RO
10 | INNER_TEMP | 0x1390 | 03 | S16 | ℃ 0.1 | RO | temperature | Internal temperature
11 | Total apparentpower | 0x1391 | 03 | U32 | VA | RO |  | Valid for inverters:SG5KTL-MT
12 | Nominal reactivepower | 0x13B9 | 03 | U16 |  | RO
13 | Array insulationresistance | 0x13CF | 03 | U16 |  | RO
14 | Daily running time | 0x13F9 | 03 | U16 |  | RO
15 | Present country | 0x13FA | 03 | U16 |  | RO
16 | Monthly poweryields | 0x1408 | 03 | U32 | kWh 0.1 | RO
17 | Total power yields | 0x1418 | 03 | U32 | kWh 0.1 | RO | cumulative_energy
18 | Bus voltage | 0x141B | 03 | U16 | V 0.1 | RO
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Total run bit (device isgrid-connected running) | 0x0011 | 03 | U16 |  | RO
2 | Total fault bit (device is infault stop state) | 0x0012 | 03 | U16 |  | RO
3 | Work state | 0x13AE | 03 | U16 |  | RO | inverter_status
4 | Work state | 0x13D9 | 03 | U32 |  | RO | inverter_status
5 | PID work state | 0x141E | 03 | U16 |  | RO | inverter_status
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Fault | 0x0009 | 03 | U16 |  | RO | alarm1
2 | Alarm run | 0x000A | 03 | U16 |  | RO
3 | Communicate fault | 0x000D | 03 | U16 |  | RO
4 | PV connection fault | 0x0017 | 03 | U16 |  | RO
5 | Fan alarm | 0x0046 | 03 | U16 |  | RO
6 | AC-side SPD alarm | 0x0047 | 03 | U16 |  | RO
7 | DC-side SPD alarm | 0x0048 | 03 | U16 |  | RO
8 | Communication alarm | 0x004A | 03 | U16 |  | RO
9 | PV1 abnormal | 0x004E | 03 | U16 |  | RO
10 | PV2 abnormal | 0x004F | 03 | U16 |  | RO
11 | PV3 abnormal | 0x0050 | 03 | U16 |  | RO
12 | PV4 abnormal | 0x0051 | 03 | U16 |  | RO
13 | Electric arc fault | 0x0058 | 03 | U16 |  | RO
14 | Grounding cable fault | 0x006A | 03 | U16 |  | RO
15 | PV5 abnormal | 0x00DC | 03 | U16 |  | RO
16 | PV6 abnormal | 0x00DD | 03 | U16 |  | RO
17 | PV7 abnormal | 0x00DE | 03 | U16 |  | RO
18 | PV8 abnormal | 0x00DF | 03 | U16 |  | RO
19 | PV9 abnormal | 0x00E0 | 03 | U16 |  | RO
20 | PV10 abnormal | 0x00E1 | 03 | U16 |  | RO
21 | PV11 abnormal | 0x00E2 | 03 | U16 |  | RO
22 | PV12 abnormal | 0x00E3 | 03 | U16 |  | RO
23 | String 1 reverse connection fault | 0x01C0 | 03 | STRINGING |  | RO
24 | String 2 reverse connection fault | 0x01C1 | 03 | STRINGING |  | RO
25 | String 3 reverse connection fault | 0x01C2 | 03 | STRINGING |  | RO
26 | String 4 reverse connection fault | 0x01C3 | 03 | STRINGING |  | RO
27 | String 5 reverse connection fault | 0x01C4 | 03 | STRINGING |  | RO
28 | String 6 reverse connection fault | 0x01C5 | 03 | STRINGING |  | RO
29 | String 7 reverse connection fault | 0x01C6 | 03 | STRINGING |  | RO
30 | String 8 reverse connection fault | 0x01C7 | 03 | STRINGING |  | RO
31 | String 9 reverse connection fault | 0x01C8 | 03 | STRINGING |  | RO
32 | String 10 reverse connection fault | 0x01C9 | 03 | STRINGING |  | RO
33 | String 11 reverse connection fault | 0x01CA | 03 | STRINGING |  | RO
34 | String 12 reverse connection fault | 0x01CB | 03 | STRINGING |  | RO
35 | String 13 reverse connection fault | 0x01CC | 03 | STRINGING |  | RO
36 | String 14 reverse connection fault | 0x01CD | 03 | STRINGING |  | RO
37 | String 15 reverse connection fault | 0x01CE | 03 | STRINGING |  | RO
38 | String 16 reverse connection fault | 0x01CF | 03 | STRINGING |  | RO
39 | String 17 reverse connection fault | 0x01D0 | 03 | STRINGING |  | RO
40 | String 18 reverse connection fault | 0x01D1 | 03 | STRINGING |  | RO
41 | String 19 reverse connection fault | 0x01D2 | 03 | STRINGING |  | RO
42 | String 20 reverse connection fault | 0x01D3 | 03 | STRINGING |  | RO
43 | String 21 reverse connection fault | 0x01D4 | 03 | STRINGING |  | RO
44 | String 22 reverse connection fault | 0x01D5 | 03 | STRINGING |  | RO
45 | String 23 reverse connection fault | 0x01D6 | 03 | STRINGING |  | RO
46 | String 24 reverse connection fault | 0x01D7 | 03 | STRINGING |  | RO
47 | Meter communication abnormalalarm | 0x0202 | 03 | U16 |  | RO
48 | String 1 reverse connection alarm | 0x0214 | 03 | STRINGING |  | RO
49 | String 2 reverse connection alarm | 0x0215 | 03 | STRINGING |  | RO
50 | String 3 reverse connection alarm | 0x0216 | 03 | STRINGING |  | RO
51 | String 4 reverse connection alarm | 0x0217 | 03 | STRINGING |  | RO
52 | String 5 reverse connection alarm | 0x0218 | 03 | STRINGING |  | RO
53 | String 6 reverse connection alarm | 0x0219 | 03 | STRINGING |  | RO
54 | String 7 reverse connection alarm | 0x021A | 03 | STRINGING |  | RO
55 | String 8 reverse connection alarm | 0x021B | 03 | STRINGING |  | RO
56 | String 9 reverse connection alarm | 0x021C | 03 | STRINGING |  | RO
57 | String 10 reverse connection alarm | 0x021D | 03 | STRINGING |  | RO
58 | String 11 reverse connection alarm | 0x021E | 03 | STRINGING |  | RO
59 | String 12 reverse connection alarm | 0x021F | 03 | STRINGING |  | RO
60 | String 13 reverse connection alarm | 0x0220 | 03 | STRINGING |  | RO
61 | String 14 reverse connection alarm | 0x0221 | 03 | STRINGING |  | RO
62 | String 15 reverse connection alarm | 0x0222 | 03 | STRINGING |  | RO
63 | String 16 reverse connection alarm | 0x0223 | 03 | STRINGING |  | RO
64 | String 1 abnormal alarm | 0x0224 | 03 | STRINGING |  | RO
65 | String 2 abnormal alarm | 0x0225 | 03 | STRINGING |  | RO
66 | String 3 abnormal alarm | 0x0226 | 03 | STRINGING |  | RO
67 | String 4 abnormal alarm | 0x0227 | 03 | STRINGING |  | RO
68 | String 5 abnormal alarm | 0x0228 | 03 | STRINGING |  | RO
69 | String 6 abnormal alarm | 0x0229 | 03 | STRINGING |  | RO
70 | String 7 abnormal alarm | 0x022A | 03 | STRINGING |  | RO
71 | String 8 abnormal alarm | 0x022B | 03 | STRINGING |  | RO
72 | String 9 abnormal alarm | 0x022C | 03 | STRINGING |  | RO
73 | String 10 abnormal alarm | 0x022D | 03 | STRINGING |  | RO
74 | String 11 abnormal alarm | 0x022E | 03 | STRINGING |  | RO
75 | String 12 abnormal alarm | 0x022F | 03 | STRINGING |  | RO
76 | String 13 abnormal alarm | 0x0230 | 03 | STRINGING |  | RO
77 | String 14 abnormal alarm | 0x0231 | 03 | STRINGING |  | RO
78 | String 15 abnormal alarm | 0x0232 | 03 | STRINGING |  | RO
79 | String 16 abnormal alarm | 0x0233 | 03 | STRINGING |  | RO
80 | String 17 reverse connection alarm | 0x0234 | 03 | STRINGING |  | RO
81 | String 18 reverse connection alarm | 0x0235 | 03 | STRINGING |  | RO
82 | String 19 reverse connection alarm | 0x0236 | 03 | STRINGING |  | RO
83 | String 20 reverse connection alarm | 0x0237 | 03 | STRINGING |  | RO
84 | String 21 reverse connection alarm | 0x0238 | 03 | STRINGING |  | RO
85 | String 22 reverse connection alarm | 0x0239 | 03 | STRINGING |  | RO
86 | String 23 reverse connection alarm | 0x023A | 03 | STRINGING |  | RO
87 | String 24 reverse connection alarm | 0x023B | 03 | STRINGING |  | RO
88 | String 17 abnormal alarm | 0x0244 | 03 | STRINGING |  | RO
89 | String 18 abnormal alarm | 0x0245 | 03 | STRINGING |  | RO
90 | String 19 abnormal alarm | 0x0246 | 03 | STRINGING |  | RO
91 | String 20 abnormal alarm | 0x0247 | 03 | STRINGING |  | RO
92 | String 21 abnormal alarm | 0x0248 | 03 | STRINGING |  | RO
93 | String 22 abnormal alarm | 0x0249 | 03 | STRINGING |  | RO
94 | String 23 abnormal alarm | 0x024A | 03 | STRINGING |  | RO
95 | String 24 abnormal alarm | 0x024B | 03 | STRINGING |  | RO
96 | Fault/Alarm time:Year | 0x13AF | 03 | U16 |  | RO
97 | Fault/Alarm time:Month | 0x13B0 | 03 | U16 |  | RO
98 | Fault/Alarm time:Day | 0x13B1 | 03 | U16 |  | RO
99 | Fault/Alarm time:Hour | 0x13B2 | 03 | U16 |  | RO
100 | Fault/Alarm time:Minute | 0x13B3 | 03 | U16 |  | RO
101 | Fault/Alarm time:Second | 0x13B4 | 03 | U16 |  | RO
102 | Fault/Alarm code 1 | 0x13B5 | 03 | U16 |  | RO
103 | PID alarm code | 0x141F | 03 | U16 |  | RO
104 | Communicate fault | 0x2500 | 03 | U16 |  | RO
105 | Fault | 0x5500 | 03 | U16 |  | RO | alarm1
106 | Alarm run | 0x9100 | 03 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 65/65
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x1399 | PV_TOTAL_INPUT_POWER | U32
13 | cumulative_energy | PDF | O | 0x138C | Total power yields | U32 | kWh |  | kWh→Wh (*1000)
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x13AE | Work state | U16 |  |  | 37=Nominal reactiv, 38=Reserved, 39=Array insulatio, 40=Reserved, 41=Reserved, 42=Active PowerReg... (+27)
16 | alarm1 | PDF | O | 0x13B5 | Fault/Alarm code 1 | U16
17 | alarm2 | PDF | O | 0x141F | PID alarm code | U16
18 | alarm3 | PDF | O | 0x0058 | Electric arc fault | U16
19 | mppt1_voltage | PDF | O | 0x1393 | MPPT 1 voltage | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x1394 | MPPT 1 current | U16 | A | 0.1
21 | mppt2_voltage | PDF | O | 0x1395 | MPPT 2 voltage | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x1396 | MPPT 2 current | U16 | A | 0.1
23 | mppt3_voltage | PDF | O | 0x1397 | MPPT 3 voltage | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x1398 | MPPT 3 current | U16 | A | 0.1
25 | mppt4_voltage | PDF | O | 0x13FB | MPPT 4 voltage | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x13FC | MPPT 4 current | U16 | A | 0.1
27 | mppt5_voltage | PDF | O | 0x13FD | MPPT 5 voltage | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x13FE | MPPT 5 current | U16 | A | 0.1
29 | mppt6_voltage | PDF | O | 0x13FF | MPPT 6 voltage | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x1400 | MPPT 6 current | U16 | A | 0.1
31 | mppt7_voltage | PDF | O | 0x1401 | MPPT 7 voltage | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x1402 | MPPT 7 current | U16 | A | 0.1
33 | mppt8_voltage | PDF | O | 0x1403 | MPPT 8 voltage | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x1404 | MPPT 8 current | U16 | A | 0.1
35 | mppt9_voltage | PDF | O | 0x140A | MPPT 9 voltage | U16 | V | 0.1
36 | mppt9_current | PDF | O | 0x140B | MPPT 9 current | U16 | A | 0.1
37 | mppt10_voltage | PDF | O | 0x140C | MPPT 10 voltage | U16 | V | 0.1
38 | mppt10_current | PDF | O | 0x140D | MPPT 10 current | U16 | A | 0.1
39 | mppt11_voltage | PDF | O | 0x140E | MPPT 11 voltage | U16 | V | 0.1
40 | mppt11_current | PDF | O | 0x140F | MPPT 11 current | U16 | A | 0.1
41 | mppt12_voltage | PDF | O | 0x1410 | MPPT 12 voltage | U16 | V | 0.1
42 | mppt12_current | PDF | O | 0x1411 | MPPT 12 current | U16 | A | 0.1
43 | string1_current | PDF | O | 0x1B65 | String 1 current | STRINGING | A | 0.01
44 | string2_current | PDF | O | 0x1B66 | String 2 current | STRINGING | A | 0.01
45 | string3_current | PDF | O | 0x1B67 | String 3 current | STRINGING | A | 0.01
46 | string4_current | PDF | O | 0x1B68 | String 4 current | STRINGING | A | 0.01
47 | string5_current | PDF | O | 0x1B69 | String 5 current | STRINGING | A | 0.01
48 | string6_current | PDF | O | 0x1B6A | String 6 current | STRINGING | A | 0.01
49 | string7_current | PDF | O | 0x1B6B | String 7 current | STRINGING | A | 0.01
50 | string8_current | PDF | O | 0x1B6C | String 8 current | STRINGING | A | 0.01
51 | string9_current | PDF | O | 0x1B6D | String 9 current | STRINGING | A | 0.01
52 | string10_current | PDF | O | 0x1B6E | String 10 current | STRINGING | A | 0.01
53 | string11_current | PDF | O | 0x1B6F | String 11 current | STRINGING | A | 0.01
54 | string12_current | PDF | O | 0x1B70 | String 12 current | STRINGING | A | 0.01
55 | string13_current | PDF | O | 0x1B71 | String 13 current | STRINGING | A | 0.01
56 | string14_current | PDF | O | 0x1B72 | String 14 current | STRINGING | A | 0.01
57 | string15_current | PDF | O | 0x1B73 | String 15 current | STRINGING | A | 0.01
58 | string16_current | PDF | O | 0x1B74 | String 16 current | STRINGING | A | 0.01
59 | string17_current | PDF | O | 0x1B75 | String 17 current | STRINGING | A | 0.01
60 | string18_current | PDF | O | 0x1B76 | String 18 current | STRINGING | A | 0.01
61 | string19_current | PDF | O | 0x1B77 | String 19 current | STRINGING | A | 0.01
62 | string20_current | PDF | O | 0x1B78 | String 20 current | STRINGING | A | 0.01
63 | string21_current | PDF | O | 0x1B79 | String 21 current | STRINGING | A | 0.01
64 | string22_current | PDF | O | 0x1B7A | String 22 current | STRINGING | A | 0.01
65 | string23_current | PDF | O | 0x1B7B | String 23 current | STRINGING | A | 0.01
66 | string24_current | PDF | O | 0x1B7C | String 24 current | STRINGING | A | 0.01

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 12ch / String 24ch
MPPT 채널 수 | 12
String 채널 수 | 24
String 모니터링 | Yes
MPPT 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x1393 | MPPT 1 voltage | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x1394 | MPPT 1 current | U16 | A | 0.1
3 | mppt2_voltage | PDF | O | 0x1395 | MPPT 2 voltage | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x1396 | MPPT 2 current | U16 | A | 0.1
5 | mppt3_voltage | PDF | O | 0x1397 | MPPT 3 voltage | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x1398 | MPPT 3 current | U16 | A | 0.1
7 | mppt4_voltage | PDF | O | 0x13FB | MPPT 4 voltage | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x13FC | MPPT 4 current | U16 | A | 0.1
9 | mppt5_voltage | PDF | O | 0x13FD | MPPT 5 voltage | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x13FE | MPPT 5 current | U16 | A | 0.1
11 | mppt6_voltage | PDF | O | 0x13FF | MPPT 6 voltage | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x1400 | MPPT 6 current | U16 | A | 0.1
13 | mppt7_voltage | PDF | O | 0x1401 | MPPT 7 voltage | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x1402 | MPPT 7 current | U16 | A | 0.1
15 | mppt8_voltage | PDF | O | 0x1403 | MPPT 8 voltage | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x1404 | MPPT 8 current | U16 | A | 0.1
17 | mppt9_voltage | PDF | O | 0x140A | MPPT 9 voltage | U16 | V | 0.1
18 | mppt9_current | PDF | O | 0x140B | MPPT 9 current | U16 | A | 0.1
19 | mppt10_voltage | PDF | O | 0x140C | MPPT 10 voltage | U16 | V | 0.1
20 | mppt10_current | PDF | O | 0x140D | MPPT 10 current | U16 | A | 0.1
21 | mppt11_voltage | PDF | O | 0x140E | MPPT 11 voltage | U16 | V | 0.1
22 | mppt11_current | PDF | O | 0x140F | MPPT 11 current | U16 | A | 0.1
23 | mppt12_voltage | PDF | O | 0x1410 | MPPT 12 voltage | U16 | V | 0.1
24 | mppt12_current | PDF | O | 0x1411 | MPPT 12 current | U16 | A | 0.1
String 채널 H01 매칭 (24개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | PDF | O | 0x1B65 | String 1 current | STRINGING | A | 0.01
2 | string2_current | PDF | O | 0x1B66 | String 2 current | STRINGING | A | 0.01
3 | string3_current | PDF | O | 0x1B67 | String 3 current | STRINGING | A | 0.01
4 | string4_current | PDF | O | 0x1B68 | String 4 current | STRINGING | A | 0.01
5 | string5_current | PDF | O | 0x1B69 | String 5 current | STRINGING | A | 0.01
6 | string6_current | PDF | O | 0x1B6A | String 6 current | STRINGING | A | 0.01
7 | string7_current | PDF | O | 0x1B6B | String 7 current | STRINGING | A | 0.01
8 | string8_current | PDF | O | 0x1B6C | String 8 current | STRINGING | A | 0.01
9 | string9_current | PDF | O | 0x1B6D | String 9 current | STRINGING | A | 0.01
10 | string10_current | PDF | O | 0x1B6E | String 10 current | STRINGING | A | 0.01
11 | string11_current | PDF | O | 0x1B6F | String 11 current | STRINGING | A | 0.01
12 | string12_current | PDF | O | 0x1B70 | String 12 current | STRINGING | A | 0.01
13 | string13_current | PDF | O | 0x1B71 | String 13 current | STRINGING | A | 0.01
14 | string14_current | PDF | O | 0x1B72 | String 14 current | STRINGING | A | 0.01
15 | string15_current | PDF | O | 0x1B73 | String 15 current | STRINGING | A | 0.01
16 | string16_current | PDF | O | 0x1B74 | String 16 current | STRINGING | A | 0.01
17 | string17_current | PDF | O | 0x1B75 | String 17 current | STRINGING | A | 0.01
18 | string18_current | PDF | O | 0x1B76 | String 18 current | STRINGING | A | 0.01
19 | string19_current | PDF | O | 0x1B77 | String 19 current | STRINGING | A | 0.01
20 | string20_current | PDF | O | 0x1B78 | String 20 current | STRINGING | A | 0.01
21 | string21_current | PDF | O | 0x1B79 | String 21 current | STRINGING | A | 0.01
22 | string22_current | PDF | O | 0x1B7A | String 22 current | STRINGING | A | 0.01
23 | string23_current | PDF | O | 0x1B7B | String 23 current | STRINGING | A | 0.01
24 | string24_current | PDF | O | 0x1B7C | String 24 current | STRINGING | A | 0.01
MONITORING 전체 (131개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Grid overvoltage | 0x0002 | 03 | U16 |  | RO
2 | Grid transient overvoltage | 0x0003 | 03 | U16 |  | RO
3 | Grid undervoltage | 0x0004 | 03 | U16 |  | RO
4 | Grid low voltage | 0x0005 | 03 | U16 |  | RO
5 | AC instantaneous overcurrent | 0x0007 | 03 | U16 |  | RO
6 | Excessive leakage current | 0x000C | 03 | U16 |  | RO
7 | 10-minute grid overvoltage | 0x000E | 03 | U16 |  | RO
8 | Grid high voltage | 0x000F | 03 | U16 |  | RO
9 | Excessively high ambient temperature | 0x0025 | 03 | U16 |  | RO
10 | Low ambient temperature | 0x002B | 03 | U16 |  | RO
11 | Grid-side protection self-check failure | 0x0069 | 03 | U16 |  | RO
12 | PIDovervoltage/overcurrentprotection | 0x01B2 | 03 | U16 |  | RO
13 | PV1 overvoltage | 0x05DC | 03 | U16 |  | RO
14 | PV2 overvoltage | 0x05DD | 03 | U16 |  | RO
15 | PV3 overvoltage | 0x05DE | 03 | U16 |  | RO
16 | PV4 overvoltage | 0x05DF | 03 | U16 |  | RO
17 | PV5 overvoltage | 0x05E0 | 03 | U16 |  | RO
18 | PV6 overvoltage | 0x05E1 | 03 | U16 |  | RO
19 | PV7 overvoltage | 0x05E2 | 03 | U16 |  | RO
20 | PV8 overvoltage | 0x05E3 | 03 | U16 |  | RO
21 | PV9 overvoltage | 0x05E4 | 03 | U16 |  | RO
22 | PV10 overvoltage | 0x05E5 | 03 | U16 |  | RO
23 | PV11 overvoltage | 0x05E6 | 03 | U16 |  | RO
24 | PV12 overvoltage | 0x05E7 | 03 | U16 |  | RO
25 | PV13 overvoltage | 0x05E8 | 03 | U16 |  | RO
26 | PV14 overvoltage | 0x05E9 | 03 | U16 |  | RO
27 | PV15 overvoltage | 0x05EA | 03 | U16 |  | RO
28 | PV16 overvoltage | 0x05EB | 03 | U16 |  | RO
29 | PV17 overvoltage | 0x05EC | 03 | U16 |  | RO
30 | PV18 overvoltage | 0x05ED | 03 | U16 |  | RO
31 | PV19 overvoltage | 0x05EE | 03 | U16 |  | RO
32 | PV20 overvoltage | 0x05EF | 03 | U16 |  | RO
33 | PV21 overvoltage | 0x05F0 | 03 | U16 |  | RO
34 | PV22 overvoltage | 0x05F1 | 03 | U16 |  | RO
35 | PV23 overvoltage | 0x05F2 | 03 | U16 |  | RO
36 | PV24 overvoltage | 0x05F3 | 03 | U16 |  | RO
37 | PV25 overvoltage | 0x05F4 | 03 | U16 |  | RO
38 | PV26 overvoltage | 0x05F5 | 03 | U16 |  | RO
39 | PV27 overvoltage | 0x05F6 | 03 | U16 |  | RO
40 | PV28 overvoltage | 0x05F7 | 03 | U16 |  | RO
41 | PV29 overvoltage | 0x05F8 | 03 | U16 |  | RO
42 | PV30 overvoltage | 0x05F9 | 03 | U16 |  | RO
43 | PV31 overvoltage | 0x05FA | 03 | U16 |  | RO
44 | PV32 overvoltage | 0x05FB | 03 | U16 |  | RO
45 | Powerlimitationswitch | 0x138F | 03 | U16 |  | RO
46 | Export powerlimitation | 0x1392 | 03 | U16 |  | RO
47 | MPPT 1 voltage | 0x1393 | 03 | U16 | V 0.1 | RO | mppt1_voltage
48 | MPPT 1 current | 0x1394 | 03 | U16 | A 0.1 | RO | mppt1_current
49 | MPPT 2 voltage | 0x1395 | 03 | U16 | V 0.1 | RO | mppt2_voltage
50 | MPPT 2 current | 0x1396 | 03 | U16 | A 0.1 | RO | mppt2_current
51 | MPPT 3 voltage | 0x1397 | 03 | U16 | V 0.1 | RO | mppt3_voltage
52 | MPPT 3 current | 0x1398 | 03 | U16 | A 0.1 | RO | mppt3_current
53 | PV_TOTAL_INPUT_POWER | 0x1399 | 03 | U32 |  | RO | pv_power
54 | A-B linevoltage/phase Avoltage | 0x139B | 03 | U16 | A 0.1 | RO
55 | B-C lineVoltage/phase BVoltage | 0x139C | 03 | U16 | V 0.1 | RO
56 | C-A lineVoltage/phase CVoltage | 0x139D | 03 | U16 | A 0.1 | RO
57 | L1_CURRENT | 0x139E | 03 | U16 | A 0.1 | RO | r_current
58 | L2_CURRENT | 0x139F | 03 | U16 | A 0.1 | RO | s_current
59 | L3_CURRENT | 0x13A0 | 03 | U16 | A 0.1 | RO | t_current
60 | GRID_TOTAL_ACTIVE_POWER | 0x13A7 | 03 | U32 |  | RO | ac_power
61 | REACTIVE_POWER | 0x13A9 | 03 | S32 |  | RO | reactive_power
62 | Power factor | 0x13AB | 03 | S16 |  | RO | power_factor
63 | L1_FREQUENCY | 0x13AC | 03 | U16 | Hz 0.1 | RO | frequency
64 | Reactive powerpercentagesetting | 0x13AD | 03 | S16 | % 0.1 | RO
65 | PA(Lower Power) | 0x13BB | 03 | U16 | % 0.1 | RO
66 | PC(Upper Power) | 0x13BC | 03 | U16 | % 0.1 | RO
67 | KA(Upperlimit-PF) | 0x13BD | 03 | S16 |  | RO
68 | KC(Lower limit-PF) | 0x13BE | 03 | S16 |  | RO
69 | powerA | 0x13C9 | 03 | U16 | % 0.1 | RO
70 | powerB | 0x13CA | 03 | U16 | % 0.1 | RO
71 | powerC | 0x13CB | 03 | U16 | % 0.1 | RO
72 | pf max_ | 0x13CC | 03 | U16 |  | RO
73 | Active PowerRegulation Setpoint | 0x13D5 | 03 | U32 |  | RO
74 | Reactive PowerRegulation Setpoint | 0x13D7 | 03 | S32 |  | RO
75 | Meter power | 0x13DB | 03 | S32 |  | RO
76 | Meter A phasepower | 0x13DD | 03 | S32 | A | RO
77 | Meter B phasepower | 0x13DF | 03 | S32 |  | RO
78 | Meter C phasepower | 0x13E1 | 03 | S32 |  | RO
79 | Load power | 0x13E3 | 03 | S32 |  | RO
80 | Daily export energy | 0x13E5 | 03 | U32 | kWh 0.1 | RO
81 | Total export energy | 0x13E7 | 03 | U32 | kWh 0.1 | RO
82 | Daily import energy | 0x13E9 | 03 | U32 | kWh 0.1 | RO
83 | Total import energy | 0x13EB | 03 | U32 | kWh 0.1 | RO
84 | Daily direct energyconsumption | 0x13ED | 03 | U32 | kWh 0.1 | RO
85 | Total direct energyconsumption | 0x13EF | 03 | U32 | kWh 0.1 | RO
86 | MPPT 4 voltage | 0x13FB | 03 | U16 | V 0.1 | RO | mppt4_voltage
87 | MPPT 4 current | 0x13FC | 03 | U16 | A 0.1 | RO | mppt4_current
88 | MPPT 5 voltage | 0x13FD | 03 | U16 | V 0.1 | RO | mppt5_voltage
89 | MPPT 5 current | 0x13FE | 03 | U16 | A 0.1 | RO | mppt5_current
90 | MPPT 6 voltage | 0x13FF | 03 | U16 | V 0.1 | RO | mppt6_voltage
91 | MPPT 6 current | 0x1400 | 03 | U16 | A 0.1 | RO | mppt6_current
92 | MPPT 7 voltage | 0x1401 | 03 | U16 | V 0.1 | RO | mppt7_voltage
93 | MPPT 7 current | 0x1402 | 03 | U16 | A 0.1 | RO | mppt7_current
94 | MPPT 8 voltage | 0x1403 | 03 | U16 | V 0.1 | RO | mppt8_voltage
95 | MPPT 8 current | 0x1404 | 03 | U16 | A 0.1 | RO | mppt8_current
96 | QP ExitPowerRatio_ | 0x1405 | 03 | U16 | % 0.1 | RO
97 | MPPT 9 voltage | 0x140A | 03 | U16 | V 0.1 | RO | mppt9_voltage
98 | MPPT 9 current | 0x140B | 03 | U16 | A 0.1 | RO | mppt9_current
99 | MPPT 10 voltage | 0x140C | 03 | U16 | V 0.1 | RO | mppt10_voltage
100 | MPPT 10 current | 0x140D | 03 | U16 | A 0.1 | RO | mppt10_current
101 | MPPT 11 voltage | 0x140E | 03 | U16 | V 0.1 | RO | mppt11_voltage
102 | MPPT 11 current | 0x140F | 03 | U16 | A 0.1 | RO | mppt11_current
103 | MPPT 12 voltage | 0x1410 | 03 | U16 | V 0.1 | RO | mppt12_voltage
104 | MPPT 12 current | 0x1411 | 03 | U16 | A 0.1 | RO | mppt12_current
105 | QU EnterPower_ | 0x1419 | 03 | U16 | % 0.1 | RO
106 | Negative voltage tothe ground | 0x141A | 03 | S16 | V 0.1 | RO
107 | L1_FREQUENCY | 0x141C | 03 | U16 | Hz 0.01 | RO | frequency
108 | String 1 current | 0x1B65 | 03 | STRINGING | A 0.01 | RO | string1_current
109 | String 2 current | 0x1B66 | 03 | STRINGING | A 0.01 | RO | string2_current
110 | String 3 current | 0x1B67 | 03 | STRINGING | A 0.01 | RO | string3_current
111 | String 4 current | 0x1B68 | 03 | STRINGING | A 0.01 | RO | string4_current
112 | String 5 current | 0x1B69 | 03 | STRINGING | A 0.01 | RO | string5_current
113 | String 6 current | 0x1B6A | 03 | STRINGING | A 0.01 | RO | string6_current
114 | String 7 current | 0x1B6B | 03 | STRINGING | A 0.01 | RO | string7_current
115 | String 8 current | 0x1B6C | 03 | STRINGING | A 0.01 | RO | string8_current
116 | String 9 current | 0x1B6D | 03 | STRINGING | A 0.01 | RO | string9_current
117 | String 10 current | 0x1B6E | 03 | STRINGING | A 0.01 | RO | string10_current
118 | String 11 current | 0x1B6F | 03 | STRINGING | A 0.01 | RO | string11_current
119 | String 12 current | 0x1B70 | 03 | STRINGING | A 0.01 | RO | string12_current
120 | String 13 current | 0x1B71 | 03 | STRINGING | A 0.01 | RO | string13_current
121 | String 14 current | 0x1B72 | 03 | STRINGING | A 0.01 | RO | string14_current
122 | String 15 current | 0x1B73 | 03 | STRINGING | A 0.01 | RO | string15_current
123 | String 16 current | 0x1B74 | 03 | STRINGING | A 0.01 | RO | string16_current
124 | String 17 current | 0x1B75 | 03 | STRINGING | A 0.01 | RO | string17_current
125 | String 18 current | 0x1B76 | 03 | STRINGING | A 0.01 | RO | string18_current
126 | String 19 current | 0x1B77 | 03 | STRINGING | A 0.01 | RO | string19_current
127 | String 20 current | 0x1B78 | 03 | STRINGING | A 0.01 | RO | string20_current
128 | String 21 current | 0x1B79 | 03 | STRINGING | A 0.01 | RO | string21_current
129 | String 22 current | 0x1B7A | 03 | STRINGING | A 0.01 | RO | string22_current
130 | String 23 current | 0x1B7B | 03 | STRINGING | A 0.01 | RO | string23_current
131 | String 24 current | 0x1B7C | 03 | STRINGING | A 0.01 | RO | string24_current

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)