## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=12, STR=24)
제조사 | Sungrow
용량 | -
MPPT | 12
String/MPPT | 2
Total Strings | 24
H01 매칭 | 65/66
DER 매칭 | 33/33
총 레지스터 | 260
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Excessively high module temperature | 0x0024 | U16 |  | RO | temperature
2 | Low system insulation resistance | 0x0027 | U16 |  | RO
3 | SERIAL_NUMBER | 0x137E | U16 |  | RO |  | SN ¦ Data type :UTF-8
4 | Device type code | 0x1388 | U16 |  | RO |  | See Appendix 6
5 | Nominal activepower | 0x1389 | U16 | kW 0.1 | RO
6 | Output type | 0x138A | U16 |  | RO
7 | Daily power yields | 0x138B | U16 | kWh 0.1 | RO | daily_energy
8 | Total power yields | 0x138C | U32 | kWh | RO | cumulative_energy
9 | Total running time | 0x138E | U32 |  | RO
10 | INNER_TEMP | 0x1390 | S16 | ℃ 0.1 | RO | temperature | Internal temperature
11 | Total apparentpower | 0x1391 | U32 | VA | RO |  | Valid for inverters:SG5KTL-MT
12 | Nominal reactivepower | 0x13B9 | U16 |  | RO
13 | Array insulationresistance | 0x13CF | U16 |  | RO
14 | Daily running time | 0x13F9 | U16 |  | RO
15 | Present country | 0x13FA | U16 |  | RO
16 | Monthly poweryields | 0x1408 | U32 | kWh 0.1 | RO
17 | Total power yields | 0x1418 | U32 | kWh 0.1 | RO | cumulative_energy
18 | Bus voltage | 0x141B | U16 | V 0.1 | RO
H01 MONITORING (131개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Grid overvoltage | 0x0002 | U16 |  | RO
2 | Grid transient overvoltage | 0x0003 | U16 |  | RO
3 | Grid undervoltage | 0x0004 | U16 |  | RO
4 | Grid low voltage | 0x0005 | U16 |  | RO
5 | AC instantaneous overcurrent | 0x0007 | U16 |  | RO
6 | Excessive leakage current | 0x000C | U16 |  | RO
7 | 10-minute grid overvoltage | 0x000E | U16 |  | RO
8 | Grid high voltage | 0x000F | U16 |  | RO
9 | Excessively high ambient temperature | 0x0025 | U16 |  | RO
10 | Low ambient temperature | 0x002B | U16 |  | RO
11 | Grid-side protection self-check failure | 0x0069 | U16 |  | RO
12 | PIDovervoltage/overcurrentprotection | 0x01B2 | U16 |  | RO
13 | PV1 overvoltage | 0x05DC | U16 |  | RO
14 | PV2 overvoltage | 0x05DD | U16 |  | RO
15 | PV3 overvoltage | 0x05DE | U16 |  | RO
16 | PV4 overvoltage | 0x05DF | U16 |  | RO
17 | PV5 overvoltage | 0x05E0 | U16 |  | RO
18 | PV6 overvoltage | 0x05E1 | U16 |  | RO
19 | PV7 overvoltage | 0x05E2 | U16 |  | RO
20 | PV8 overvoltage | 0x05E3 | U16 |  | RO
21 | PV9 overvoltage | 0x05E4 | U16 |  | RO
22 | PV10 overvoltage | 0x05E5 | U16 |  | RO
23 | PV11 overvoltage | 0x05E6 | U16 |  | RO
24 | PV12 overvoltage | 0x05E7 | U16 |  | RO
25 | PV13 overvoltage | 0x05E8 | U16 |  | RO
26 | PV14 overvoltage | 0x05E9 | U16 |  | RO
27 | PV15 overvoltage | 0x05EA | U16 |  | RO
28 | PV16 overvoltage | 0x05EB | U16 |  | RO
29 | PV17 overvoltage | 0x05EC | U16 |  | RO
30 | PV18 overvoltage | 0x05ED | U16 |  | RO
31 | PV19 overvoltage | 0x05EE | U16 |  | RO
32 | PV20 overvoltage | 0x05EF | U16 |  | RO
33 | PV21 overvoltage | 0x05F0 | U16 |  | RO
34 | PV22 overvoltage | 0x05F1 | U16 |  | RO
35 | PV23 overvoltage | 0x05F2 | U16 |  | RO
36 | PV24 overvoltage | 0x05F3 | U16 |  | RO
37 | PV25 overvoltage | 0x05F4 | U16 |  | RO
38 | PV26 overvoltage | 0x05F5 | U16 |  | RO
39 | PV27 overvoltage | 0x05F6 | U16 |  | RO
40 | PV28 overvoltage | 0x05F7 | U16 |  | RO
41 | PV29 overvoltage | 0x05F8 | U16 |  | RO
42 | PV30 overvoltage | 0x05F9 | U16 |  | RO
43 | PV31 overvoltage | 0x05FA | U16 |  | RO
44 | PV32 overvoltage | 0x05FB | U16 |  | RO
45 | Powerlimitationswitch | 0x138F | U16 |  | RO
46 | Export powerlimitation | 0x1392 | U16 |  | RO
47 | MPPT 1 voltage | 0x1393 | U16 | V 0.1 | RO | mppt1_voltage
48 | MPPT 1 current | 0x1394 | U16 | A 0.1 | RO | mppt1_current
49 | MPPT 2 voltage | 0x1395 | U16 | V 0.1 | RO | mppt2_voltage
50 | MPPT 2 current | 0x1396 | U16 | A 0.1 | RO | mppt2_current
51 | MPPT 3 voltage | 0x1397 | U16 | V 0.1 | RO | mppt3_voltage
52 | MPPT 3 current | 0x1398 | U16 | A 0.1 | RO | mppt3_current
53 | PV_TOTAL_INPUT_POWER | 0x1399 | U32 |  | RO | pv_power
54 | A-B linevoltage/phase Avoltage | 0x139B | U16 | A 0.1 | RO
55 | B-C lineVoltage/phase BVoltage | 0x139C | U16 | V 0.1 | RO
56 | C-A lineVoltage/phase CVoltage | 0x139D | U16 | A 0.1 | RO
57 | L1_CURRENT | 0x139E | U16 | A 0.1 | RO | r_current
58 | L2_CURRENT | 0x139F | U16 | A 0.1 | RO | s_current
59 | L3_CURRENT | 0x13A0 | U16 | A 0.1 | RO | t_current
60 | GRID_TOTAL_ACTIVE_POWER | 0x13A7 | U32 |  | RO | ac_power
61 | REACTIVE_POWER | 0x13A9 | S32 |  | RO | reactive_power
62 | Power factor | 0x13AB | S16 |  | RO | power_factor
63 | L1_FREQUENCY | 0x13AC | U16 | Hz 0.1 | RO | frequency
64 | Reactive powerpercentagesetting | 0x13AD | S16 | % 0.1 | RO
65 | PA(Lower Power) | 0x13BB | U16 | % 0.1 | RO
66 | PC(Upper Power) | 0x13BC | U16 | % 0.1 | RO
67 | KA(Upperlimit-PF) | 0x13BD | S16 |  | RO
68 | KC(Lower limit-PF) | 0x13BE | S16 |  | RO
69 | powerA | 0x13C9 | U16 | % 0.1 | RO
70 | powerB | 0x13CA | U16 | % 0.1 | RO
71 | powerC | 0x13CB | U16 | % 0.1 | RO
72 | pf max_ | 0x13CC | U16 |  | RO
73 | Active PowerRegulation Setpoint | 0x13D5 | U32 |  | RO
74 | Reactive PowerRegulation Setpoint | 0x13D7 | S32 |  | RO
75 | Meter power | 0x13DB | S32 |  | RO
76 | Meter A phasepower | 0x13DD | S32 | A | RO
77 | Meter B phasepower | 0x13DF | S32 |  | RO
78 | Meter C phasepower | 0x13E1 | S32 |  | RO
79 | Load power | 0x13E3 | S32 |  | RO
80 | Daily export energy | 0x13E5 | U32 | kWh 0.1 | RO
81 | Total export energy | 0x13E7 | U32 | kWh 0.1 | RO
82 | Daily import energy | 0x13E9 | U32 | kWh 0.1 | RO
83 | Total import energy | 0x13EB | U32 | kWh 0.1 | RO
84 | Daily direct energyconsumption | 0x13ED | U32 | kWh 0.1 | RO
85 | Total direct energyconsumption | 0x13EF | U32 | kWh 0.1 | RO
86 | MPPT 4 voltage | 0x13FB | U16 | V 0.1 | RO | mppt4_voltage
87 | MPPT 4 current | 0x13FC | U16 | A 0.1 | RO | mppt4_current
88 | MPPT 5 voltage | 0x13FD | U16 | V 0.1 | RO | mppt5_voltage
89 | MPPT 5 current | 0x13FE | U16 | A 0.1 | RO | mppt5_current
90 | MPPT 6 voltage | 0x13FF | U16 | V 0.1 | RO | mppt6_voltage
91 | MPPT 6 current | 0x1400 | U16 | A 0.1 | RO | mppt6_current
92 | MPPT 7 voltage | 0x1401 | U16 | V 0.1 | RO | mppt7_voltage
93 | MPPT 7 current | 0x1402 | U16 | A 0.1 | RO | mppt7_current
94 | MPPT 8 voltage | 0x1403 | U16 | V 0.1 | RO | mppt8_voltage
95 | MPPT 8 current | 0x1404 | U16 | A 0.1 | RO | mppt8_current
96 | QP ExitPowerRatio_ | 0x1405 | U16 | % 0.1 | RO
97 | MPPT 9 voltage | 0x140A | U16 | V 0.1 | RO | mppt9_voltage
98 | MPPT 9 current | 0x140B | U16 | A 0.1 | RO | mppt9_current
99 | MPPT 10 voltage | 0x140C | U16 | V 0.1 | RO | mppt10_voltage
100 | MPPT 10 current | 0x140D | U16 | A 0.1 | RO | mppt10_current
101 | MPPT 11 voltage | 0x140E | U16 | V 0.1 | RO | mppt11_voltage
102 | MPPT 11 current | 0x140F | U16 | A 0.1 | RO | mppt11_current
103 | MPPT 12 voltage | 0x1410 | U16 | V 0.1 | RO | mppt12_voltage
104 | MPPT 12 current | 0x1411 | U16 | A 0.1 | RO | mppt12_current
105 | QU EnterPower_ | 0x1419 | U16 | % 0.1 | RO
106 | Negative voltage tothe ground | 0x141A | S16 | V 0.1 | RO
107 | L1_FREQUENCY | 0x141C | U16 | Hz 0.01 | RO | frequency
108 | String 1 current | 0x1B65 | STRINGING | A 0.01 | RO | string1_current
109 | String 2 current | 0x1B66 | STRINGING | A 0.01 | RO | string2_current
110 | String 3 current | 0x1B67 | STRINGING | A 0.01 | RO | string3_current
111 | String 4 current | 0x1B68 | STRINGING | A 0.01 | RO | string4_current
112 | String 5 current | 0x1B69 | STRINGING | A 0.01 | RO | string5_current
113 | String 6 current | 0x1B6A | STRINGING | A 0.01 | RO | string6_current
114 | String 7 current | 0x1B6B | STRINGING | A 0.01 | RO | string7_current
115 | String 8 current | 0x1B6C | STRINGING | A 0.01 | RO | string8_current
116 | String 9 current | 0x1B6D | STRINGING | A 0.01 | RO | string9_current
117 | String 10 current | 0x1B6E | STRINGING | A 0.01 | RO | string10_current
118 | String 11 current | 0x1B6F | STRINGING | A 0.01 | RO | string11_current
119 | String 12 current | 0x1B70 | STRINGING | A 0.01 | RO | string12_current
120 | String 13 current | 0x1B71 | STRINGING | A 0.01 | RO | string13_current
121 | String 14 current | 0x1B72 | STRINGING | A 0.01 | RO | string14_current
122 | String 15 current | 0x1B73 | STRINGING | A 0.01 | RO | string15_current
123 | String 16 current | 0x1B74 | STRINGING | A 0.01 | RO | string16_current
124 | String 17 current | 0x1B75 | STRINGING | A 0.01 | RO | string17_current
125 | String 18 current | 0x1B76 | STRINGING | A 0.01 | RO | string18_current
126 | String 19 current | 0x1B77 | STRINGING | A 0.01 | RO | string19_current
127 | String 20 current | 0x1B78 | STRINGING | A 0.01 | RO | string20_current
128 | String 21 current | 0x1B79 | STRINGING | A 0.01 | RO | string21_current
129 | String 22 current | 0x1B7A | STRINGING | A 0.01 | RO | string22_current
130 | String 23 current | 0x1B7B | STRINGING | A 0.01 | RO | string23_current
131 | String 24 current | 0x1B7C | STRINGING | A 0.01 | RO | string24_current
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Total run bit (device isgrid-connected running) | 0x0011 | U16 |  | RO
2 | Total fault bit (device is infault stop state) | 0x0012 | U16 |  | RO
3 | Work state | 0x13AE | U16 |  | RO | inverter_status
4 | Work state | 0x13D9 | U32 |  | RO | inverter_status
5 | PID work state | 0x141E | U16 |  | RO | inverter_status
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Fault | 0x0009 | U16 |  | RO | alarm1
2 | Alarm run | 0x000A | U16 |  | RO
3 | Communicate fault | 0x000D | U16 |  | RO
4 | PV connection fault | 0x0017 | U16 |  | RO
5 | Fan alarm | 0x0046 | U16 |  | RO
6 | AC-side SPD alarm | 0x0047 | U16 |  | RO
7 | DC-side SPD alarm | 0x0048 | U16 |  | RO
8 | Communication alarm | 0x004A | U16 |  | RO
9 | PV1 abnormal | 0x004E | U16 |  | RO
10 | PV2 abnormal | 0x004F | U16 |  | RO
11 | PV3 abnormal | 0x0050 | U16 |  | RO
12 | PV4 abnormal | 0x0051 | U16 |  | RO
13 | Electric arc fault | 0x0058 | U16 |  | RO
14 | Grounding cable fault | 0x006A | U16 |  | RO
15 | PV5 abnormal | 0x00DC | U16 |  | RO
16 | PV6 abnormal | 0x00DD | U16 |  | RO
17 | PV7 abnormal | 0x00DE | U16 |  | RO
18 | PV8 abnormal | 0x00DF | U16 |  | RO
19 | PV9 abnormal | 0x00E0 | U16 |  | RO
20 | PV10 abnormal | 0x00E1 | U16 |  | RO
21 | PV11 abnormal | 0x00E2 | U16 |  | RO
22 | PV12 abnormal | 0x00E3 | U16 |  | RO
23 | String 1 reverse connection fault | 0x01C0 | STRINGING |  | RO
24 | String 2 reverse connection fault | 0x01C1 | STRINGING |  | RO
25 | String 3 reverse connection fault | 0x01C2 | STRINGING |  | RO
26 | String 4 reverse connection fault | 0x01C3 | STRINGING |  | RO
27 | String 5 reverse connection fault | 0x01C4 | STRINGING |  | RO
28 | String 6 reverse connection fault | 0x01C5 | STRINGING |  | RO
29 | String 7 reverse connection fault | 0x01C6 | STRINGING |  | RO
30 | String 8 reverse connection fault | 0x01C7 | STRINGING |  | RO
31 | String 9 reverse connection fault | 0x01C8 | STRINGING |  | RO
32 | String 10 reverse connection fault | 0x01C9 | STRINGING |  | RO
33 | String 11 reverse connection fault | 0x01CA | STRINGING |  | RO
34 | String 12 reverse connection fault | 0x01CB | STRINGING |  | RO
35 | String 13 reverse connection fault | 0x01CC | STRINGING |  | RO
36 | String 14 reverse connection fault | 0x01CD | STRINGING |  | RO
37 | String 15 reverse connection fault | 0x01CE | STRINGING |  | RO
38 | String 16 reverse connection fault | 0x01CF | STRINGING |  | RO
39 | String 17 reverse connection fault | 0x01D0 | STRINGING |  | RO
40 | String 18 reverse connection fault | 0x01D1 | STRINGING |  | RO
41 | String 19 reverse connection fault | 0x01D2 | STRINGING |  | RO
42 | String 20 reverse connection fault | 0x01D3 | STRINGING |  | RO
43 | String 21 reverse connection fault | 0x01D4 | STRINGING |  | RO
44 | String 22 reverse connection fault | 0x01D5 | STRINGING |  | RO
45 | String 23 reverse connection fault | 0x01D6 | STRINGING |  | RO
46 | String 24 reverse connection fault | 0x01D7 | STRINGING |  | RO
47 | Meter communication abnormalalarm | 0x0202 | U16 |  | RO
48 | String 1 reverse connection alarm | 0x0214 | STRINGING |  | RO
49 | String 2 reverse connection alarm | 0x0215 | STRINGING |  | RO
50 | String 3 reverse connection alarm | 0x0216 | STRINGING |  | RO
51 | String 4 reverse connection alarm | 0x0217 | STRINGING |  | RO
52 | String 5 reverse connection alarm | 0x0218 | STRINGING |  | RO
53 | String 6 reverse connection alarm | 0x0219 | STRINGING |  | RO
54 | String 7 reverse connection alarm | 0x021A | STRINGING |  | RO
55 | String 8 reverse connection alarm | 0x021B | STRINGING |  | RO
56 | String 9 reverse connection alarm | 0x021C | STRINGING |  | RO
57 | String 10 reverse connection alarm | 0x021D | STRINGING |  | RO
58 | String 11 reverse connection alarm | 0x021E | STRINGING |  | RO
59 | String 12 reverse connection alarm | 0x021F | STRINGING |  | RO
60 | String 13 reverse connection alarm | 0x0220 | STRINGING |  | RO
61 | String 14 reverse connection alarm | 0x0221 | STRINGING |  | RO
62 | String 15 reverse connection alarm | 0x0222 | STRINGING |  | RO
63 | String 16 reverse connection alarm | 0x0223 | STRINGING |  | RO
64 | String 1 abnormal alarm | 0x0224 | STRINGING |  | RO
65 | String 2 abnormal alarm | 0x0225 | STRINGING |  | RO
66 | String 3 abnormal alarm | 0x0226 | STRINGING |  | RO
67 | String 4 abnormal alarm | 0x0227 | STRINGING |  | RO
68 | String 5 abnormal alarm | 0x0228 | STRINGING |  | RO
69 | String 6 abnormal alarm | 0x0229 | STRINGING |  | RO
70 | String 7 abnormal alarm | 0x022A | STRINGING |  | RO
71 | String 8 abnormal alarm | 0x022B | STRINGING |  | RO
72 | String 9 abnormal alarm | 0x022C | STRINGING |  | RO
73 | String 10 abnormal alarm | 0x022D | STRINGING |  | RO
74 | String 11 abnormal alarm | 0x022E | STRINGING |  | RO
75 | String 12 abnormal alarm | 0x022F | STRINGING |  | RO
76 | String 13 abnormal alarm | 0x0230 | STRINGING |  | RO
77 | String 14 abnormal alarm | 0x0231 | STRINGING |  | RO
78 | String 15 abnormal alarm | 0x0232 | STRINGING |  | RO
79 | String 16 abnormal alarm | 0x0233 | STRINGING |  | RO
80 | String 17 reverse connection alarm | 0x0234 | STRINGING |  | RO
81 | String 18 reverse connection alarm | 0x0235 | STRINGING |  | RO
82 | String 19 reverse connection alarm | 0x0236 | STRINGING |  | RO
83 | String 20 reverse connection alarm | 0x0237 | STRINGING |  | RO
84 | String 21 reverse connection alarm | 0x0238 | STRINGING |  | RO
85 | String 22 reverse connection alarm | 0x0239 | STRINGING |  | RO
86 | String 23 reverse connection alarm | 0x023A | STRINGING |  | RO
87 | String 24 reverse connection alarm | 0x023B | STRINGING |  | RO
88 | String 17 abnormal alarm | 0x0244 | STRINGING |  | RO
89 | String 18 abnormal alarm | 0x0245 | STRINGING |  | RO
90 | String 19 abnormal alarm | 0x0246 | STRINGING |  | RO
91 | String 20 abnormal alarm | 0x0247 | STRINGING |  | RO
92 | String 21 abnormal alarm | 0x0248 | STRINGING |  | RO
93 | String 22 abnormal alarm | 0x0249 | STRINGING |  | RO
94 | String 23 abnormal alarm | 0x024A | STRINGING |  | RO
95 | String 24 abnormal alarm | 0x024B | STRINGING |  | RO
96 | Fault/Alarm time:Year | 0x13AF | U16 |  | RO
97 | Fault/Alarm time:Month | 0x13B0 | U16 |  | RO
98 | Fault/Alarm time:Day | 0x13B1 | U16 |  | RO
99 | Fault/Alarm time:Hour | 0x13B2 | U16 |  | RO
100 | Fault/Alarm time:Minute | 0x13B3 | U16 |  | RO
101 | Fault/Alarm time:Second | 0x13B4 | U16 |  | RO
102 | Fault/Alarm code 1 | 0x13B5 | U16 |  | RO
103 | PID alarm code | 0x141F | U16 |  | RO
104 | Communicate fault | 0x2500 | U16 |  | RO
105 | Fault | 0x5500 | U16 |  | RO | alarm1
106 | Alarm run | 0x9100 | U16 |  | RO

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | Sungrow
용량 | -
MPPT | 12 (PDF max 12개)
String | 24 (2/MPPT)
H01 매칭 | 65/66
DER 매칭 | 33/33
총 레지스터 | 260
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 18
MONITORING | 131
STATUS | 5
ALARM | 106
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | PDF | O | 0x1399 | PV_TOTAL_INPUT_POWER
13 | cumulative_energy | PDF | O | 0x138C | Total power yields
14 | cumulative_energy_low | PDF | - | - | -
15 | status | PDF | O | 0x13AE | Work state
16 | alarm1 | PDF | O | 0x13B5 | Fault/Alarm code 1
17 | alarm2 | PDF | O | 0x141F | PID alarm code
18 | alarm3 | PDF | O | 0x0058 | Electric arc fault
19 | mppt1_voltage | PDF | O | 0x1393 | MPPT 1 voltage
20 | mppt1_current | PDF | O | 0x1394 | MPPT 1 current
21 | mppt2_voltage | PDF | O | 0x1395 | MPPT 2 voltage
22 | mppt2_current | PDF | O | 0x1396 | MPPT 2 current
23 | mppt3_voltage | PDF | O | 0x1397 | MPPT 3 voltage
24 | mppt3_current | PDF | O | 0x1398 | MPPT 3 current
25 | mppt4_voltage | PDF | O | 0x13FB | MPPT 4 voltage
26 | mppt4_current | PDF | O | 0x13FC | MPPT 4 current
27 | mppt5_voltage | PDF | O | 0x13FD | MPPT 5 voltage
28 | mppt5_current | PDF | O | 0x13FE | MPPT 5 current
29 | mppt6_voltage | PDF | O | 0x13FF | MPPT 6 voltage
30 | mppt6_current | PDF | O | 0x1400 | MPPT 6 current
31 | mppt7_voltage | PDF | O | 0x1401 | MPPT 7 voltage
32 | mppt7_current | PDF | O | 0x1402 | MPPT 7 current
33 | mppt8_voltage | PDF | O | 0x1403 | MPPT 8 voltage
34 | mppt8_current | PDF | O | 0x1404 | MPPT 8 current
35 | mppt9_voltage | PDF | O | 0x140A | MPPT 9 voltage
36 | mppt9_current | PDF | O | 0x140B | MPPT 9 current
37 | mppt10_voltage | PDF | O | 0x140C | MPPT 10 voltage
38 | mppt10_current | PDF | O | 0x140D | MPPT 10 current
39 | mppt11_voltage | PDF | O | 0x140E | MPPT 11 voltage
40 | mppt11_current | PDF | O | 0x140F | MPPT 11 current
41 | mppt12_voltage | PDF | O | 0x1410 | MPPT 12 voltage
42 | mppt12_current | PDF | O | 0x1411 | MPPT 12 current
43 | string1_current | PDF | O | 0x1B65 | String 1 current
44 | string2_current | PDF | O | 0x1B66 | String 2 current
45 | string3_current | PDF | O | 0x1B67 | String 3 current
46 | string4_current | PDF | O | 0x1B68 | String 4 current
47 | string5_current | PDF | O | 0x1B69 | String 5 current
48 | string6_current | PDF | O | 0x1B6A | String 6 current
49 | string7_current | PDF | O | 0x1B6B | String 7 current
50 | string8_current | PDF | O | 0x1B6C | String 8 current
51 | string9_current | PDF | O | 0x1B6D | String 9 current
52 | string10_current | PDF | O | 0x1B6E | String 10 current
53 | string11_current | PDF | O | 0x1B6F | String 11 current
54 | string12_current | PDF | O | 0x1B70 | String 12 current
55 | string13_current | PDF | O | 0x1B71 | String 13 current
56 | string14_current | PDF | O | 0x1B72 | String 14 current
57 | string15_current | PDF | O | 0x1B73 | String 15 current
58 | string16_current | PDF | O | 0x1B74 | String 16 current
59 | string17_current | PDF | O | 0x1B75 | String 17 current
60 | string18_current | PDF | O | 0x1B76 | String 18 current
61 | string19_current | PDF | O | 0x1B77 | String 19 current
62 | string20_current | PDF | O | 0x1B78 | String 20 current
63 | string21_current | PDF | O | 0x1B79 | String 21 current
64 | string22_current | PDF | O | 0x1B7A | String 22 current
65 | string23_current | PDF | O | 0x1B7B | String 23 current
66 | string24_current | PDF | O | 0x1B7C | String 24 current