## Register_Mapping
No | Section | Source_Addr_Hex | Source_Addr_Dec | Source_Name | Source_Type | Source_Unit | Source_Scale | Source_RW | Source_Regs | → | Solarize_Name | Solarize_Addr_Hex | Match_Type | Notes
--- Registers ---
1 | Registers | 0x0064 | 100 | Hz | U16 |  |  | RO | 1 | → | HZ |  | Ref(100%)
2 | Registers | 0x0064 | 100 | Hz | U16 |  |  | RO | 1 | → | HZ |  | Ref(100%)
3 | Registers | 0x0100 | 256 | Active power adjust | U16 |  |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(81%)
4 | Registers | 0x0101 | 257 | PF reactive power adjust | U16 |  |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(81%)
5 | Registers | 0xFFFF | 65535 | 1 % 1-20,lagging 0.99-0.8 80-100,leading 0.80-1, Note: if read command the inverter is not in PF setting mode (1547 use) | U16 |  |  | RO | 1 | → | REG_1_1_20LAGGING_0_99_0_8_80_100LEADING_0_80_1_NOTE_IF_READ_COMMAND_THE_INVERTER_IS_NOT_IN_PF_SETTING_MODE_1547_USE |  | Ref(99%)
6 | Registers | 0xFFFF | 65535 | % 1-20,lagging 0.99-0.8 80-100,leading 0.80-1, Note: if read command the inverter is not in PF setting mode (1547 use) | U16 |  |  | RO | 1 | → | REG_1_20LAGGING_0_99_0_8_80_100LEADING_0_80_1_NOTE_IF_READ_COMMAND_THE_INVERTER_IS_NOT_IN_PF_SETTING_MODE_1547_USE |  | Ref(99%)
7 | Registers | 0x0102 | 258 | Reactive power adjust | S32 |  |  | RW | 1 | → | REACTIVE_POWER_SET |  | Ref(87%)
8 | Registers | 0x0104 | 260 | Max value of reactive power | U32 |  |  | RO | 1 | → | DEA_TOTAL_REACTIVE_POWER_LOW |  | Ref(69%)
9 | Registers | 0x0106 | 262 | Export Power Limit Adjust | S16 |  |  | WO | 1 | → | EXPORT_POWER_LIMIT_COMMUNICATION_OVERTIME_SET |  | Ref(63%)
10 | Registers | 0x0107 | 263 | TaiWan Safety Vpset | U16 |  |  | RW | 1 | → | TAI_WAN_SAFETY_VPSET |  | Ref(100%)
11 | Registers | 0x0108 | 264 | TaiWan Safety PF adjust | U16 |  |  | RW | 1 | → | TAI_WAN_SAFETY_PF_ADJUST |  | Ref(100%)
12 | Registers | 0x0064 | 100 | % For Taiwan safety regulations (80-100) | U16 |  |  | RO | 1 | → | FOR_TAIWAN_SAFETY_REGULATIONS_80_100 |  | Ref(100%)
13 | Registers | 0x0109 | 265 | TaiWan Safety reactive power adjust | S16 |  |  | RW | 1 | → | TAI_WAN_SAFETY_PF_ADJUST |  | Ref(77%)
14 | Registers | 0x010A | 266 | TaiWan Safety active power adjust | U16 |  |  | RW | 1 | → | TAI_WAN_SAFETY_PF_ADJUST |  | Ref(79%)
15 | Registers | 0x010B | 267 | Export power limit Communication Overtime set | U16 |  |  | RW | 1 | → | EXPORT_POWER_LIMIT_COMMUNICATION_OVERTIME_SET |  | Ref(100%)
16 | Registers | 0x010C | 268 | TaiWan VPC curve switch | U16 |  |  | RW | 1 | → | IV_CURVE_SCAN |  | Ref(59%)
17 | Registers | 0x0120 | 288 | Power On(Allow on grid self-test) | U16 |  |  | WO | 1 | → | POWER_ON_ALLOW_ON_GRID_SELF_TEST |  | Ref(100%)
18 | Registers | 0x0121 | 289 | Power Off(Not allow on grid self-test) | U16 |  |  | WO | 1 | → | POWER_OFF_NOT_ALLOW_ON_GRID_SELF_TEST |  | Ref(100%)
19 | Registers | 0x0122 | 290 | Restart | U16 |  |  | WO | 1 | → | RESTART |  | Ref(100%)
20 | Registers | 0x0123 | 291 | On Grid Export Power Limit Switch | U16 |  |  | RW | 1 | → | GRID_POWER_LOW |  | Ref(55%)
21 | Registers | 0x0124 | 292 | Set the Export power percentage(Nee d to turn on the limit switch) | U16 |  |  | RW | 1 | → | SET_THE_EXPORT_POWER_PERCENTAGE_NEE_D_TO_TURN_ON_THE_LIMIT_SWITCH |  | Ref(100%)
22 | Registers | 0x0125 | 293 | Set the Export power percentage(No need to turn on the limit switch) | U16 |  |  | RW | 1 | → | SET_THE_EXPORT_POWER_PERCENTAGE_NO_NEED_TO_TURN_ON_THE_LIMIT_SWITCH |  | Ref(100%)
23 | Registers | 0x0130 | 304 | Automatic Reactive power Adjust | U16 |  |  | WO | 1 | → | REACTIVE_POWER_SET |  | Ref(69%)
24 | Registers | 0x0131 | 305 | Automatic Reactive power Adjust ID | U32 |  |  | WO | 1 | → | DEA_TOTAL_REACTIVE_POWER_HIGH |  | Ref(67%)
25 | Registers | 0x0133 | 307 | Battery Mode Switch(Brazil) | U16 |  |  | WO | 1 | → | BATTERY_MODE_SWITCH_BRAZIL |  | Ref(100%)
26 | Registers | 0x0134 | 308 | Battery Voltage set(Brazil) | U16 |  |  | WO | 1 | → | BATTERY_MODE_SWITCH_BRAZIL |  | Ref(77%)
27 | Registers | 0x0138 | 312 | Shadow mode switch | U16 |  |  | RW | 1 | → | SHADOW_MODE_SWITCH |  | Ref(100%)
28 | Registers | 0x0200 | 512 | Device Serial | STR |  |  | RO | 1 | → | DEVICE_MODEL |  | Ref(72%)
29 | Registers | 0x0210 | 528 | Device Type | STR |  |  | RO | 1 | → | DEVICE_TYPE |  | Ref(100%)
30 | Registers | 0x0220 | 544 | Error Message | U32 |  |  | RO | 1 | → | ERROR_CODE1 |  | Ref(58%)
31 | Registers | 0x0222 | 546 | High Byte of Total Feed Power to grid /Total power generation | U16 |  |  | RO | 1 | → | HIGH_BYTE_OF_TOTAL_FEED_POWER_TO_GRID_TOTAL_POWER_GENERATION |  | Ref(100%)
32 | Registers | 0x0223 | 547 | Low Byte of Total Feed Power to grid/Total power generation | U16 |  |  | RO | 1 | → | LOW_BYTE_OF_TOTAL_FEED_POWER_TO_GRID_TOTAL_POWER_GENERATION |  | Ref(100%)
33 | Registers | 0x0224 | 548 | High Byte of Total feeding hours/Hourly power generation | U16 |  |  | RO | 1 | → | HIGH_BYTE_OF_TOTAL_FEEDING_HOURS_HOURLY_POWER_GENERATION |  | Ref(100%)
34 | Registers | 0x0225 | 549 | Low Byte of Total feeding hours/Hourly power generation | U16 |  |  | RO | 1 | → | LOW_BYTE_OF_TOTAL_FEEDING_HOURS_HOURLY_POWER_GENERATION |  | Ref(100%)
35 | Registers | 0x0226 | 550 | Vpv1 /PPV1 input voltage | U16 |  |  | RO | 1 | → | PV1_VOLTAGE |  | Ref(65%)
36 | Registers | 0x0227 | 551 | Vpv2 /PV2 input voltage | U16 |  |  | RO | 1 | → | PV2_VOLTAGE |  | Ref(67%)
37 | Registers | 0x0228 | 552 | Ipv1 /PV1 input current | U16 |  |  | RO | 1 | → | PV1_CURRENT |  | Ref(67%)
38 | Registers | 0x0229 | 553 | Ipv2 /PV2 input current | U16 |  |  | RO | 1 | → | PV2_CURRENT |  | Ref(67%)
39 | Registers | 0x022A | 554 | Vac1 /L1 Phase voltage | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(78%)
40 | Registers | 0x022B | 555 | Vac2 /L2 Phase voltage | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(78%)
41 | Registers | 0x022C | 556 | Vac3 /L3 Phase voltage | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(78%)
42 | Registers | 0x022D | 557 | Iac1 /L1 Phase current | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(78%)
43 | Registers | 0x022E | 558 | Iac2 /L2 Phase current | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(78%)
44 | Registers | 0x022F | 559 | Iac3 /L3 Phase current | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(78%)
45 | Registers | 0x0230 | 560 | Fac1 /L1 Phase frequency | U16 |  |  | RO | 1 | → | L1_FREQUENCY |  | Ref(69%)
46 | Registers | 0x0064 | 100 | Hz Phase L1 frequency | U16 |  |  | RO | 1 | → | L1_FREQUENCY |  | Ref(73%)
47 | Registers | 0x0231 | 561 | Fac2 /L2 Phase frequency | U16 |  |  | RO | 1 | → | L2_FREQUENCY |  | Ref(69%)
48 | Registers | 0x0064 | 100 | Hz Phase L2 frequency | U16 |  |  | RO | 1 | → | L2_FREQUENCY |  | Ref(73%)
49 | Registers | 0x0232 | 562 | Fac3 /L3 Phase frequency | U16 |  |  | RO | 1 | → | L3_FREQUENCY |  | Ref(69%)
50 | Registers | 0x0064 | 100 | Hz Phase L3 frequency | U16 |  |  | RO | 1 | → | L3_FREQUENCY |  | Ref(73%)
51 | Registers | 0x0233 | 563 | Pac L /Inverter current output power | U16 |  |  | RO | 1 | → | PAC_L_INVERTER_CURRENT_OUTPUT_POWER |  | Ref(100%)
52 | Registers | 0x0234 | 564 | Work Mode | U16 |  |  | RO | 1 | → | WORKING_MODE |  | Ref(86%)
53 | Registers | 0x0235 | 565 | Inverter internal temperature | U16 |  |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(62%)
54 | Registers | 0x0236 | 566 | E-Day /Daily power generation | U16 |  |  | RO | 1 | → | E_DAY_DAILY_POWER_GENERATION |  | Ref(100%)
55 | Registers | 0x0300 | 768 | Vpv1 /PV1 input voltage | U16 |  |  | RO | 1 | → | PV1_VOLTAGE |  | Ref(67%)
56 | Registers | 0x0301 | 769 | Vpv2 /PV2 input voltage | U16 |  |  | RO | 1 | → | PV2_VOLTAGE |  | Ref(67%)
57 | Registers | 0x0302 | 770 | Ipv1 /PV1 input current | U16 |  |  | RO | 1 | → | PV1_CURRENT |  | Ref(67%)
58 | Registers | 0x0303 | 771 | Ipv2 /PV2 input current | U16 |  |  | RO | 1 | → | PV2_CURRENT |  | Ref(67%)
59 | Registers | 0x0304 | 772 | Vac1 /L1 Phase voltage | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(78%)
60 | Registers | 0x0305 | 773 | Vac2 /L2 Phase voltage | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(78%)
61 | Registers | 0x0306 | 774 | Vac3 /L3 Phase voltage | U16 |  |  | RO | 1 | → | S_PHASE_VOLTAGE |  | Ref(78%)
62 | Registers | 0x0307 | 775 | Iac1 /L1 Phase current | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(78%)
63 | Registers | 0x0308 | 776 | Iac2 /L2 Phase current | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(78%)
64 | Registers | 0x0309 | 777 | Iac3 /L3 Phase current | U16 |  |  | RO | 1 | → | R_PHASE_CURRENT |  | Ref(78%)
65 | Registers | 0x030A | 778 | Fac1 /L1 Phase frequency | U16 |  |  | RO | 1 | → | L1_FREQUENCY |  | Ref(69%)
66 | Registers | 0x0064 | 100 | Hz Phase L1 frequency | U16 |  |  | RO | 1 | → | L1_FREQUENCY |  | Ref(73%)
67 | Registers | 0x030B | 779 | Fac2 /L2 Phase frequency | U16 |  |  | RO | 1 | → | L2_FREQUENCY |  | Ref(69%)
68 | Registers | 0x0064 | 100 | Hz Phase L2 frequency | U16 |  |  | RO | 1 | → | L2_FREQUENCY |  | Ref(73%)
69 | Registers | 0x030C | 780 | Fac3 /L3 Phase frequency | U16 |  |  | RO | 1 | → | L3_FREQUENCY |  | Ref(69%)
70 | Registers | 0x0064 | 100 | Hz Phase L3 frequency | U16 |  |  | RO | 1 | → | L3_FREQUENCY |  | Ref(73%)
71 | Registers | 0x030D | 781 | Pac L /Inverter current output power | U16 |  |  | RO | 1 | → | PAC_L_INVERTER_CURRENT_OUTPUT_POWER |  | Ref(100%)
72 | Registers | 0x030E | 782 | Work Mode | U16 |  |  | RO | 1 | → | WORKING_MODE |  | Ref(86%)
73 | Registers | 0x030F | 783 | Inverter internal temperature | U16 |  |  | RO | 1 | → | INTERNAL_TEMP |  | Ref(62%)
74 | Registers | 0x0310 | 784 | Error Message H | U16 |  |  | RO | 1 | → | ERROR_CODE1_HIGH |  | Ref(58%)
75 | Registers | 0x0311 | 785 | Error Message L | U16 |  |  | RO | 1 | → | DSP_ERROR_CODE_L |  | Ref(58%)
76 | Registers | 0x0312 | 786 | High Byte of Total Feed Power to grid/Total power generation | U16 |  |  | RO | 1 | → | HIGH_BYTE_OF_TOTAL_FEED_POWER_TO_GRID_TOTAL_POWER_GENERATION |  | Ref(100%)
77 | Registers | 0x0313 | 787 | Low Byte of Total Feed Power to grid/Total power generation | U16 |  |  | RO | 1 | → | LOW_BYTE_OF_TOTAL_FEED_POWER_TO_GRID_TOTAL_POWER_GENERATION |  | Ref(100%)
78 | Registers | 0x0314 | 788 | High Byte of Total feeding hours/Hourly power generation | U16 |  |  | RO | 1 | → | HIGH_BYTE_OF_TOTAL_FEEDING_HOURS_HOURLY_POWER_GENERATION |  | Ref(100%)
79 | Registers | 0x0315 | 789 | Low Byte of Total feeding hours/Hourly power generation | U16 |  |  | RO | 1 | → | LOW_BYTE_OF_TOTAL_FEEDING_HOURS_HOURLY_POWER_GENERATION |  | Ref(100%)
80 | Registers | 0x0316 | 790 | Firmware Version | U16 |  |  | RO | 1 | → | FIRMWARE_VERSION |  | Ref(100%)
81 | Registers | 0x0317 | 791 | Warning Code | U16 |  |  | RO | 1 | → | WORKING_MODE |  | Ref(75%)
82 | Registers | 0x0318 | 792 | RSVD | U16 |  |  | RO | 1 | → | RSVD |  | Ref(100%)
83 | Registers | 0x0319 | 793 | Function Status Bits | U16 |  |  | RO | 1 | → | RUNNING_STATUS |  | Ref(65%)
84 | Registers | 0x031A | 794 | RSVD | U16 |  |  | RO | 1 | → | RSVD |  | Ref(100%)
85 | Registers | 0x031B | 795 | RSVD | U16 |  |  | RO | 1 | → | RSVD |  | Ref(100%)
86 | Registers | 0x031C | 796 | BUS Voltage | U16 |  |  | RO | 1 | → | BUS_VOLTAGE |  | Ref(100%)
87 | Registers | 0x031D | 797 | NBUS Voltage | U16 |  |  | RO | 1 | → | BUS_VOLTAGE |  | Ref(96%)
88 | Registers | 0x031E | 798 | RSVD | U16 |  |  | RO | 1 | → | RSVD |  | Ref(100%)
89 | Registers | 0x0064 | 100 | Hz RSVD | U16 |  |  | RO | 1 | → | HZ_RSVD |  | Ref(100%)
90 | Registers | 0x031F | 799 | Safety Code | U16 |  |  | RO | 1 | → | FAULT_CODE_1 |  | Ref(61%)
91 | Registers | 0x0320 | 800 | Feed Power to grid in today/ Daily power | U16 |  |  | RO | 1 | → | FEED_POWER_TO_GRID_IN_TODAY_DAILY_POWER |  | Ref(100%)
92 | Registers | 0x0324 | 804 | Vpv5 /PV5 input voltage | U16 |  |  | RO | 1 | → | PV5_VOLTAGE |  | Ref(67%)
93 | Registers | 0x0325 | 805 | Ipv5 /PV5 input current | U16 |  |  | RO | 1 | → | PV5_CURRENT |  | Ref(67%)
94 | Registers | 0x0326 | 806 | Vpv6 /PV6 input voltage | U16 |  |  | RO | 1 | → | PV6_VOLTAGE |  | Ref(67%)
95 | Registers | 0x0327 | 807 | Ipv6 /PV6 input current | U16 |  |  | RO | 1 | → | PV6_CURRENT |  | Ref(67%)
96 | Registers | 0x033B | 827 | Year :Month | U16 |  |  | RO | 1 | → | YEARLY_PRODUCTION_H |  | Ref(55%)
97 | Registers | 0x033C | 828 | Date :Hour | U16 |  |  | RO | 1 | → | ACTIVE_POWER |  | Ref(57%)
98 | Registers | 0x033D | 829 | Minute :Second | U16 |  |  | RO | 1 | → | INVERTER_CONTROL |  | Ref(55%)
99 | Registers | 0x033E | 830 | Manufacture ID | U16 |  |  | RO | 1 | → | MANUFACTURE_ID |  | Ref(100%)
100 | Registers | 0x033F | 831 | Wireless signal strength | U16 |  |  | RO | 1 | → | WIRELESS_SIGNAL_STRENGTH |  | Ref(100%)
101 | Registers | 0x0340 | 832 | High Byte of PV Mode（SMT only） | U16 |  |  | RO | 1 | → | HIGH_BYTE_OF_PV_MODE_SMT_ONLY |  | Ref(100%)
102 | Registers | 0x0341 | 833 | Low Byte of PV Mode（SMT only） | U16 |  |  | RO | 1 | → | LOW_BYTE_OF_PV_MODE_SMT_ONLY |  | Ref(100%)
103 | Registers | 0x0352 | 850 | High Byte of Power | U16 |  |  | RO | 1 | → | HIGH_BYTE_OF_PV_MODE_SMT_ONLY |  | Ref(68%)
104 | Registers | 0x0353 | 851 | Low Byte of Power | U16 |  |  | RO | 1 | → | LOW_BYTE_OF_PV_MODE_SMT_ONLY |  | Ref(67%)
105 | Registers | 0x0354 | 852 | Firmware Version of ARM | U16 |  |  | RO | 1 | → | FIRMWARE_VERSION |  | Ref(82%)
106 | Registers | 0x0355 | 853 | GPRS Burn-in Mode | U16 |  |  | RO | 1 | → | OPERATION_MODE |  | Ref(58%)
107 | Registers | 0x0000 | 0 | 1 NA | U16 |  |  | RO | 1 | → | REG_1_NA |  | Ref(100%)
108 | Registers | 0x0000 | 0 | NA | U16 |  |  | RO | 1 | → | NA |  | Ref(100%)
109 | Registers | 0x0356 | 854 | Pac H /High Byte of Power | U16 |  |  | RO | 1 | → | HIGH_BYTE_OF_PV_MODE_SMT_ONLY |  | Ref(60%)
110 | Registers | 0x0357 | 855 | Vpv3 /PV3 input voltage | U16 |  |  | RO | 1 | → | PV3_VOLTAGE |  | Ref(67%)
111 | Registers | 0x0358 | 856 | Vpv4 /PV4 input voltage | U16 |  |  | RO | 1 | → | PV4_VOLTAGE |  | Ref(67%)
112 | Registers | 0x0359 | 857 | Ipv3 /PV3 input current | U16 |  |  | RO | 1 | → | PV3_CURRENT |  | Ref(67%)
113 | Registers | 0x035A | 858 | Ipv4 /PV4 input current | U16 |  |  | RO | 1 | → | PV4_CURRENT |  | Ref(67%)
114 | Registers | 0x035B | 859 | Istr1/PV String1 Current | U16 |  |  | RO | 1 | → | STRING1_CURRENT |  | Ref(77%)
115 | Registers | 0x035C | 860 | Istr2/PV String2 Current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(77%)
116 | Registers | 0x035D | 861 | Istr3/PV String3 Current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(77%)
117 | Registers | 0x035E | 862 | Istr4/PV String4 Current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(77%)
118 | Registers | 0x035F | 863 | Istr5/PV String5 Current | U16 |  |  | RO | 1 | → | STRING5_CURRENT |  | Ref(77%)
119 | Registers | 0x0360 | 864 | Istr6/PV String6 Current | U16 |  |  | RO | 1 | → | STRING6_CURRENT |  | Ref(77%)
120 | Registers | 0x0361 | 865 | Istr7/PV String7 Current | U16 |  |  | RO | 1 | → | STRING7_CURRENT |  | Ref(77%)
121 | Registers | 0x0362 | 866 | Istr8/PV String8 Current | U16 |  |  | RO | 1 | → | STRING8_CURRENT |  | Ref(77%)
122 | Registers | 0x0363 | 867 | Istr9/PV String9 Current | U16 |  |  | RO | 1 | → | STRING9_CURRENT |  | Ref(77%)
123 | Registers | 0x0364 | 868 | Istr10/PV String10 Current | U16 |  |  | RO | 1 | → | STRING1_CURRENT |  | Ref(73%)
124 | Registers | 0x0365 | 869 | Istr11/PV String11 Current | U16 |  |  | RO | 1 | → | IV_STRING1_1_CURRENT_BASE |  | Ref(75%)
125 | Registers | 0x0366 | 870 | Istr12/PV String12 Current | U16 |  |  | RO | 1 | → | IV_STRING1_2_CURRENT_BASE |  | Ref(75%)
126 | Registers | 0x0367 | 871 | Istr13/PV String13 Current | U16 |  |  | RO | 1 | → | STRING3_CURRENT |  | Ref(73%)
127 | Registers | 0x0368 | 872 | Istr14/PV String14 Current | U16 |  |  | RO | 1 | → | STRING4_CURRENT |  | Ref(73%)
128 | Registers | 0x0369 | 873 | Istr15/PV String15 Current | U16 |  |  | RO | 1 | → | STRING5_CURRENT |  | Ref(73%)
129 | Registers | 0x036A | 874 | Istr16/PV String16 Current | U16 |  |  | RO | 1 | → | STRING6_CURRENT |  | Ref(73%)
130 | Registers | 0x036B | 875 | Istr17/PV String17 Current | U16 |  |  | RO | 1 | → | STRING7_CURRENT |  | Ref(73%)
131 | Registers | 0x036C | 876 | Istr18/PV String18 Current | U16 |  |  | RO | 1 | → | STRING8_CURRENT |  | Ref(73%)
132 | Registers | 0x036D | 877 | Istr19/PV String19 Current | U16 |  |  | RO | 1 | → | STRING9_CURRENT |  | Ref(73%)
133 | Registers | 0x036E | 878 | Istr20/PV String20 Current | U16 |  |  | RO | 1 | → | STRING2_CURRENT |  | Ref(73%)
134 | Registers | 0x036F | 879 | PID&SPD Status | U16 |  |  | RO | 1 | → | IV_SCAN_STATUS |  | Ref(67%)
135 | Registers | 0x0370 | 880 | Output control state | U16 |  |  | RO | 1 | → | OUTPUT_CONTROL_STATE |  | Ref(100%)
136 | Registers | 0x0376 | 886 | Power Factor | U16 |  |  | RO | 1 | → | POWER_FACTOR | 0x103D | Auto
137 | Registers | 0x03E8 | 1000 | NA Power Factor | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW | 0x03E8 | Auto
138 | Registers | 0x037D | 893 | High Byte of AC reactive power | U16 |  |  | RO | 1 | → | GRID_TOTAL_REACTIVE_POWER_LOW |  | Ref(68%)
139 | Registers | 0x03E8 | 1000 | kVar AC reactive power high byte | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW | 0x03E8 | Auto
140 | Registers | 0x037E | 894 | Low Byte of AC reactive power | U16 |  |  | RO | 1 | → | DEA_REACTIVE_POWER_LOW |  | Ref(67%)
141 | Registers | 0x03E8 | 1000 | kVar AC reactive power low byte | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW | 0x03E8 | Auto
142 | Registers | 0x037F | 895 | ISO detection value | U16 |  |  | RO | 1 | → | ISO_DETECTION_VALUE |  | Ref(100%)
143 | Registers | 0x0380 | 896 | Leak current Value | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW |  | Ref(67%)
144 | Registers | 0x03E8 | 1000 | Current R phase size | U32 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW | 0x03E8 | Auto
145 | Registers | 0x03EA | 1002 | Current S phase size | U32 |  |  | RO | 1 | → | DEA_L2_CURRENT_LOW | 0x03EA | Auto
146 | Registers | 0x03EC | 1004 | Current T phase size | U32 |  |  | RO | 1 | → | DEA_L3_CURRENT_LOW | 0x03EC | Auto
147 | Registers | 0x03EE | 1006 | Current R phase size | U32 |  |  | RO | 1 | → | DEA_L1_VOLTAGE_LOW | 0x03EE | Auto
148 | Registers | 0x03F0 | 1008 | Current S phase size | U32 |  |  | RO | 1 | → | DEA_L2_VOLTAGE_LOW | 0x03F0 | Auto
149 | Registers | 0x03F2 | 1010 | Current T phase size | U32 |  |  | RO | 1 | → | DEA_L3_VOLTAGE_LOW | 0x03F2 | Auto
150 | Registers | 0x03F4 | 1012 | 3 phase effective power | U32 |  |  | RO | 1 | → | DEA_TOTAL_ACTIVE_POWER_LOW | 0x03F4 | Auto
151 | Registers | 0x03F6 | 1014 | 3 phase ineffective power | U32 |  |  | RO | 1 | → | DEA_TOTAL_REACTIVE_POWER_LOW | 0x03F6 | Auto
152 | Registers | 0x03F8 | 1016 | 3 Phase force rate | U16 |  |  | RO | 1 | → | DEA_POWER_FACTOR_LOW | 0x03F8 | Auto
153 | Registers | 0x03E8 | 1000 | 0.001 (+ PF): 800~1000 (- PF):-800~- 1000,-1000 Handled as PF=1 | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW | 0x03E8 | Auto
154 | Registers | 0x03FA | 1018 | Frequency | U32 |  |  | RO | 1 | → | DEA_FREQUENCY_LOW | 0x03FA | Auto
155 | Registers | 0x03FC | 1020 | Status Flag1 | U32 |  |  | RO | 1 | → | DEA_STATUS_FLAG_LOW | 0x03FC | Auto
156 | Registers | 0x07D0 | 2000 | PF WR | S16 |  |  | RO | 1 | → | DER_POWER_FACTOR_SET | 0x07D0 | Auto
157 | Registers | 0x03E8 | 1000 | 0.001 (+ PF): 800~1000 (- PF):-800~-990 | U16 |  |  | RO | 1 | → | DEA_L1_CURRENT_LOW | 0x03E8 | Auto
158 | Registers | 0x07D1 | 2001 | Work and Mode WR | U16 |  |  | RO | 1 | → | DER_ACTION_MODE | 0x07D1 | Auto
159 | Registers | 0x07D2 | 2002 | Constant Reactive Power WR | S16 |  |  | RO | 1 | → | DER_REACTIVE_POWER_PCT | 0x07D2 | Auto
160 | Registers | 0x07D3 | 2003 | Constant Active Power WR | U16 |  |  | RO | 1 | → | DER_ACTIVE_POWER_PCT | 0x07D3 | Auto
161 | Registers | 0x0002 | 2 | Utility Loss 1. Grid power fails.¦2. AC connection is not good.¦3. AC breaker fails 4. Grid is not connected. Bit8 | U16 |  |  | RO | 1 | → | UTILITY_LOSS_1_GRID_POWER_FAILS_2_AC_CONNECTION_IS_NOT_GOOD_3_AC_BREAKER_FAILS_4_GRID_IS_NOT_CONNECTED_BIT8 |  | Ref(100%)
162 | Registers | 0x0001 | 1 | AC HCT Fail 1. An occasional situation, caused by external factors like external magnetic field etc.¦2. Control board has a problem. Bit7 | U16 |  |  | RO | 1 | → | AC_HCT_FAIL_1_AN_OCCASIONAL_SITUATION_CAUSED_BY_EXTERNAL_FACTORS_LIKE_EXTERNAL_MAGNETIC_FIELD_ETC_2_CONTROL_BOARD_HAS_A_PROBLEM_BIT7 |  | Ref(100%)
163 | Registers | 0x0000 | 0 | Relay Fail 1. An occasional situation, caused by external factors like external magnetic field etc.¦2. Control board has a problem. Bit6 | U16 |  |  | RO | 1 | → | RELAY_FAIL_1_AN_OCCASIONAL_SITUATION_CAUSED_BY_EXTERNAL_FACTORS_LIKE_EXTERNAL_MAGNETIC_FIELD_ETC_2_CONTROL_BOARD_HAS_A_PROBLEM_BIT6 |  | Ref(100%)
164 | Registers | 0x0000 | 0 | GFCI Fail 1. An occasional situation, caused by external factors like external magnetic field etc.¦2. Control board has a problem. Bit5 | U16 |  |  | RO | 1 | → | GFCI_FAIL_1_AN_OCCASIONAL_SITUATION_CAUSED_BY_EXTERNAL_FACTORS_LIKE_EXTERNAL_MAGNETIC_FIELD_ETC_2_CONTROL_BOARD_HAS_A_PROBLEM_BIT5 |  | Ref(100%)
165 | Registers | 0x0000 | 0 | 00000020 Please contact after sales. Bit4 | U16 |  |  | RO | 1 | → | REG_00000020_PLEASE_CONTACT_AFTER_SALES_BIT4 |  | Ref(100%)
166 | Registers | 0x0000 | 0 | DC SPD Fail Inverter suffering from lighting strike Bit3 | U16 |  |  | RO | 1 | → | DC_SPD_FAIL_INVERTER_SUFFERING_FROM_LIGHTING_STRIKE_BIT3 |  | Ref(100%)
167 | Registers | 0x0000 | 0 | DC Switch Fail The number of times of use of the DC trip switch exceeds the service life Bit2 | U16 |  |  | RO | 1 | → | DC_SWITCH_FAIL_THE_NUMBER_OF_TIMES_OF_USE_OF_THE_DC_TRIP_SWITCH_EXCEEDS_THE_SERVICE_LIFE_BIT2 |  | Ref(100%)
168 | Registers | 0x0000 | 0 | Ref 1.5V Fail 1. An occasional situation, caused by external factors like external magnetic field etc.¦2. Control board has a problem. Bit1 | U16 |  |  | RO | 1 | → | REF_1_5V_FAIL_1_AN_OCCASIONAL_SITUATION_CAUSED_BY_EXTERNAL_FACTORS_LIKE_EXTERNAL_MAGNETIC_FIELD_ETC_2_CONTROL_BOARD_HAS_A_PROBLEM_BIT1 |  | Ref(100%)
169 | Registers | 0x0000 | 0 | AC HCT Check Fail 1. Try to restart inverter, check if it still happens, if not, means it is just an occasional situation.¦2. If restart cannot solve the problem, Please contact after sales. Bit0 | U16 |  |  | RO | 1 | → | AC_HCT_CHECK_FAIL_1_TRY_TO_RESTART_INVERTER_CHECK_IF_IT_STILL_HAPPENS_IF_NOT_MEANS_IT_IS_JUST_AN_OCCASIONAL_SITUATION_2_IF_RESTART_CANNOT_SOLVE_THE_PROBLEM_PLEASE_CONTACT_AFTER_SALES_BIT0 |  | Ref(100%)
170 | Registers | 0x0000 | 0 | GFCI Check Fail 1. Try to restart inverter, check if it still happens, if not, means it is just an occasional situation.¦2. If restart cannot solve the problem, Please contact after sales. Table 8-3 Bit No Status 1 | U16 |  |  | RO | 1 | → | GFCI_CHECK_FAIL_1_TRY_TO_RESTART_INVERTER_CHECK_IF_IT_STILL_HAPPENS_IF_NOT_MEANS_IT_IS_JUST_AN_OCCASIONAL_SITUATION_2_IF_RESTART_CANNOT_SOLVE_THE_PROBLEM_PLEASE_CONTACT_AFTER_SALES_TABLE_8_3_BIT_NO_STATUS_1 |  | Ref(100%)
Mode: OFFLINE ¦ Match stats: Auto/Ref=170, Unmapped=0 ¦ Edit "Solarize_Name" for Unmapped rows (red = needs review).

## Status_Mapping
Raw_Code | Raw_Name | InverterMode_State | Solarize_Code | Notes
3 | Set : Separate, Reset : Contact 1 | Unknown |  | Review - could not auto-match
0 | Separate operation | Unknown |  | Review - could not auto-match
NOTE: Edit "InverterMode_State" column: INITIAL/STANDBY/ON_GRID/FAULT/SHUTDOWN

## DER_AVM_Control
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x07D0 | 2000 | DER_POWER_FACTOR_SET | S16 | FC06 | 1 |  | 0.001 | RW | Power factor setpoint [-1000,-800],[800,1000]
0x07D1 | 2001 | DER_ACTION_MODE | U16 | FC06 | 1 |  | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
0x07D2 | 2002 | DER_REACTIVE_POWER_PCT | S16 | FC06 | 1 | % | 0.1 | RW | Reactive power % [-484,484]
0x07D3 | 2003 | DER_ACTIVE_POWER_PCT | U16 | FC06 | 1 | % | 0.1 | RW | Active power % [0,1100]
0x0834 | 2100 | INVERTER_ON_OFF | U16 | FC06 | 1 |  | 1 | RW | On/Off control: 0=ON, 1=OFF
0x0835 | 2101 | CLEAR_PV_INSULATION_WARNING | U16 | FC06 | 1 |  | 1 | WO | Clear PV insulation warning: 1=Clear
0x6001 | 24577 | INVERTER_CONTROL | U16 | FC06 | 1 |  | 1 | WO | Inverter control: 0=Power on, 1=Shut down
0x600D | 24589 | IV_CURVE_SCAN | U16 | FC06 | 1 |  | 1 | RW | IV curve scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
0x600F | 24591 | POWER_FACTOR_DYNAMIC | S16 | FC06 | 1 |  | 0.001 | RW | Dynamic power factor control
0x6010 | 24592 | REACTIVE_POWER_DYNAMIC | S16 | FC06 | 1 | % | 0.01 | RW | Dynamic reactive power control (%)
0x3005 | 12293 | POWER_DERATING_PCT | U16 | FC06 | 1 | % | 1 | RW | Active power derating [0-110]%
NOTE: DER-AVM control registers (always included). Do not modify addresses.

## DEA_AVM_Monitor
Address_Hex | Address_Dec | Name | Data_Type | FC | Registers | Unit | Scale | R/W | Description
0x03E8 | 1000 | DEA_L1_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L1 current (low word)
0x03E9 | 1001 | DEA_L1_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 current (high word)
0x03EA | 1002 | DEA_L2_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L2 current (low word)
0x03EB | 1003 | DEA_L2_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 current (high word)
0x03EC | 1004 | DEA_L3_CURRENT_LOW | S32 | FC03 | 2 | A | 0.1 | RO | DEA L3 current (low word)
0x03ED | 1005 | DEA_L3_CURRENT_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 current (high word)
0x03EE | 1006 | DEA_L1_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L1 voltage (low word)
0x03EF | 1007 | DEA_L1_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L1 voltage (high word)
0x03F0 | 1008 | DEA_L2_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L2 voltage (low word)
0x03F1 | 1009 | DEA_L2_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L2 voltage (high word)
0x03F2 | 1010 | DEA_L3_VOLTAGE_LOW | S32 | FC03 | 2 | V | 0.1 | RO | DEA L3 voltage (low word)
0x03F3 | 1011 | DEA_L3_VOLTAGE_HIGH | S32 | FC03 | 1 |  |  | RO | DEA L3 voltage (high word)
0x03F4 | 1012 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | FC03 | 2 | kW | 0.1 | RO | DEA total active power (low word)
0x03F5 | 1013 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total active power (high word)
0x03F6 | 1014 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | FC03 | 2 | Var | 1 | RO | DEA total reactive power (low word)
0x03F7 | 1015 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | FC03 | 1 |  |  | RO | DEA total reactive power (high word)
0x03F8 | 1016 | DEA_POWER_FACTOR_LOW | S32 | FC03 | 2 |  | 0.001 | RO | DEA power factor (low word)
0x03F9 | 1017 | DEA_POWER_FACTOR_HIGH | S32 | FC03 | 1 |  |  | RO | DEA power factor (high word)
0x03FA | 1018 | DEA_FREQUENCY_LOW | S32 | FC03 | 2 | Hz | 0.1 | RO | DEA frequency (low word)
0x03FB | 1019 | DEA_FREQUENCY_HIGH | S32 | FC03 | 1 |  |  | RO | DEA frequency (high word)
0x03FC | 1020 | DEA_STATUS_FLAG_LOW | S32 | FC03 | 2 |  | 1 | RO | DEA status flag (low word)
0x03FD | 1021 | DEA_STATUS_FLAG_HIGH | S32 | FC03 | 1 |  |  | RO | DEA status flag (high word)
NOTE: DEA-AVM monitoring registers (always included). Do not modify addresses.