## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=6, STR=18)
제조사 | GoodWe
용량 | -
MPPT | 6
String/MPPT | 3
Total Strings | 18
H01 매칭 | 50/50
DER 매칭 | 33/33
총 레지스터 | 139
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Device SerialNumber | 0x0200 | STRING | 1 | RO |  | ASCII code, 16 bytes
2 | Device Type | 0x0210 | STRING | 1 | RO |  | ASCII code, 16 bytes
3 | Inverter internaltemperature | 0x0235 | U16 | 10 | RO |  | Inverter internal temperature
4 | Inverter internaltemperature | 0x030F | U16 | 10 | RO |  | Inverter internal temperature
5 | FirmwareVersion | 0x0316 | U16 | 1 | RO |  | Firmware Version
6 | BUS Voltage | 0x031C | U16 | V 10 | RO |  | BUS Voltage
7 | NBUS Voltage | 0x031D | U16 | V 10 | RO |  | NBUS Voltage
8 | FirmwareVersion of ARM | 0x0354 | U16 |  | RO
9 | 1. Safety country of Inverter is set wrong.¦2. Grid voltageis not stable.¦3. AC (to grid) cable too small or too long | 0x20000 | U16 |  | RO
10 | 1. The Ground cable of panels is not connected or notconnected well.¦2. DC cable is broken.¦3. Neutral &ground cable are not connected well on AC side.¦4. TheISO failure happens on rainy days or early morning orsunset, when the humidity is comparatively heavy. | 0x40000 | U16 |  | RO
11 | 1. Cable between control board and power board (forDT) is not tight.¦2. Neutral & ground cable are notconnected well on AC side. ¦3. Control board problem. | 0x2000000 | U16 |  | RO
12 | 1. Safety country of Inverter is set wrong.¦2. Gridfrequency is not stable. | 0x20000000 | U16 |  | RO
H01 MONITORING (112개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Power onvoltage | 0x0000 | U16 | V 10 | RW
2 | Lower limit ofgrid voltage | 0x0002 | U16 | V 10 | RW
3 | Upper limit ofgrid voltage | 0x0003 | U16 | V 10 | RW
4 | Lower limit ofgrid frequency | 0x0004 | U16 | Hz 100 | RW
5 | Upper limit ofgrid frequency | 0x0005 | U16 | Hz 100 | RW
6 | Bit3 | 0x0008 | U16 |  | RO
7 | Bit5 | 0x0020 | U16 |  | RO
8 | Bit6 | 0x0040 | U16 |  | RO
9 | Bit7 | 0x0080 | U16 |  | RO
10 | Active poweradjust | 0x0100 | U16 | 1 | RW
11 | PF reactivepower adjust | 0x0101 | U16 | 1 | RW
12 | Reactive poweradjust | 0x0102 | S32 | 1 | RW
13 | Max value ofreactive power | 0x0104 | U32 | 1 | RO
14 | Export PowerLimit AdjustRange | 0x0106 | S16 | 1 | WO
15 | Export powerlimitCommunicationOvertime set | 0x010B | U16 |  | RW
16 | Power On(Allowon grid self-test) | 0x0120 | U16 |  | WO
17 | Power Off(Notallow on gridself-test) | 0x0121 | U16 |  | WO
18 | AutomaticReactive powerAdjust | 0x0130 | U16 |  | WO
19 | AutomaticReactive powerAdjust ID | 0x0131 | U32 |  | WO
20 | Battery Voltageset(Brazil) | 0x0134 | U16 | V 10 | WO
21 | High Byte ofTotal FeedPower to grid/Total powergeneration | 0x0222 | U16 | KWH 10 | RO | cumulative_energy
22 | Low Byte ofTotal FeedPower togrid/Total powergeneration | 0x0223 | U16 | KWH 10 | RO | cumulative_energy_low
23 | High Byte ofTotal feedinghours/Hourlypowergeneration | 0x0224 | U16 | 1 | RO | cumulative_energy
24 | Low Byte ofTotal feedinghours/Hourlypowergeneration | 0x0225 | U16 | 1 | RO | cumulative_energy_low
25 | Vpv1 /PPV1input voltage | 0x0226 | U16 | V 10 | RO | mppt1_voltage
26 | Vpv2 /PV2 inputvoltage | 0x0227 | U16 | V 10 | RO | mppt2_voltage
27 | Ipv1 /PV1 inputcurrent | 0x0228 | U16 | A 10 | RO | mppt1_current
28 | Ipv2 /PV2 inputcurrent | 0x0229 | U16 | A 10 | RO | mppt2_current
29 | Vac1 /L1 Phasevoltage | 0x022A | U16 | V 10 | RO
30 | Vac2 /L2 Phasevoltage | 0x022B | U16 | V 10 | RO
31 | Vac3 /L3 Phasevoltage | 0x022C | U16 | V 10 | RO
32 | Iac1 /L1 Phasecurrent | 0x022D | U16 | A 10 | RO
33 | Iac2 /L2 Phasecurrent | 0x022E | U16 | A 10 | RO
34 | Iac3 /L3 Phasecurrent | 0x022F | U16 | A 10 | RO
35 | Fac1 /L1 Phasefrequency | 0x0230 | U16 | Hz 100 | RO
36 | Fac2 /L2 Phasefrequency | 0x0231 | U16 | Hz 100 | RO
37 | Fac3 /L3 Phasefrequency | 0x0232 | U16 | Hz 100 | RO
38 | Pac L /Invertercurrent outputpower | 0x0233 | U16 | W 1 | RO | pv_power
39 | E-Day /Dailypowergeneration | 0x0236 | U16 | KWH 10 | RO
40 | Vpv1 /PV1 inputvoltage | 0x0300 | U16 | V 10 | RO | mppt1_voltage
41 | Vpv2 /PV2 inputvoltage | 0x0301 | U16 | V 10 | RO | mppt2_voltage
42 | Ipv1 /PV1 inputcurrent | 0x0302 | U16 | A 10 | RO | mppt1_current
43 | Ipv2 /PV2 inputcurrent | 0x0303 | U16 | A 10 | RO | mppt2_current
44 | Vac1 /L1 Phasevoltage | 0x0304 | U16 | V 10 | RO
45 | Vac2 /L2 Phasevoltage | 0x0305 | U16 | V 10 | RO
46 | Vac3 /L3 Phasevoltage | 0x0306 | U16 | V 10 | RO
47 | Iac1 /L1 Phasecurrent | 0x0307 | U16 | A 10 | RO
48 | Iac2 /L2 Phasecurrent | 0x0308 | U16 | A 10 | RO
49 | Iac3 /L3 Phasecurrent | 0x0309 | U16 | A 10 | RO
50 | Fac1 /L1 Phasefrequency | 0x030A | U16 | Hz 100 | RO
51 | Fac2 /L2 Phasefrequency | 0x030B | U16 | Hz 100 | RO
52 | Fac3 /L3 Phasefrequency | 0x030C | U16 | Hz 100 | RO
53 | Pac L /Invertercurrent outputpower | 0x030D | U16 | W 1 | RO | pv_power
54 | High Byte ofTotal FeedPower togrid/Total powergeneration | 0x0312 | U16 | KWH 10 | RO | cumulative_energy
55 | Low Byte ofTotal FeedPower togrid/Total powergeneration | 0x0313 | U16 | KWH 10 | RO | cumulative_energy_low
56 | High Byte ofTotal feedinghours/Hourlypowergeneration | 0x0314 | U16 | 1 | RO | cumulative_energy
57 | Low Byte ofTotal feedinghours/Hourlypowergeneration | 0x0315 | U16 | 1 | RO | cumulative_energy_low
58 | RSVD | 0x0318 | U16 | V 10 | RO
59 | RSVD | 0x031A | U16 | V 10 | RO
60 | RSVD | 0x031B | U16 | V 10 | RO
61 | RSVD | 0x031E | U16 | Hz 100 | RO
62 | Safety Code | 0x031F | U16 | 1 | RO
63 | Feed Power togrid in today/Daily power | 0x0320 | U16 | KWH 10 | RO
64 | Vpv5 /PV5 inputvoltage | 0x0324 | U16 |  | RO | mppt5_voltage
65 | Ipv5 /PV5 inputcurrent | 0x0325 | U16 |  | RO | mppt5_current
66 | Vpv6 /PV6 inputvoltage | 0x0326 | U16 |  | RO | mppt6_voltage
67 | Ipv6 /PV6 inputcurrent | 0x0327 | U16 |  | RO | mppt6_current
68 | Year :Month | 0x033B | U16 |  | RO
69 | Date :Hour | 0x033C | U16 |  | RO
70 | Minute :Second | 0x033D | U16 |  | RO
71 | Manufacture ID | 0x033E | U16 |  | RO
72 | Wireless signalstrength | 0x033F | U16 |  | RO
73 | High Byte ofPower | 0x0352 | U16 |  | RO
74 | Low Byte ofPower | 0x0353 | U16 |  | RO
75 | Pac H /High Byteof Power | 0x0356 | U16 |  | RO | pv_power
76 | Vpv3 /PV3 inputvoltage | 0x0357 | U16 |  | RO | mppt3_voltage
77 | Vpv4 /PV4 inputvoltage | 0x0358 | U16 |  | RO | mppt4_voltage
78 | Ipv3 /PV3 inputcurrent | 0x0359 | U16 |  | RO | mppt3_current
79 | Ipv4 /PV4 inputcurrent | 0x035A | U16 |  | RO | mppt4_current
80 | Istr1/PV String1Current | 0x035B | U16 |  | RO | string1_current
81 | Istr2/PV String2Current | 0x035C | U16 |  | RO | string2_current
82 | Istr3/PV String3Current | 0x035D | U16 |  | RO | string3_current
83 | Istr4/PV String4Current | 0x035E | U16 | A 10 | RO | string4_current
84 | Istr5/PV String5Current | 0x035F | U16 | A 10 | RO | string5_current
85 | Istr6/PV String6Current | 0x0360 | U16 | A 10 | RO | string6_current
86 | Istr7/PV String7Current | 0x0361 | U16 | A 10 | RO | string7_current
87 | Istr8/PV String8Current | 0x0362 | U16 | A 10 | RO | string8_current
88 | Istr9/PV String9Current | 0x0363 | U16 | A 10 | RO | string9_current
89 | Istr10/PVString10 Current | 0x0364 | U16 | A 10 | RO | string10_current
90 | Istr11/PVString11 Current | 0x0365 | U16 | A 10 | RO | string11_current
91 | Istr12/PVString12 Current | 0x0366 | U16 | A 10 | RO | string12_current
92 | Istr13/PVString13 Current | 0x0367 | U16 | A 10 | RO | string13_current
93 | Istr14/PVString14 Current | 0x0368 | U16 | A 10 | RO | string14_current
94 | Istr15/PVString15 Current | 0x0369 | U16 | A 10 | RO | string15_current
95 | Istr16/PVString16 Current | 0x036A | U16 | A 10 | RO | string16_current
96 | Istr17/PVString17 Current | 0x036B | U16 | A 10 | RO | string17_current
97 | Istr18/PVString18 Current | 0x036C | U16 | A 10 | RO | string18_current
98 | Power Factor | 0x0376 | U16 | 1000 | RO | power_factor
99 | High Byte of ACreactive power | 0x037D | U16 | 1000 | RO
100 | Low Byte of ACreactive power | 0x037E | U16 | 1000 | RO
101 | Leak currentValue | 0x0380 | U16 | 1 | RO
102 | Bit10 | 0x0400 | U16 |  | RO
103 | Bit11 | 0x0800 | STRINGING |  | RO
104 | Bit12 | 0x1000 | U16 |  | RO
105 | Bit13 | 0x2000 | U16 |  | RO
106 | Bit14 | 0x4000 | U16 |  | RO
107 | Bit15 | 0x8000 | U16 |  | RO
108 | Bit16 | 0x10000 | U16 |  | RO
109 | Inverter detects a higher DC component in AC output. | 0x80000 | U16 |  | RO
110 | The cable inside for communication of LCD gets loosen. | 0x100000 | U16 |  | RO
111 | Some string current is too high. | 0x200000 | STRINGING |  | RO
112 | 1. PV string reverse connection | 0x400000 | STRINGING |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Battery ModeSwitch(Brazil) | 0x0133 | U16 | 1 | WO |  | 0-Off,1-On
2 | Shadow modeswitch | 0x0138 | U16 | 1 | RW |  | 0-Off,1-On
3 | Work Mode | 0x0234 | U16 | 1 | RO | inverter_status | 0:cWaitMode1:cNormalMode2:cFaultMode
4 | Work Mode | 0x030E | U16 | 1 | RO | inverter_status | 0:cWaitMode1:cNormalMode2:cFaultMode
5 | Function StatusBits | 0x0319 | U16 | A 1 | RO |  | Table 8-3
6 | High Byte of PVMode（SMTonly） | 0x0340 | U16 |  | RO
7 | Low Byte of PVMode（SMTonly） | 0x0341 | U16 |  | RO
8 | GPRS Burn-inMode | 0x0355 | U16 |  | RO
9 | PID&SPD Status | 0x036F | U16 | 1 | RO |  | Table 8-6
10 | Output controlstate | 0x0370 | U16 | 1 | RO |  | For Japanese models: 0-unprotected, 1-protected
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Error Message | 0x0220 | U32 | 1 | RO |  | Failure description for status‘failure’ Table8-2
2 | Error Message H | 0x0310 | U16 | 1 | RO |  | Failure description for status‘failure’ Table8-2
3 | Error Message L | 0x0311 | U16 | 1 | RO |  | Failure description for status‘failure’ Table8-2
4 | Warning Code | 0x0317 | U16 | 1 | RO |  | Warning Code
5 | 1. The device is abnormal | 0x8000000 | U16 |  | RO

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | GoodWe
용량 | -
MPPT | 6 (PDF max 6개)
String | 18 (3/MPPT)
H01 매칭 | 50/50
DER 매칭 | 33/33
총 레지스터 | 139
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 12
MONITORING | 112
STATUS | 10
ALARM | 5
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | PDF | O | 0x0233 | Pac L /Invertercurrent outputpower
13 | cumulative_energy | PDF | O | 0x0222 | High Byte ofTotal FeedPower to grid/Total powergeneration
14 | cumulative_energy_low | PDF | O | 0x0223 | Low Byte ofTotal FeedPower togrid/Total powergeneration
15 | status | PDF | O | 0x0234 | Work Mode
16 | alarm1 | PDF | O | 0x0220 | Error Message
17 | alarm2 | PDF | O | 0x0310 | Error Message H
18 | alarm3 | PDF | O | 0x0311 | Error Message L
19 | mppt1_voltage | PDF | O | 0x0226 | Vpv1 /PPV1input voltage
20 | mppt1_current | PDF | O | 0x0228 | Ipv1 /PV1 inputcurrent
21 | mppt2_voltage | PDF | O | 0x0227 | Vpv2 /PV2 inputvoltage
22 | mppt2_current | PDF | O | 0x0229 | Ipv2 /PV2 inputcurrent
23 | mppt3_voltage | PDF | O | 0x0357 | Vpv3 /PV3 inputvoltage
24 | mppt3_current | PDF | O | 0x0359 | Ipv3 /PV3 inputcurrent
25 | mppt4_voltage | PDF | O | 0x0358 | Vpv4 /PV4 inputvoltage
26 | mppt4_current | PDF | O | 0x035A | Ipv4 /PV4 inputcurrent
27 | mppt5_voltage | PDF | O | 0x0324 | Vpv5 /PV5 inputvoltage
28 | mppt5_current | PDF | O | 0x0325 | Ipv5 /PV5 inputcurrent
29 | mppt6_voltage | PDF | O | 0x0326 | Vpv6 /PV6 inputvoltage
30 | mppt6_current | PDF | O | 0x0327 | Ipv6 /PV6 inputcurrent
31 | string1_current | PDF | O | 0x035B | Istr1/PV String1Current
32 | string2_current | PDF | O | 0x035C | Istr2/PV String2Current
33 | string3_current | PDF | O | 0x035D | Istr3/PV String3Current
34 | string4_current | PDF | O | 0x035E | Istr4/PV String4Current
35 | string5_current | PDF | O | 0x035F | Istr5/PV String5Current
36 | string6_current | PDF | O | 0x0360 | Istr6/PV String6Current
37 | string7_current | PDF | O | 0x0361 | Istr7/PV String7Current
38 | string8_current | PDF | O | 0x0362 | Istr8/PV String8Current
39 | string9_current | PDF | O | 0x0363 | Istr9/PV String9Current
40 | string10_current | PDF | O | 0x0364 | Istr10/PVString10 Current
41 | string11_current | PDF | O | 0x0365 | Istr11/PVString11 Current
42 | string12_current | PDF | O | 0x0366 | Istr12/PVString12 Current
43 | string13_current | PDF | O | 0x0367 | Istr13/PVString13 Current
44 | string14_current | PDF | O | 0x0368 | Istr14/PVString14 Current
45 | string15_current | PDF | O | 0x0369 | Istr15/PVString15 Current
46 | string16_current | PDF | O | 0x036A | Istr16/PVString16 Current
47 | string17_current | PDF | O | 0x036B | Istr17/PVString17 Current
48 | string18_current | PDF | O | 0x036C | Istr18/PVString18 Current
49 | string19_current | PDF | O | 0x036D | Istr19/PVString19 Current
50 | string20_current | PDF | O | 0x036E | Istr20/PVString20 Current