## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | Growatt
프로토콜 버전 | V1.20
설비 타입 | inverter
MPPT | 8
String | 8
String 모니터링 | No (MPPT당 1 String)
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | Growatt PV Inverter Modbus RS485 RTU Protocol v120.pdf
추출 일시 | 2026-04-03 15:58
H01 매칭 | 41/41
DER 매칭 | 33/33
추출 레지스터 | 926
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Fw version H | 0x0009 | 03 | ASCII |  | RO
2 | Fw versionM | 0x000A | 03 | U16 |  | RO
3 | Fw version L | 0x000B | 03 | U16 |  | RO
4 | Fw version2H | 0x000C | 03 | ASCII |  | RO
5 | Fw version2M | 0x000D | 03 | U16 |  | RO
6 | Fw version2L | 0x000E | 03 | U16 |  | RO
7 | Serial NO | 0x0017 | 03 | ASCII |  | RO
8 | Serial NO | 0x0018 | 03 | U16 |  | RO
9 | Serial NO | 0x0019 | 03 | U16 |  | RO
10 | Serial NO | 0x001A | 03 | U16 |  | RO
11 | Serial NO | 0x001B | 03 | U16 |  | RO
12 | Manufacturer Info 8 | 0x0022 | 03 | ASCII |  | RO
13 | Manufacturer Info 7 | 0x0023 | 03 | U16 |  | RO
14 | Manufacturer Info 6 | 0x0024 | 03 | U16 |  | RO
15 | Manufacturer Info 5 | 0x0025 | 03 | U16 |  | RO
16 | Manufacturer Info 4 | 0x0026 | 03 | U16 |  | RO
17 | Manufacturer Info3 | 0x0027 | 03 | U16 |  | RO
18 | Manufacturer Info 2 | 0x0028 | 03 | U16 |  | RO
19 | Manufacturer Info 1 | 0x0029 | 03 | U16 |  | RO
20 | PFModel | 0x0059 | 03 | U16 |  | RO
21 | P Bus Voltage | 0x0062 | 04 | U16 | V 0.1 | RO
22 | N Bus Voltage | 0x0063 | 04 | U16 | V 0.1 | RO
23 | TrakerModel | 0x007C | 03 | U16 |  | RO
24 | PID WorkingModel | 0x00C9 | 03 | U16 |  | RO
25 | NewSerial NO | 0x00D1 | 03 | ASCII |  | RO
26 | NewSerial NO | 0x00D2 | 03 | ASCII |  | RO
27 | NewSerial NO | 0x00D3 | 03 | ASCII |  | RO
28 | NewSerial NO | 0x00D4 | 03 | ASCII |  | RO
29 | NewSerial NO | 0x00D5 | 03 | ASCII |  | RO
30 | NewSerial NO | 0x00D6 | 03 | ASCII |  | RO
31 | NewSerial NO | 0x00D7 | 03 | ASCII |  | RO
32 | NewSerial NO | 0x00D8 | 03 | ASCII |  | RO
33 | NewSerial NO | 0x00D9 | 03 | ASCII |  | RO
34 | NewSerial NO | 0x00DA | 03 | ASCII |  | RO
35 | NewSerial NO | 0x00DB | 03 | ASCII |  | RO
36 | NewSerial NO | 0x00DC | 03 | ASCII |  | RO
37 | NewSerial NO | 0x00DD | 03 | ASCII |  | RO
38 | NewSerial NO | 0x00DE | 03 | ASCII |  | RO
39 | NewSerial NO | 0x00DF | 03 | ASCII |  | RO
40 | SP Bus Volt | 0x0412 | 04 | U16 | V 0.1 | RO
41 | dwExportLimitApparentPower | 0x0428 | 04 | U16 | kWh 0.1 | RO
42 | dwExportLimitApparentPower | 0x0429 | 04 | U16 | kWh 0.1 | RO
43 | P Bus Voltage | 0x0832 | 04 | U16 | V 0.1 | RO
44 | N Bus Voltage | 0x0833 | 04 | U16 | V 0.1 | RO
45 | NewSerial NO | 0x0BB9 | 03 | ASCII |  | R/W
46 | NewSerial NO | 0x0BBA | 03 | ASCII |  | R/W
47 | NewSerial NO | 0x0BBB | 03 | ASCII |  | R/W
48 | NewSerial NO | 0x0BBC | 03 | ASCII |  | R/W
49 | NewSerial NO | 0x0BBD | 03 | ASCII |  | R/W
50 | NewSerial NO | 0x0BBE | 03 | ASCII |  | R/W
51 | NewSerial NO | 0x0BBF | 03 | ASCII |  | R/W
52 | NewSerial NO | 0x0BC0 | 03 | ASCII |  | R/W
53 | NewSerial NO | 0x0BC1 | 03 | ASCII |  | R/W
54 | NewSerial NO | 0x0BC2 | 03 | ASCII |  | R/W
55 | NewSerial NO | 0x0BC3 | 03 | ASCII |  | R/W
56 | NewSerial NO | 0x0BC4 | 03 | ASCII |  | R/W
57 | NewSerial NO | 0x0BC5 | 03 | ASCII |  | R/W
58 | NewSerial NO | 0x0BC6 | 03 | ASCII |  | R/W
59 | NewSerial NO | 0x0BC7 | 03 | ASCII |  | R/W
60 | Serial NO | 0x0C0F | 03 | ASCII |  | R/W
61 | Serial No | 0x0C10 | 03 | ASCII |  | R/W
62 | Serial No | 0x0C11 | 03 | ASCII |  | R/W
63 | Serial No | 0x0C12 | 03 | ASCII |  | R/W
64 | Serial No | 0x0C13 | 03 | ASCII |  | R/W
65 | Model H | 0x0C14 | 03 | U16 |  | R/W
66 | Model L | 0x0C15 | 03 | U16 |  | R/W
67 | P Bus Voltage | 0x0C1A | 04 | U16 | V 0.1 | RO
68 | Bus Voltage error | 0x400000 | 04 | U16 |  | RO
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Inverter Status | 0x0000 | 04 | U16 |  | RO | inverter_status
2 | PF CMDmemorystate | 0x0002 | 03 | U16 |  | RO |  | Means these settings will beacting or not when nextpower on
3 | DeratingMode | 0x0068 | 04 | U16 |  | RO
4 | PID Status | 0x008D | 04 | U16 |  | RO
5 | SVG/APFStatus+SVGAPFEqualRatio | 0x00CE | 04 | U16 |  | RO
6 | bCTMode | 0x040D | 03 | U16 |  | RO
7 | SP DSP Status | 0x0411 | 04 | U16 |  | RO
8 | BMS StatusOld_ | 0x043A | 04 | U16 |  | RO
9 | BMS Status_ | 0x043B | 04 | U16 |  | RO
10 | Inverter Status | 0x0BB8 | 04 | U16 |  | RO | inverter_status
11 | DeratingMode | 0x0C0E | 04 | U16 |  | RO
12 | BDC OnOffState_ | 0x0C2E | 04 | U16 |  | RO
13 | DryContactState | 0x0C2F | 04 | U16 |  | RO
14 | SysState Mode_ | 0x0C5E | 04 | U16 |  | RO | inverter_status
15 | SysState Mode_ | 0x0C75 | 04 | U16 |  | RO | inverter_status
16 | BMS Status_ | 0x0C8C | 04 | U16 |  | RO
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | PV VoltageHigh Fault | 0x0051 | 03 | U16 | V 0.1 | RO
2 | Fault code | 0x0069 | 04 | U16 |  | RO | alarm1
3 | Fault Bitcode H | 0x006A | 04 | U16 |  | RO
4 | Fault Bitcode L | 0x006B | 04 | U16 |  | RO
5 | Warning bit H | 0x006E | 04 | U16 |  | RO
6 | Warning bit L | 0x006F | 04 | U16 |  | RO
7 | bINVAllFaultCode | 0x0073 | 04 | U16 |  | RO
8 | PIDFaultCode | 0x00B1 | 04 | U16 |  | RO
9 | PV Warning Value | 0x00B3 | 04 | U16 |  | RO
10 | DSP075 WarningValue | 0x00B4 | 04 | U16 |  | RO
11 | DSP075 FaultValue | 0x00B5 | 04 | U16 |  | RO
12 | bFanFaultBit | 0x00E5 | 04 | U16 |  | RO
13 | BMS ErrorOld_ | 0x043C | 04 | U16 |  | RO
14 | BMS Error_ | 0x043D | 04 | U16 |  | RO
15 | String12abnormal | 0x0800 | 04 | U16 |  | RO
16 | VbatWarning | 0x0BD1 | 03 | U16 | V 0.1 | R/W
17 | Fault code | 0x0C21 | 04 | U16 |  | RO | alarm1
18 | Warning code | 0x0C22 | 04 | U16 |  | RO
19 | Systemfaultword0 | 0x0C23 | 04 | U16 |  | RO
20 | Systemfaultword1 | 0x0C24 | 04 | U16 |  | RO
21 | Systemfaultword2 | 0x0C25 | 04 | U16 |  | RO
22 | Systemfaultword3 | 0x0C26 | 04 | U16 |  | RO
23 | Systemfaultword4 | 0x0C27 | 04 | U16 |  | RO
24 | Systemfaultword5 | 0x0C28 | 04 | U16 |  | RO
25 | Systemfaultword6 | 0x0C29 | 04 | U16 |  | RO
26 | Systemfaultword7 | 0x0C2A | 04 | U16 |  | RO
27 | FaultCode | 0x0C5F | 04 | U16 |  | RO
28 | FaultCode | 0x0C76 | 04 | U16 |  | RO
29 | BMS Error_ | 0x0C8D | 04 | U16 |  | RO
30 | AFCI Fault | 0x1000 | 04 | U16 |  | RO
31 | String14abnormal | 0x2000 | 04 | U16 |  | RO
32 | AFCI Module fault | 0x4000 | 04 | U16 |  | RO
33 | String16abnormal | 0x8000 | 04 | U16 |  | RO
34 | Relay check fault | 0x20000 | 04 | U16 |  | RO
35 | Communication error | 0x200000 | 04 | U16 |  | RO

## 2_H01
H01 모니터링 매칭 — 41/41
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | PDF | O | 0x0023 | Pac H | U16 | W | 0.1
13 | cumulative_energy | PDF | O | 0x0037 | Eac total H | U16
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x0000 | Inverter Status | U16 |  |  | 1=String1abnormal, 2=String2abnormal, 4=String3abnormal, 8=String4abnormal, 16=String5abnormal, 32=String6abnormal... (+10)
16 | alarm1 | PDF | O | 0x0069 | Fault code | U16 |  |  | 0=Resved;, 1=Resved;, 2=Resved;, 3=Resved;, 4=Resved;, 5=bDischargeEn；... (+8)
17 | alarm2 | PDF | O | 0x0073 | bINVAllFaultCode | U16
18 | alarm3 | PDF | O | 0x00B1 | PIDFaultCode | U16
19 | mppt1_voltage | PDF | O | 0x0003 | Vpv1 | U16 | V | 0.1
20 | mppt1_current | PDF | O | 0x0004 | PV1Curr | U16 | A | 0.1
21 | mppt2_voltage | PDF | O | 0x0007 | Vpv2 | U16 | V | 0.1
22 | mppt2_current | PDF | O | 0x0008 | PV2Curr | U16 | A | 0.1
23 | mppt3_voltage | PDF | O | 0x000B | Vpv3 | U16 | V | 0.1
24 | mppt3_current | PDF | O | 0x000C | PV3Curr | U16 | A | 0.1
25 | mppt4_voltage | PDF | O | 0x000F | Vpv4 | U16 | V | 0.1
26 | mppt4_current | PDF | O | 0x0010 | PV4Curr | U16 | A | 0.1
27 | mppt5_voltage | PDF | O | 0x0013 | Vpv5 | U16 | V | 0.1
28 | mppt5_current | PDF | O | 0x0014 | PV5Curr | U16 | A | 0.1
29 | mppt6_voltage | PDF | O | 0x0017 | Vpv6 | U16 | V | 0.1
30 | mppt6_current | PDF | O | 0x0018 | PV6Curr | U16 | A | 0.1
31 | mppt7_voltage | PDF | O | 0x001B | Vpv7 | U16 | V | 0.1
32 | mppt7_current | PDF | O | 0x001C | PV7Curr | U16 | A | 0.1
33 | mppt8_voltage | PDF | O | 0x001F | Vpv8 | U16 | V | 0.1
34 | mppt8_current | PDF | O | 0x0020 | PV8Curr | U16 | A | 0.1
35 | string1_current | HANDLER | O | 0x0004 | PV1Curr | U16 | A | 0.1
36 | string2_current | HANDLER | O | 0x0008 | PV2Curr | U16 | A | 0.1
37 | string3_current | HANDLER | O | 0x000C | PV3Curr | U16 | A | 0.1
38 | string4_current | HANDLER | O | 0x0010 | PV4Curr | U16 | A | 0.1
39 | string5_current | HANDLER | O | 0x0014 | PV5Curr | U16 | A | 0.1
40 | string6_current | HANDLER | O | 0x0018 | PV6Curr | U16 | A | 0.1
41 | string7_current | HANDLER | O | 0x001C | PV7Curr | U16 | A | 0.1
42 | string8_current | HANDLER | O | 0x0020 | PV8Curr | U16 | A | 0.1

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 8ch / String 8ch
MPPT 채널 수 | 8
String 채널 수 | 8
String 모니터링 | No (MPPT당 1 String)
MPPT 채널 H01 매칭 (16개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | mppt1_voltage | PDF | O | 0x0003 | Vpv1 | U16 | V | 0.1
2 | mppt1_current | PDF | O | 0x0004 | PV1Curr | U16 | A | 0.1
3 | mppt2_voltage | PDF | O | 0x0007 | Vpv2 | U16 | V | 0.1
4 | mppt2_current | PDF | O | 0x0008 | PV2Curr | U16 | A | 0.1
5 | mppt3_voltage | PDF | O | 0x000B | Vpv3 | U16 | V | 0.1
6 | mppt3_current | PDF | O | 0x000C | PV3Curr | U16 | A | 0.1
7 | mppt4_voltage | PDF | O | 0x000F | Vpv4 | U16 | V | 0.1
8 | mppt4_current | PDF | O | 0x0010 | PV4Curr | U16 | A | 0.1
9 | mppt5_voltage | PDF | O | 0x0013 | Vpv5 | U16 | V | 0.1
10 | mppt5_current | PDF | O | 0x0014 | PV5Curr | U16 | A | 0.1
11 | mppt6_voltage | PDF | O | 0x0017 | Vpv6 | U16 | V | 0.1
12 | mppt6_current | PDF | O | 0x0018 | PV6Curr | U16 | A | 0.1
13 | mppt7_voltage | PDF | O | 0x001B | Vpv7 | U16 | V | 0.1
14 | mppt7_current | PDF | O | 0x001C | PV7Curr | U16 | A | 0.1
15 | mppt8_voltage | PDF | O | 0x001F | Vpv8 | U16 | V | 0.1
16 | mppt8_current | PDF | O | 0x0020 | PV8Curr | U16 | A | 0.1
String 채널 H01 매칭 (8개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | string1_current | HANDLER | O | 0x0004 | PV1Curr | U16 | A | 0.1
2 | string2_current | HANDLER | O | 0x0008 | PV2Curr | U16 | A | 0.1
3 | string3_current | HANDLER | O | 0x000C | PV3Curr | U16 | A | 0.1
4 | string4_current | HANDLER | O | 0x0010 | PV4Curr | U16 | A | 0.1
5 | string5_current | HANDLER | O | 0x0014 | PV5Curr | U16 | A | 0.1
6 | string6_current | HANDLER | O | 0x0018 | PV6Curr | U16 | A | 0.1
7 | string7_current | HANDLER | O | 0x001C | PV7Curr | U16 | A | 0.1
8 | string8_current | HANDLER | O | 0x0020 | PV8Curr | U16 | A | 0.1
MONITORING 전체 (732개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | Ppv H | 0x0001 | 04 | U16 | W 0.1 | RO
2 | First Republic | 0x0001 |  | U16 |  | RO
3 | SaftyFuncEn | 0x0001 | 03 | U16 |  | RO
4 | Ppv L | 0x0002 | 04 | U16 | W 0.1 | RO
5 | Vpv1 | 0x0003 | 04 | U16 | V 0.1 | RO | mppt1_voltage
6 | Active PRate | 0x0003 | 03 | U16 |  | RO
7 | PV1Curr | 0x0004 | 04 | U16 | A 0.1 | RO | mppt1_current
8 | Reactive PRate | 0x0004 | 03 | U16 |  | RO
9 | Ppv1 H | 0x0005 | 04 | U16 | W 0.1 | RO | mppt1_power
10 | Power factor | 0x0005 | 03 | U16 |  | RO | power_factor
11 | Ppv1 L | 0x0006 | 04 | U16 | W 0.1 | RO | mppt1_power
12 | Pmax H | 0x0006 | 03 | U16 | VA 0.1 | RO
13 | Vpv2 | 0x0007 | 04 | U16 | V 0.1 | RO | mppt2_voltage
14 | Pmax L | 0x0007 | 03 | U16 | VA 0.1 | RO
15 | PV2Curr | 0x0008 | 04 | U16 | A 0.1 | RO | mppt2_current
16 | Vnormal | 0x0008 | 03 | U16 | V 0.1 | RO
17 | Ppv2 H | 0x0009 | 04 | U16 | W 0.1 | RO | mppt2_power
18 | Ppv2 L | 0x000A | 04 | U16 | W 0.1 | RO | mppt2_power
19 | Vpv3 | 0x000B | 04 | U16 | V 0.1 | RO | mppt3_voltage
20 | PV3Curr | 0x000C | 04 | U16 | A 0.1 | RO | mppt3_current
21 | Ppv3 H | 0x000D | 04 | U16 | W 0.1 | RO | mppt3_power
22 | Ppv3 L | 0x000E | 04 | U16 | W 0.1 | RO | mppt3_power
23 | Vpv4 | 0x000F | 04 | U16 | V 0.1 | RO | mppt4_voltage
24 | LCDlanguage | 0x000F | 03 | U16 |  | RO
25 | PV4Curr | 0x0010 | 04 | U16 | A 0.1 | RO | mppt4_current
26 | CountrySelected | 0x0010 | 03 | U16 |  | RO
27 | Ppv4 H | 0x0011 | 04 | U16 | W 0.1 | RO | mppt4_power
28 | Vpv start | 0x0011 | 03 | U16 | V 0.1 | RO
29 | Ppv4 L | 0x0012 | 04 | U16 | W 0.1 | RO | mppt4_power
30 | Time start | 0x0012 | 03 | U16 |  | RO
31 | Vpv5 | 0x0013 | 04 | U16 | V 0.1 | RO | mppt5_voltage
32 | RestartDelayTime | 0x0013 | 03 | U16 |  | RO
33 | PV5Curr | 0x0014 | 04 | U16 | A 0.1 | RO | mppt5_current
34 | wPowerStartSlope | 0x0014 | 03 | U16 | % 0.1 | RO
35 | Ppv5H | 0x0015 | 04 | U16 | W 0.1 | RO
36 | wPowerRestartSlopeEE | 0x0015 | 03 | U16 | % 0.1 | RO
37 | wSelectBaud | 0x0016 | 03 | U16 |  | RO
38 | Vpv6 | 0x0017 | 04 | U16 | V 0.1 | RO | mppt6_voltage
39 | PV6Curr | 0x0018 | 04 | U16 | A 0.1 | RO | mppt6_current
40 | Ppv6 H | 0x0019 | 04 | U16 | W 0.1 | RO | mppt6_power
41 | Ppv6 L | 0x001A | 04 | U16 | W 0.1 | RO | mppt6_power
42 | Vpv7 | 0x001B | 04 | U16 | V 0.1 | RO | mppt7_voltage
43 | PV7Curr | 0x001C | 04 | U16 | A 0.1 | RO | mppt7_current
44 | Module H | 0x001C | 03 | U16 |  | RO
45 | Ppv7 H | 0x001D | 04 | U16 | W 0.1 | RO | mppt7_power
46 | Module L | 0x001D | 03 | U16 |  | RO
47 | Ppv7 L | 0x001E | 04 | U16 | W 0.1 | RO | mppt7_power
48 | ComAddress | 0x001E | 03 | U16 |  | RO
49 | Vpv8 | 0x001F | 04 | U16 | V 0.1 | RO | mppt8_voltage
50 | FlashStart | 0x001F | 03 | U16 |  | RO
51 | PV8Curr | 0x0020 | 04 | U16 | A 0.1 | RO | mppt8_current
52 | Reset UserInfo | 0x0020 | 03 | U16 |  | RO
53 | Ppv8 H | 0x0021 | 04 | U16 | W 0.1 | RO | mppt8_power
54 | Reset tofactory | 0x0021 | 03 | U16 |  | RO
55 | Ppv8 L | 0x0022 | 04 | U16 | W 0.1 | RO | mppt8_power
56 | Pac H | 0x0023 | 04 | U16 | W 0.1 | RO | pv_power
57 | Pac L | 0x0024 | 04 | U16 | W 0.1 | RO | pv_power
58 | L1_FREQUENCY | 0x0025 | 04 | U16 | Hz 0.01 | RO | frequency
59 | Vac1 | 0x0026 | 04 | U16 | V 0.1 | RO
60 | Iac1 | 0x0027 | 04 | U16 | A 0.1 | RO
61 | Pac1 H | 0x0028 | 04 | U16 | VA 0.1 | RO
62 | Pac1 L | 0x0029 | 04 | U16 | VA 0.1 | RO
63 | Vac2 | 0x002A | 04 | U16 | V 0.1 | RO
64 | bfailsafeEn; | 0x002A | 03 | U16 |  | RO
65 | Iac2 | 0x002B | 04 | U16 | A 0.1 | RO
66 | Pac2 H | 0x002C | 04 | U16 | VA 0.1 | RO
67 | Input tracker num andoutput phase num | 0x002C | 03 | U16 |  | RO
68 | Pac2 L | 0x002D | 04 | U16 | VA 0.1 | RO
69 | Vac3 | 0x002E | 04 | U16 | V 0.1 | RO
70 | Sys Month | 0x002E | 03 | U16 |  | RO
71 | Iac3 | 0x002F | 04 | U16 | A 0.1 | RO
72 | Sys Day | 0x002F | 03 | U16 |  | RO
73 | Pac3 H | 0x0030 | 04 | U16 | VA 0.1 | RO
74 | Sys Hour | 0x0030 | 03 | U16 |  | RO
75 | Pac3 L | 0x0031 | 04 | U16 | VA 0.1 | RO
76 | Sys Min | 0x0031 | 03 | U16 |  | RO
77 | Vac RS_ | 0x0032 | 04 | U16 | V 0.1 | RO
78 | Sys Sec | 0x0032 | 03 | U16 |  | RO
79 | Vac ST_ | 0x0033 | 04 | U16 | V 0.1 | RO
80 | Sys Weekly | 0x0033 | 03 | U16 |  | RO
81 | Vac TR_ | 0x0034 | 04 | U16 | V 0.1 | RO
82 | Vac low | 0x0034 | 03 | U16 | V 0.1 | RO
83 | Eactoday H | 0x0035 | 04 | U16 |  | RO
84 | Vac high | 0x0035 | 03 | U16 | V 0.1 | RO
85 | Eac today L | 0x0036 | 04 | U16 |  | RO | daily_energy
86 | Fac low | 0x0036 | 03 | U16 | Hz 0.01 | RO
87 | Eac total H | 0x0037 | 04 | U16 |  | RO | cumulative_energy
88 | Fac high | 0x0037 | 03 | U16 | Hz 0.01 | RO
89 | Eac total L | 0x0038 | 04 | U16 |  | RO | cumulative_energy
90 | Vac low 2 | 0x0038 | 03 | U16 | V 0.1 | RO
91 | Time total H | 0x0039 | 04 | U16 |  | RO
92 | Vac high 2 | 0x0039 | 03 | U16 | V 0.1 | RO
93 | Time total L | 0x003A | 04 | U16 |  | RO
94 | Fac low 2 | 0x003A | 03 | U16 | Hz 0.01 | RO
95 | Epv1 today H_ | 0x003B | 04 | U16 | kWh 0.1 | RO
96 | Fac high 2 | 0x003B | 03 | U16 | Hz 0.01 | RO
97 | Epv1 today L_ | 0x003C | 04 | U16 | kWh 0.1 | RO
98 | Vac low 3 | 0x003C | 03 | U16 | V 0.1 | RO
99 | Vac high 3 | 0x003D | 03 | U16 | V 0.1 | RO
100 | Epv1 total L_ | 0x003E | 04 | U16 | kWh 0.1 | RO
101 | Fac low 3 | 0x003E | 03 | U16 | Hz 0.01 | RO
102 | Epv2 today H_ | 0x003F | 04 | U16 | kWh 0.1 | RO
103 | Fac high 3 | 0x003F | 03 | U16 | Hz 0.01 | RO
104 | Epv2 today L_ | 0x0040 | 04 | U16 | kWh 0.1 | RO
105 | Vac low C | 0x0040 | 03 | U16 | V 0.1 | RO
106 | Epv2 total H_ | 0x0041 | 04 | U16 | kWh 0.1 | RO
107 | Vac high C | 0x0041 | 03 | U16 | V 0.1 | RO
108 | Epv2 total L_ | 0x0042 | 04 | U16 | kWh 0.1 | RO
109 | Fac low C | 0x0042 | 03 | U16 | Hz 0.01 | RO
110 | Epv3 today H_ | 0x0043 | 04 | U16 | kWh 0.1 | RO
111 | Fac high C | 0x0043 | 03 | U16 | Hz 0.01 | RO
112 | Epv3 today L_ | 0x0044 | 04 | U16 | kWh 0.1 | RO
113 | Vac low1time | 0x0044 | 03 | U16 |  | RO
114 | Epv3 total H_ | 0x0045 | 04 | U16 | kWh 0.1 | RO
115 | Epv3 total L_ | 0x0046 | 04 | U16 | kWh 0.1 | RO
116 | Vac low2time | 0x0046 | 03 | U16 |  | RO
117 | Epv4 today H_ | 0x0047 | 04 | U16 | kWh 0.1 | RO
118 | Vac high2time | 0x0047 | 03 | U16 |  | RO
119 | Epv4 today L_ | 0x0048 | 04 | U16 | kWh 0.1 | RO
120 | Fac low1time | 0x0048 | 03 | U16 |  | RO
121 | Epv4 total H_ | 0x0049 | 04 | U16 | kWh 0.1 | RO
122 | Fac high1time | 0x0049 | 03 | U16 |  | RO
123 | Epv4 total L_ | 0x004A | 04 | U16 | kWh 0.1 | RO
124 | Fac low2time | 0x004A | 03 | U16 |  | RO
125 | Epv5 today H_ | 0x004B | 04 | U16 | kWh 0.1 | RO
126 | Fac high2time | 0x004B | 03 | U16 |  | RO
127 | Epv5 today L_ | 0x004C | 04 | U16 | kWh 0.1 | RO
128 | Vac low3time | 0x004C | 03 | U16 |  | RO
129 | Epv5 total H_ | 0x004D | 04 | U16 | kWh 0.1 | RO
130 | Vac high3time | 0x004D | 03 | U16 |  | RO
131 | Epv5 total L_ | 0x004E | 04 | U16 | kWh 0.1 | RO
132 | Fac low3time | 0x004E | 03 | U16 |  | RO
133 | Epv6 today H_ | 0x004F | 04 | U16 | kWh 0.1 | RO
134 | Fac high3time | 0x004F | 03 | U16 |  | RO
135 | Epv6 today L_ | 0x0050 | 04 | U16 | kWh 0.1 | RO
136 | U10min | 0x0050 | 03 | U16 | V 0.1 | RO
137 | Epv6 total H_ | 0x0051 | 04 | U16 | kWh 0.1 | RO
138 | Epv6 total L_ | 0x0052 | 04 | U16 | kWh 0.1 | RO
139 | FW Build No.5 | 0x0052 | 03 | ASCII |  | RO
140 | Epv7 today H_ | 0x0053 | 04 | U16 | kWh 0.1 | RO
141 | FW Build No.4 | 0x0053 | 03 | ASCII |  | RO
142 | Epv7 today L_ | 0x0054 | 04 | U16 | kWh 0.1 | RO
143 | FW Build No.3 | 0x0054 | 03 | ASCII |  | RO
144 | Epv7 total H_ | 0x0055 | 04 | U16 | kWh 0.1 | RO
145 | FW Build No.2 | 0x0055 | 03 | ASCII |  | RO
146 | Epv7 total L_ | 0x0056 | 04 | U16 | kWh 0.1 | RO
147 | FW Build No.1 | 0x0056 | 03 | ASCII |  | RO
148 | Epv8 today H_ | 0x0057 | 04 | U16 | kWh 0.1 | RO
149 | FW Build No.0 | 0x0057 | 03 | ASCII |  | RO
150 | Epv8 today L_ | 0x0058 | 04 | U16 | kWh 0.1 | RO
151 | ModbusVersion | 0x0058 | 03 | U16 |  | RO
152 | Epv8 total H_ | 0x0059 | 04 | U16 | kWh 0.1 | RO
153 | Epv8 total L_ | 0x005A | 04 | U16 | kWh 0.1 | RO
154 | GPRS IP Flag | 0x005A | 03 | U16 |  | RO
155 | Epv total H_ | 0x005B | 04 | U16 | kWh 0.1 | RO
156 | FreqDerateStart | 0x005B | 03 | U16 |  | RO
157 | Epv total L_ | 0x005C | 04 | U16 | kWh 0.1 | RO
158 | FLrate | 0x005C | 03 | U16 |  | RO
159 | Temp1 | 0x005D | 04 | U16 |  | RO
160 | Temp2 | 0x005E | 04 | U16 |  | RO
161 | Temp3 | 0x005F | 04 | U16 |  | RO
162 | Temp4 | 0x0060 | 04 | U16 |  | RO
163 | uwBatVolt DSP_ | 0x0061 | 04 | U16 | V 0.1 | RO
164 | Qlockinpower | 0x0061 | 03 | U16 |  | RO
165 | QlockOutpower | 0x0062 | 03 | U16 |  | RO
166 | LIGridV | 0x0063 | 03 | U16 | V 0.1 | RO
167 | LOGridV | 0x0064 | 03 | U16 | V 0.1 | RO
168 | RealOPPercent | 0x0065 | 04 | U16 |  | RO
169 | PFAdj1 | 0x0065 | 03 | U16 |  | RO
170 | OPFullwatt H | 0x0066 | 04 | U16 |  | RO
171 | PFAdj2 | 0x0066 | 03 | U16 |  | RO
172 | OPFullwatt L | 0x0067 | 04 | U16 | W 0.1 | RO
173 | PFAdj3 | 0x0067 | 03 | U16 |  | RO
174 | PFAdj4 | 0x0068 | 03 | U16 |  | RO
175 | PFAdj5 | 0x0069 | 03 | U16 |  | RO
176 | PFAdj6 | 0x006A | 03 | U16 |  | RO
177 | QVRPDelayTimeEE | 0x006B | 03 | U16 |  | RO
178 | RemoteCtrlEn | 0x006C | 04 | U16 |  | RO
179 | OverFDeratD | 0x006C | 03 | U16 |  | RO
180 | RemoteCtrlPower | 0x006D | 04 | U16 |  | RO
181 | QpercentMax | 0x006D | 03 | U16 | % 0.1 | RO
182 | PFLineP1 LP_ | 0x006E | 03 | U16 |  | RO
183 | PFLineP1 PF_ | 0x006F | 03 | U16 |  | RO
184 | bINVWarnCode | 0x0070 | 04 | U16 |  | RO
185 | PFLineP2 LP_ | 0x0070 | 03 | U16 |  | RO
186 | real PowerPercent | 0x0071 | 04 | U16 |  | RO
187 | PFLineP2 PF_ | 0x0071 | 03 | U16 |  | RO
188 | inv start delaytime | 0x0072 | 04 | U16 |  | RO
189 | PFLineP3 LP_ | 0x0072 | 03 | U16 |  | RO
190 | PFLineP3 PF_ | 0x0073 | 03 | U16 |  | RO
191 | AC chargePower H_ | 0x0074 | 04 | U16 |  | RO
192 | PFLineP4 LP_ | 0x0074 | 03 | U16 |  | RO
193 | PFLineP4 PF_ | 0x0075 | 03 | U16 |  | RO
194 | Priority | 0x0076 | 04 | U16 |  | RO
195 | Module 4 | 0x0076 | 03 | U16 |  | RO
196 | Battery Type | 0x0077 | 04 | U16 |  | RO
197 | Module 3 | 0x0077 | 03 | U16 |  | RO
198 | AutoProofreadCMD | 0x0078 | 04 | U16 |  | RO
199 | Module 2 | 0x0078 | 03 | U16 |  | RO
200 | Module 1 | 0x0079 | 03 | U16 |  | RO
201 | ExportLimitPowerRate | 0x007B | 03 | U16 | % 0.1 | R/W
202 | PID PV1+ Voltage | 0x007D | 04 | U16 | V 0.1 | RO
203 | INV Type-1 | 0x007D | 03 | ASCII |  | RO
204 | PID PV1+ Current | 0x007E | 04 | U16 |  | RO
205 | INV Type-2 | 0x007E | 03 | ASCII |  | RO
206 | PID PV2+ Voltage | 0x007F | 04 | U16 | V 0.1 | RO
207 | INV Type-3 | 0x007F | 03 | ASCII |  | RO
208 | PID PV2+ Current | 0x0080 | 04 | U16 |  | RO
209 | INV Type-4 | 0x0080 | 03 | ASCII |  | RO
210 | PID PV3+ Voltage | 0x0081 | 04 | U16 | V 0.1 | RO
211 | INV Type-5 | 0x0081 | 03 | ASCII |  | RO
212 | PID PV3+ Current | 0x0082 | 04 | U16 |  | RO
213 | INV Type-6 | 0x0082 | 03 | ASCII |  | RO
214 | PID PV4+ Voltage | 0x0083 | 04 | U16 | V 0.1 | RO
215 | INV Type-7 | 0x0083 | 03 | ASCII |  | RO
216 | PID PV4+ Current | 0x0084 | 04 | U16 |  | RO
217 | INV Type-8 | 0x0084 | 03 | ASCII |  | RO
218 | PID PV5+ Voltage | 0x0085 | 04 | U16 | V 0.1 | RO
219 | BLVersion1 | 0x0085 | 03 | U16 |  | RO
220 | PID PV5+ Current | 0x0086 | 04 | U16 |  | RO
221 | BLVersion2 | 0x0086 | 03 | U16 |  | RO
222 | PID PV6+ Voltage | 0x0087 | 04 | U16 | V 0.1 | RO
223 | BLVersion3 | 0x0087 | 03 | U16 |  | RO
224 | PID PV6+ Current | 0x0088 | 04 | U16 |  | RO
225 | BLVersion4 | 0x0088 | 03 | U16 |  | RO
226 | PID PV7+ Voltage | 0x0089 | 04 | U16 | V 0.1 | RO
227 | PID PV7+ Current | 0x008A | 04 | U16 |  | RO
228 | PID PV8+ Voltage | 0x008B | 04 | U16 | V 0.1 | RO
229 | PID PV8+ Current | 0x008C | 04 | U16 |  | RO
230 | V String1_ | 0x008E | 04 | U16 | V 0.1 | RO
231 | Curr String1_ | 0x008F | 04 | U16 | A 0.1 | RO
232 | V String2_ | 0x0090 | 04 | U16 | V 0.1 | RO
233 | Curr String2_ | 0x0091 | 04 | U16 | A 0.1 | RO
234 | ZeroCurrentEnable | 0x0091 | 03 | U16 |  | R/W
235 | V String3_ | 0x0092 | 04 | U16 | V 0.1 | RO
236 | uwZeroCurrentStaticlowVolt | 0x0092 | 03 | U16 | V 0.1 | R/W
237 | Curr String3_ | 0x0093 | 04 | U16 | A 0.1 | RO
238 | uwZeroCurrentStaticHighVolt | 0x0093 | 03 | U16 | V 0.1 | R/W
239 | V String4_ | 0x0094 | 04 | U16 | V 0.1 | RO
240 | V String5_ | 0x0096 | 04 | U16 | V 0.1 | RO
241 | uwQVPowerStableTime | 0x0096 | 03 | U16 |  | R/W
242 | Curr String5_ | 0x0097 | 04 | U16 | A 0.1 | RO
243 | V String6_ | 0x0098 | 04 | U16 | V 0.1 | RO
244 | Curr String6_ | 0x0099 | 04 | U16 | A 0.1 | RO
245 | V String7_ | 0x009A | 04 | U16 | V 0.1 | RO
246 | Curr String7_ | 0x009B | 04 | U16 | A 0.1 | RO
247 | V String8_ | 0x009C | 04 | U16 | V 0.1 | RO
248 | Curr String8_ | 0x009D | 04 | U16 | A 0.1 | RO
249 | V String9_ | 0x009E | 04 | U16 | V 0.1 | RO
250 | Curr String9_ | 0x009F | 04 | U16 | A 0.1 | RO
251 | V String10_ | 0x00A0 | 04 | U16 | V 0.1 | RO
252 | Curr String10_ | 0x00A1 | 04 | U16 | A 0.1 | RO
253 | V String11_ | 0x00A2 | 04 | U16 | V 0.1 | RO
254 | Curr String11_ | 0x00A3 | 04 | U16 | A 0.1 | RO
255 | V String12_ | 0x00A4 | 04 | U16 | V 0.1 | RO
256 | Curr String12_ | 0x00A5 | 04 | U16 | A 0.1 | RO
257 | V String13_ | 0x00A6 | 04 | U16 | V 0.1 | RO
258 | Curr String13_ | 0x00A7 | 04 | U16 | A 0.1 | RO
259 | V String14_ | 0x00A8 | 04 | U16 | V 0.1 | RO
260 | Curr String14_ | 0x00A9 | 04 | U16 | A 0.1 | RO
261 | V String15_ | 0x00AA | 04 | U16 | V 0.1 | RO
262 | Curr String15_ | 0x00AB | 04 | U16 | A 0.1 | RO
263 | V String16_ | 0x00AC | 04 | U16 | V 0.1 | RO
264 | Curr String16_ | 0x00AD | 04 | U16 | A 0.1 | RO
265 | StrUnmatch | 0x00AE | 04 | U16 |  | RO
266 | StrCurrentUnblance | 0x00AF | 04 | U16 |  | RO
267 | StrDisconnect | 0x00B0 | 04 | U16 |  | RO
268 | String Prompt | 0x00B2 | 04 | STRINGING |  | RO
269 | OverFDeratResponseTime | 0x00B2 | 03 | U16 |  | RO
270 | UnderFUploadResponseTime | 0x00B3 | 03 | U16 |  | RO
271 | DSP067 DebugData1 | 0x00B6 | 04 | U16 |  | RO
272 | DSP067 DebugData2 | 0x00B7 | 04 | U16 |  | RO
273 | DSP067 DebugData3 | 0x00B8 | 04 | U16 |  | RO
274 | DSP067 DebugData4 | 0x00B9 | 04 | U16 |  | RO
275 | DSP067 DebugData5 | 0x00BA | 04 | U16 |  | RO
276 | DSP067 DebugData6 | 0x00BB | 04 | U16 |  | RO
277 | DSP067 DebugData7 | 0x00BC | 04 | U16 |  | RO
278 | DSP067 DebugData8 | 0x00BD | 04 | U16 |  | RO
279 | DSP075 DebugData1 | 0x00BE | 04 | U16 |  | RO
280 | DSP075 DebugData2 | 0x00BF | 04 | U16 |  | RO
281 | DSP075 DebugData3 | 0x00C0 | 04 | U16 |  | RO
282 | DSP075 DebugData4 | 0x00C1 | 04 | U16 |  | RO
283 | DSP075 DebugData55 | 0x00C2 | 04 | U16 |  | RO
284 | DSP075 DebugData6 | 0x00C3 | 04 | U16 |  | RO
285 | DSP075 DebugData7 | 0x00C4 | 04 | U16 |  | RO
286 | DSP075 DebugData8 | 0x00C5 | 04 | U16 |  | RO
287 | bUSBAgingTestOkFlag | 0x00C6 | 04 | U16 |  | RO
288 | bFlashEraseAgingOkFlag | 0x00C7 | 04 | U16 |  | RO
289 | PVISO | 0x00C8 | 04 | U16 |  | RO
290 | R DCI_ | 0x00C9 | 04 | U16 |  | RO
291 | S DCI_ | 0x00CA | 04 | U16 |  | RO
292 | PID On/OffCtrl | 0x00CA | 03 | U16 |  | RO
293 | T DCI_ | 0x00CB | 04 | U16 |  | RO
294 | PID VoltOption | 0x00CB | 03 | U16 |  | RO
295 | PID Bus_ | 0x00CC | 04 | U16 | V 0.1 | RO
296 | GFCI | 0x00CD | 04 | U16 |  | RO
297 | CT I R_ _ | 0x00CF | 04 | U16 | A 0.1 | RO
298 | CT I S_ _ | 0x00D0 | 04 | U16 | A 0.1 | RO
299 | CT I T_ _ | 0x00D1 | 04 | U16 | A 0.1 | RO
300 | CT Q R H_ _ | 0x00D2 | 04 | U16 |  | RO
301 | CT Q R L_ _ | 0x00D3 | 04 | U16 |  | RO
302 | CT Q S H_ _ | 0x00D4 | 04 | U16 |  | RO
303 | CT Q S L_ _ | 0x00D5 | 04 | U16 |  | RO
304 | CT Q T H_ _ | 0x00D6 | 04 | U16 |  | RO
305 | CT Q T L_ _ | 0x00D7 | 04 | U16 |  | RO
306 | CT HAR I R__ | 0x00D8 | 04 | U16 | A 0.1 | RO
307 | CT HAR I S__ | 0x00D9 | 04 | U16 | A 0.1 | RO
308 | CT HAR I T__ | 0x00DA | 04 | U16 | A 0.1 | RO
309 | COMP Q R H_ _ | 0x00DB | 04 | U16 |  | RO
310 | COMP Q R L_ _ | 0x00DC | 04 | U16 |  | RO
311 | COMP Q S H_ _ | 0x00DD | 04 | U16 |  | RO
312 | COMP Q S L_ _ | 0x00DE | 04 | U16 |  | RO
313 | COMP Q T H_ _ | 0x00DF | 04 | U16 |  | RO
314 | COMP Q T L_ _ | 0x00E0 | 04 | U16 |  | RO
315 | COMP HAR I R__ | 0x00E1 | 04 | U16 | A 0.1 | RO
316 | COMP HAR I S__ | 0x00E2 | 04 | U16 | A 0.1 | RO
317 | COMP HAR I T__ | 0x00E3 | 04 | U16 | A 0.1 | RO
318 | bRS232AgingTestOkFlag | 0x00E4 | 04 | U16 |  | RO
319 | EnergyAdjust | 0x00E5 | 03 | U16 | % 0.1 | RO
320 | Sac H | 0x00E6 | 04 | U16 | W 0.1 | RO
321 | IslandDisable | 0x00E6 | 03 | U16 |  | RO
322 | Sac L | 0x00E7 | 04 | U16 | W 0.1 | RO
323 | FanCheck | 0x00E7 | 03 | U16 |  | RO
324 | ReActPowerH | 0x00E8 | 04 | S32 | W 0.1 | RO
325 | EnableNLine | 0x00E8 | 03 | U16 |  | RO
326 | ReActPowerL | 0x00E9 | 04 | U16 |  | RO
327 | wCheckHard | 0x00E9 | 03 | U16 |  | RO
328 | ReActPowerMaxH | 0x00EA | 04 | U16 |  | RO
329 | wCheckHardware2 | 0x00EA | 03 | U16 |  | RO
330 | ReActPowerMaxL | 0x00EB | 04 | U16 |  | RO
331 | ReActPower Total_H | 0x00EC | 04 | U16 |  | RO
332 | ReActPower Total_L | 0x00ED | 04 | U16 |  | RO
333 | Check Step | 0x00F0 | 03 | U16 |  | RO
334 | INV-Lng | 0x00F1 | 03 | U16 |  | RO
335 | INV-Lat | 0x00F2 | 03 | U16 |  | RO
336 | PV1 or PV2 circuit short | 0x0100 | 04 | U16 |  | RO
337 | PV1 or PV2 boost driver broken | 0x0200 | 04 | U16 |  | RO
338 | PactouserTotal L | 0x03FE | 04 | U16 |  | RO
339 | Reserve | 0x03FE | 03 | U16 |  | RO
340 | Pac to grid R H | 0x03FF | 04 | U16 |  | RO | pv_power
341 | Reserve | 0x03FF | 03 | U16 |  | RO
342 | Pac to grid R L | 0x0400 | 04 | U16 |  | RO | pv_power
343 | Reserve | 0x0400 | 03 | U16 |  | RO
344 | Pactogrid S H | 0x0401 | 04 | U16 |  | RO
345 | Reserve | 0x0401 | 03 | U16 |  | RO
346 | Pactogrid S L | 0x0402 | 04 | U16 |  | RO
347 | Pactogrid T H | 0x0403 | 04 | U16 |  | RO
348 | Reserve | 0x0403 | 03 | U16 |  | RO
349 | Pactogrid T L | 0x0404 | 04 | U16 |  | RO
350 | Reserve | 0x0404 | 03 | U16 |  | RO
351 | Pactogrid total H | 0x0405 | 04 | U16 |  | RO
352 | Reserve | 0x0405 | 03 | U16 |  | RO
353 | Pactogrid total L | 0x0406 | 04 | U16 |  | RO
354 | Reserve | 0x0406 | 03 | U16 |  | RO
355 | PLocalLoad R H | 0x0407 | 04 | U16 |  | RO
356 | Reserve | 0x0407 | 03 | U16 |  | RO
357 | Reserve | 0x0408 | 03 | U16 |  | RO
358 | PLocalLoad S H | 0x0409 | 04 | U16 |  | RO
359 | Reserve | 0x0409 | 03 | U16 |  | RO
360 | PLocalLoad S L | 0x040A | 04 | U16 |  | RO
361 | Reserve | 0x040A | 03 | U16 |  | RO
362 | PLocalLoadT H | 0x040B | 04 | U16 |  | RO
363 | Reserve | 0x040B | 03 | U16 |  | RO
364 | PLocalLoadT L | 0x040C | 04 | U16 |  | RO
365 | Reserve | 0x040C | 03 | U16 |  | RO
366 | PLocalLoad total H | 0x040D | 04 | U16 |  | RO
367 | PLocalLoad total L | 0x040E | 04 | U16 |  | RO
368 | CTAdjust | 0x040E | 03 | U16 |  | RO
369 | IPM Temperature | 0x040F | 04 | U16 | ℃ 0.1 | RO
370 | Reserve | 0x040F | 03 | U16 |  | RO
371 | BatteryTemperature | 0x0410 | 04 | U16 | ℃ 0.1 | RO
372 | Reserve | 0x0410 | 03 | U16 |  | RO
373 | Reserve | 0x0411 | 03 | U16 |  | RO
374 | Reserve | 0x0412 | 03 | U16 |  | RO
375 | Reserve | 0x0413 | 03 | U16 |  | RO
376 | Etouser today H_ | 0x0414 | 04 | U16 | kWh 0.1 | RO
377 | Etouser today L_ | 0x0415 | 04 | U16 | kWh 0.1 | RO
378 | Reserve | 0x0415 | 03 | U16 |  | RO
379 | Etouser total H_ | 0x0416 | 04 | U16 | kWh 0.1 | RO
380 | Reserve | 0x0416 | 03 | U16 |  | RO
381 | Etouser total L_ | 0x0417 | 04 | U16 | kWh 0.1 | RO
382 | AgingTestStepCmd | 0x0417 | 03 | U16 |  | RO
383 | Etogrid today H_ | 0x0418 | 04 | U16 | kWh 0.1 | RO
384 | BatteryType | 0x0418 | 03 | U16 |  | RO
385 | Etogrid today L_ | 0x0419 | 04 | U16 | kWh 0.1 | RO
386 | Reserve | 0x0419 | 03 | U16 |  | RO
387 | Etogrid total H_ | 0x041A | 04 | U16 | kWh 0.1 | RO
388 | Reserve | 0x041A | 03 | U16 |  | RO
389 | Etogrid total L_ | 0x041B | 04 | U16 | kWh 0.1 | RO
390 | Reserve | 0x041B | 03 | U16 |  | RO
391 | Edischarge1 toda_y H | 0x041C | 04 | U16 | kWh 0.1 | RO
392 | Reserve | 0x041C | 03 | U16 |  | RO
393 | Edischarge1 toda_y L | 0x041D | 04 | U16 | kWh 0.1 | RO
394 | Reserve | 0x041D | 03 | U16 |  | RO
395 | Edischarge1 total_H | 0x041E | 04 | U16 | kWh 0.1 | RO
396 | Reserve | 0x041E | 03 | U16 |  | RO
397 | Edischarge1 total_L | 0x041F | 04 | U16 | kWh 0.1 | RO
398 | Echarge1 today H_ | 0x0420 | 04 | U16 | kWh 0.1 | RO
399 | Echarge1 today_L | 0x0421 | 04 | U16 | kWh 0.1 | RO
400 | Echarge1 total H_ | 0x0422 | 04 | U16 | kWh 0.1 | RO
401 | Echarge1 total L_ | 0x0423 | 04 | U16 | kWh 0.1 | RO
402 | ELocalLoad Today_H | 0x0424 | 04 | U16 | kWh 0.1 | RO
403 | BuckUpsFunEn | 0x0424 | 03 | U16 |  | RO
404 | ELocalLoad Today_L | 0x0425 | 04 | U16 | kWh 0.1 | RO
405 | BuckUPSVoltSet | 0x0425 | 03 | U16 | V 230 | RO
406 | ELocalLoad Total_ | 0x0426 | 04 | U16 | kWh 0.1 | RO
407 | UPSFreqSet | 0x0426 | 03 | U16 | Hz 50 | RO
408 | ELocalLoad Total_L | 0x0427 | 04 | U16 | kWh 0.1 | RO
409 | EPS Fac | 0x042B | 04 | U16 | Hz 0.01 | RO
410 | EPS Vac1 | 0x042C | 04 | U16 | V 0.1 | RO
411 | EPS Iac1 | 0x042D | 04 | U16 | A 0.1 | RO
412 | EPS Pac1 H | 0x042E | 04 | U16 | VA 0.1 | RO
413 | EPS Pac1 L | 0x042F | 04 | U16 | VA 0.1 | RO
414 | GridFirstStopSOC | 0x042F | 03 | U16 |  | RO
415 | EPS Vac2 | 0x0430 | 04 | U16 | V 0.1 | RO
416 | EPS Iac2 | 0x0431 | 04 | U16 | A 0.1 | RO
417 | EPS Pac2 H | 0x0432 | 04 | U16 | VA 0.1 | RO
418 | EPS Pac2 L | 0x0433 | 04 | U16 | VA 0.1 | RO
419 | EPS Vac3 | 0x0434 | 04 | U16 | V 0.1 | RO
420 | EPS Iac3 | 0x0435 | 04 | U16 | A 0.1 | RO
421 | EPS Pac3 H | 0x0436 | 04 | U16 | VA 0.1 | RO
422 | EPS Pac3 L | 0x0437 | 04 | U16 | VA 0.1 | RO
423 | Loadpercent | 0x0438 | 04 | U16 |  | RO
424 | Power factor | 0x0439 | 04 | U16 |  | RO | power_factor
425 | Grid First StopTime 1 | 0x0439 | 03 | U16 |  | RO
426 | Grid First StopSwitch 1 | 0x043A | 03 | U16 |  | RO
427 | Grid First StopTime 2 | 0x043C | 03 | U16 |  | RO
428 | Grid First StopSwitch 2 | 0x043D | 03 | U16 |  | RO
429 | BMS SOC_ | 0x043E | 04 | U16 |  | RO
430 | BMS BatteryVol_t | 0x043F | 04 | U16 |  | RO
431 | Grid First StopTime 3 | 0x043F | 03 | U16 |  | RO
432 | BMS BatteryCur_r | 0x0440 | 04 | U16 |  | RO
433 | Grid First StopSwitch 3 | 0x0440 | 03 | U16 |  | RO
434 | BMS BatteryTe_mp | 0x0441 | 04 | U16 |  | RO
435 | reserve | 0x0441 | 03 | U16 |  | RO
436 | BMS MaxCurr_ | 0x0442 | 04 | U16 |  | RO
437 | BatFirstPowerRate | 0x0442 | 03 | U16 |  | RO
438 | BMS GaugeRM_ | 0x0443 | 04 | U16 |  | RO
439 | wBatFirst stopSOC | 0x0443 | 03 | U16 |  | RO
440 | BMS GaugeFCC_ | 0x0444 | 04 | U16 |  | RO
441 | BMS FW_ | 0x0445 | 04 | U16 |  | RO
442 | BMS CycleCnt_ | 0x0447 | 04 | U16 |  | RO
443 | BMS SOH_ | 0x0448 | 04 | U16 |  | RO
444 | BMS ConstantV_olt | 0x0449 | 04 | U16 |  | RO
445 | BMS WarnInfoO_ld | 0x044A | 04 | U16 |  | RO
446 | BMS WarnInfo_ | 0x044B | 04 | U16 |  | RO
447 | BMS GaugeICCu_rr | 0x044C | 04 | U16 |  | RO
448 | Bat First StartTime 1 | 0x044C | 03 | U16 |  | RO
449 | BMS MCUVersi_on | 0x044D | 04 | U16 |  | RO
450 | Bat First StopTime 1 | 0x044D | 03 | U16 |  | RO
451 | BMS GaugeVers_ion | 0x044E | 04 | U16 |  | RO
452 | BatFirston/offSwitch 1 | 0x044E | 03 | U16 |  | RO
453 | BMS wGaugeFR_Version L_ | 0x044F | 04 | U16 |  | RO
454 | Bat First StartTime 2 | 0x044F | 03 | U16 |  | RO
455 | BMS wGaugeFR_Version H_ | 0x0450 | 04 | U16 |  | RO
456 | Bat First StopTime 2 | 0x0450 | 03 | U16 |  | RO
457 | BMS BMSInfo_ | 0x0451 | 04 | U16 |  | RO
458 | BatFirston/offSwitch 2 | 0x0451 | 03 | U16 |  | RO
459 | BMS PackInfo_ | 0x0452 | 04 | U16 |  | RO
460 | Bat First StartTime 3 | 0x0452 | 03 | U16 |  | RO
461 | BMS UsingCap_ | 0x0453 | 04 | U16 |  | RO
462 | Bat First StopTime 3 | 0x0453 | 03 | U16 |  | RO
463 | BMS Cell1 Volt_ _ | 0x0454 | 04 | U16 |  | RO
464 | BatFirston/offSwitch 3 | 0x0454 | 03 | U16 |  | RO
465 | BMS Cell2 Volt_ _ | 0x0455 | 04 | U16 |  | RO
466 | reserve | 0x0455 | 03 | U16 |  | RO
467 | Load FirstStop Time 1 | 0x0457 | 03 | U16 |  | RO
468 | Load FirstSwitch 1 | 0x0458 | 03 | U16 |  | RO
469 | Load FirstStop Time 2 | 0x045A | 03 | U16 |  | RO
470 | Load FirstSwitch 2 | 0x045B | 03 | U16 |  | RO
471 | Load FirstStop Time 3 | 0x045D | 03 | U16 |  | RO
472 | Load FirstSwitch 3 | 0x045E | 03 | U16 |  | RO
473 | reserve | 0x045F | 03 | U16 |  | RO
474 | BackUpEn | 0x0460 | 03 | U16 |  | RO
475 | SGIPEn | 0x0461 | 03 | U16 |  | RO
476 | 1122~1124 | 0x0462 | 03 | U16 |  | RO
477 | BMS_Cell16 Volt_ | 0x0463 | 04 | U16 |  | RO
478 | AC ChargeEnergy Today H | 0x0464 | 04 | U16 |  | RO
479 | ACChargeEnergy TodayL | 0x0465 | 04 | U16 |  | RO
480 | AC ChargeEnergy Total H | 0x0466 | 04 | U16 |  | RO | cumulative_energy
481 | ACChargeEnergy Total L | 0x0467 | 04 | U16 |  | RO | cumulative_energy
482 | AC ChargePower H | 0x0468 | 04 | U16 |  | RO
483 | AC ChargePower L | 0x0469 | 04 | U16 |  | RO
484 | 70% INV Poweradjust | 0x046A | 04 | U16 |  | RO
485 | Extra AC Powerto grid L_ | 0x046C | 04 | U16 |  | RO
486 | Eextra today H_ | 0x046D | 04 | U16 | kWh 0.1 | RO
487 | Eextra today L_ | 0x046E | 04 | U16 | kWh 0.1 | RO
488 | Eextra total H_ | 0x046F | 04 | U16 | kWh 0.1 | RO
489 | Eextra total L_ | 0x0470 | 04 | U16 | kWh 0.1 | RO
490 | Esystem today_H | 0x0471 | 04 | U16 | kWh 0.1 | RO
491 | Esystem today_L | 0x0472 | 04 | U16 | kWh 0.1 | RO
492 | Esystem total H_ | 0x0473 | 04 | U16 | kWh 0.1 | RO
493 | Esystem total L_ | 0x0474 | 04 | U16 | kWh 0.1 | RO
494 | reversed | 0x04E1 | 04 | U16 |  | RO
495 | Pac H | 0x07F3 | 04 | U16 | W 0.1 | RO | pv_power
496 | Pac L | 0x07F4 | 04 | U16 | W 0.1 | RO | pv_power
497 | L1_FREQUENCY | 0x07F5 | 04 | U16 | Hz 0.01 | RO | frequency
498 | Vac1 | 0x07F6 | 04 | U16 | V 0.1 | RO
499 | Iac1 | 0x07F7 | 04 | U16 | A 0.1 | RO
500 | Pac1 H | 0x07F8 | 04 | U16 | VA 0.1 | RO
501 | Pac1 L | 0x07F9 | 04 | U16 | VA 0.1 | RO
502 | Eac today H | 0x0805 | 04 | U16 |  | RO | daily_energy
503 | Eac today L | 0x0806 | 04 | U16 |  | RO | daily_energy
504 | Eac total H | 0x0807 | 04 | U16 |  | RO | cumulative_energy
505 | Eac total L | 0x0808 | 04 | U16 |  | RO | cumulative_energy
506 | Time total H | 0x0809 | 04 | U16 |  | RO
507 | Time total L | 0x080A | 04 | U16 |  | RO
508 | Temp1 | 0x082D | 04 | U16 |  | RO
509 | Temp2 | 0x082E | 04 | U16 |  | RO
510 | Temp3 | 0x082F | 04 | U16 |  | RO
511 | Temp4 | 0x0830 | 04 | U16 |  | RO
512 | uwBatVolt DSP_ | 0x0831 | 04 | U16 | V 0.1 | RO
513 | Extra AC Powerto grid H_ | 0x0836 | 04 | U16 |  | RO
514 | Extra AC Powerto grid L_ | 0x0837 | 04 | U16 |  | RO
515 | Eextra today H_ | 0x0838 | 04 | U16 | kWh 0.1 | RO
516 | Eextra today L_ | 0x0839 | 04 | U16 | kWh 0.1 | RO
517 | Eextra total H_ | 0x083A | 04 | U16 | kWh 0.1 | RO
518 | Eextra total L_ | 0x083B | 04 | U16 | kWh 0.1 | RO
519 | Esystem today_H | 0x083C | 04 | U16 | kWh 0.1 | RO
520 | Esystem today_L | 0x083D | 04 | U16 | kWh 0.1 | RO
521 | Esystem total H_ | 0x083E | 04 | U16 | kWh 0.1 | RO
522 | Esystem total L_ | 0x083F | 04 | U16 | kWh 0.1 | RO
523 | EACharge Today_H_ | 0x0840 | 04 | U16 |  | RO
524 | EACharge Today_L_ | 0x0841 | 04 | U16 |  | RO
525 | EACharge Total_H_ | 0x0842 | 04 | U16 |  | RO
526 | EACharge Total_L_ | 0x0843 | 04 | U16 |  | RO
527 | AC chargePower H_ | 0x0844 | 04 | U16 |  | RO
528 | AC chargePower L_ | 0x0845 | 04 | U16 |  | RO
529 | Priority | 0x0846 | 04 | U16 |  | RO
530 | Battery Type | 0x0847 | 04 | U16 |  | RO
531 | AutoProofreadCMD | 0x0848 | 04 | U16 |  | RO
532 | ExportLimitFailedPowerRate | 0x0BB8 | 03 | U16 | % 0.1 | R/W
533 | Ppv H | 0x0BB9 | 04 | U16 | W 0.1 | RO
534 | Ppv L | 0x0BBA | 04 | U16 |  | RO
535 | Vpv1 | 0x0BBB | 04 | U16 | V 0.1 | RO | mppt1_voltage
536 | Ipv1 | 0x0BBC | 04 | U16 | A 0.1 | RO | mppt_current
537 | Ppv1 H | 0x0BBD | 04 | U16 | W 0.1 | RO | mppt1_power
538 | Ppv1 L | 0x0BBE | 04 | U16 |  | RO | mppt1_power
539 | Vpv2 | 0x0BBF | 04 | U16 | V 0.1 | RO | mppt2_voltage
540 | Ipv2 | 0x0BC0 | 04 | U16 | A 0.1 | RO | mppt_current
541 | Ppv2 H | 0x0BC1 | 04 | U16 | W 0.1 | RO | mppt2_power
542 | Ppv2 L | 0x0BC2 | 04 | U16 |  | RO | mppt2_power
543 | Vpv3 | 0x0BC3 | 04 | U16 | V 0.1 | RO | mppt3_voltage
544 | Ipv3 | 0x0BC4 | 04 | U16 | A 0.1 | RO | mppt_current
545 | Ppv3 H | 0x0BC5 | 04 | U16 | W 0.1 | RO | mppt3_power
546 | Ppv3 L | 0x0BC6 | 04 | U16 |  | RO | mppt3_power
547 | Vpv4 | 0x0BC7 | 04 | U16 |  | RO | mppt4_voltage
548 | Ipv4 | 0x0BC8 | 04 | U16 |  | RO | mppt_current
549 | Ppv4H | 0x0BC9 | 04 | U16 |  | RO
550 | Ppv4L | 0x0BCA | 04 | U16 |  | RO
551 | Pac H | 0x0BCF | 04 | U16 | W 0.1 | RO | pv_power
552 | Pac L | 0x0BD0 | 04 | U16 |  | RO | pv_power
553 | Float chargecurrent limit | 0x0BD0 | 03 | U16 | A 0.1 | R/W
554 | L1_FREQUENCY | 0x0BD1 | 04 | U16 | Hz 0.01 | RO | frequency
555 | Vac1 | 0x0BD2 | 04 | U16 | V 0.1 | RO
556 | Iac1 | 0x0BD3 | 04 | U16 | A 0.1 | RO
557 | Vbatstopfordischarge | 0x0BD3 | 03 | U16 | V 0.1 | R/W
558 | Pac1 H | 0x0BD4 | 04 | U16 | VA 0.1 | RO
559 | Pac1 L | 0x0BD5 | 04 | U16 |  | RO
560 | Vac2 | 0x0BD6 | 04 | U16 | V 0.1 | RO
561 | Iac2 | 0x0BD7 | 04 | U16 | A 0.1 | RO
562 | Pac2 H | 0x0BD8 | 04 | U16 | VA 0.1 | RO
563 | Pac2 L | 0x0BD9 | 04 | U16 |  | RO
564 | Vac3 | 0x0BDA | 04 | U16 | V 0.1 | RO
565 | Iac3 | 0x0BDB | 04 | U16 | A 0.1 | RO
566 | Pac3 H | 0x0BDC | 04 | U16 | VA 0.1 | RO
567 | GridFirstDischargePowerRate | 0x0BDC | 03 | U16 |  | RO
568 | Pac3 L | 0x0BDD | 04 | U16 |  | RO
569 | GridFirstStopSOC | 0x0BDD | 03 | U16 |  | RO
570 | Vac RS_ | 0x0BDE | 04 | U16 | V 0.1 | RO
571 | Vac ST_ | 0x0BDF | 04 | U16 | V 0.1 | RO
572 | Vac TR_ | 0x0BE0 | 04 | U16 | V 0.1 | RO
573 | Ptouser total H | 0x0BE1 | 04 | U16 | W 0.1 | RO
574 | Ptouser total L | 0x0BE2 | 04 | U16 |  | RO
575 | Ptogrid total H | 0x0BE3 | 04 | U16 | W 0.1 | RO
576 | Ptogrid total L | 0x0BE4 | 04 | U16 |  | RO
577 | Ptoload total H | 0x0BE5 | 04 | U16 | W 0.1 | RO
578 | Ptoload total L | 0x0BE6 | 04 | U16 |  | RO
579 | Grid First StopSwitch 3 | 0x0BE6 | 03 | U16 |  | RO
580 | Time total H | 0x0BE7 | 04 | U16 |  | RO
581 | BatFirstPowerRate | 0x0BE7 | 03 | U16 |  | RO
582 | Time total L | 0x0BE8 | 04 | U16 |  | RO
583 | wBatFirst stopSOC | 0x0BE8 | 03 | U16 |  | RO
584 | Eac today H | 0x0BE9 | 04 | U16 | kWh 0.1 | RO | daily_energy
585 | AcChargeEnable | 0x0BE9 | 03 | U16 |  | RO
586 | Eac today L | 0x0BEA | 04 | U16 |  | RO | daily_energy
587 | Eac total H | 0x0BEB | 04 | U16 | kWh 0.1 | RO | cumulative_energy
588 | Eac total L | 0x0BEC | 04 | U16 |  | RO | cumulative_energy
589 | Epv total H_ | 0x0BED | 04 | U16 | kWh 0.1 | RO
590 | Epv total L_ | 0x0BEE | 04 | U16 |  | RO
591 | Epv1 today H_ | 0x0BEF | 04 | U16 | kWh 0.1 | RO
592 | Epv1 today L_ | 0x0BF0 | 04 | U16 |  | RO
593 | Epv1 total H_ | 0x0BF1 | 04 | U16 | kWh 0.1 | RO
594 | Epv1 total L_ | 0x0BF2 | 04 | U16 |  | RO
595 | Epv2 today H_ | 0x0BF3 | 04 | U16 | kWh 0.1 | RO
596 | Epv2 today L_ | 0x0BF4 | 04 | U16 |  | RO
597 | Epv2 total H_ | 0x0BF5 | 04 | U16 | kWh 0.1 | RO
598 | Epv2 total L_ | 0x0BF6 | 04 | U16 |  | RO
599 | Epv3 today H_ | 0x0BF7 | 04 | U16 | kWh 0.1 | RO
600 | Epv3 today L_ | 0x0BF8 | 04 | U16 |  | RO
601 | Epv3 total H_ | 0x0BF9 | 04 | U16 | kWh 0.1 | RO
602 | Epv3 total L_ | 0x0BFA | 04 | U16 |  | RO
603 | Etouser today H_ | 0x0BFB | 04 | U16 | kWh 0.1 | RO
604 | Etouser today L_ | 0x0BFC | 04 | U16 |  | RO
605 | Etouser total H_ | 0x0BFD | 04 | U16 | kWh 0.1 | RO
606 | Etouser total L_ | 0x0BFE | 04 | U16 |  | RO
607 | Etogrid today H_ | 0x0BFF | 04 | U16 | kWh 0.1 | RO
608 | Etogrid today L_ | 0x0C00 | 04 | U16 |  | RO
609 | Etogrid total H_ | 0x0C01 | 04 | U16 | kWh 0.1 | RO
610 | Etogrid total L_ | 0x0C02 | 04 | U16 |  | RO
611 | Eload today H_ | 0x0C03 | 04 | U16 | kWh 0.1 | RO
612 | Eload today L_ | 0x0C04 | 04 | U16 |  | RO
613 | Eload total H_ | 0x0C05 | 04 | U16 | kWh 0.1 | RO
614 | Eload total L_ | 0x0C06 | 04 | U16 |  | RO
615 | DCI R_ | 0x0C10 | 04 | U16 |  | RO
616 | DCI S_ | 0x0C11 | 04 | U16 |  | RO
617 | DCI T_ | 0x0C12 | 04 | U16 |  | RO
618 | GFCI | 0x0C13 | 04 | U16 |  | RO
619 | Temp1 | 0x0C15 | 04 | U16 | ℃ 0.1 | RO
620 | Temp2 | 0x0C16 | 04 | U16 | ℃ 0.1 | RO
621 | Pdischr max H | 0x0C16 | 03 | U16 | W 0.1 | RO
622 | Temp3 | 0x0C17 | 04 | U16 | ℃ 0.1 | RO
623 | Pdischr maxL | 0x0C17 | 03 | U16 |  | RO
624 | Temp4 | 0x0C18 | 04 | U16 | ℃ 0.1 | RO
625 | Pchr max H | 0x0C18 | 03 | U16 | W 0.1 | RO
626 | Temp5 | 0x0C19 | 04 | U16 | ℃ 0.1 | RO
627 | Pchr max L | 0x0C19 | 03 | U16 |  | RO
628 | FW Code1 | 0x0C1B | 04 | ASCII |  | RO
629 | FW Code2 | 0x0C1C | 04 | ASCII |  | RO
630 | Processor1FW Vision | 0x0C1D | 04 | ASCII |  | RO
631 | Reset UserInfo | 0x0C1E | 04 | U16 |  | RO
632 | Reset tofactory | 0x0C1F | 04 | U16 |  | RO
633 | StandbyFlag | 0x0C20 | 04 | U16 |  | RO
634 | inv start delaytime | 0x0C2B | 04 | U16 |  | RO
635 | Edischr today H_ | 0x0C35 | 04 | U16 | kWh 0.1 | RO
636 | Edischr today L_ | 0x0C36 | 04 | U16 |  | RO
637 | Edischr total H_ | 0x0C37 | 04 | U16 | kWh 0.1 | RO
638 | Edischr total L_ | 0x0C38 | 04 | U16 |  | RO
639 | Echr today H_ | 0x0C39 | 04 | U16 | kWh 0.1 | RO
640 | Echr today L_ | 0x0C3A | 04 | U16 |  | RO
641 | Echr total H_ | 0x0C3B | 04 | U16 | kWh 0.1 | RO
642 | Echr total L_ | 0x0C3C | 04 | U16 |  | RO
643 | Eacchr today H_ | 0x0C3D | 04 | U16 | kWh 0.1 | RO
644 | Eacchr today L_ | 0x0C3E | 04 | U16 |  | RO
645 | Eacchr total H_ | 0x0C3F | 04 | U16 | kWh 0.1 | RO
646 | Eacchr total L_ | 0x0C40 | 04 | U16 |  | RO
647 | Priority | 0x0C48 | 04 | U16 |  | RO
648 | EPS Fac | 0x0C49 | 04 | U16 | Hz 0.01 | RO
649 | EPS Vac1 | 0x0C4A | 04 | U16 | V 0.1 | RO
650 | EPS Iac1 | 0x0C4B | 04 | U16 | A 0.1 | RO
651 | EPS Pac1 H | 0x0C4C | 04 | U16 | VA 0.1 | RO
652 | EPS Pac1 L | 0x0C4D | 04 | U16 |  | RO
653 | EPS Vac2 | 0x0C4E | 04 | U16 | V 0.1 | RO
654 | EPS Iac2 | 0x0C4F | 04 | U16 | A 0.1 | RO
655 | EPS Pac2 H | 0x0C50 | 04 | U16 | VA 0.1 | RO
656 | EPS Pac2 L | 0x0C51 | 04 | U16 |  | RO
657 | EPS Vac3 | 0x0C52 | 04 | U16 | V 0.1 | RO
658 | EPS Iac3 | 0x0C53 | 04 | U16 | A 0.1 | RO
659 | EPS Pac3 H | 0x0C54 | 04 | U16 | VA 0.1 | RO
660 | EPS Pac3 L | 0x0C55 | 04 | U16 |  | RO
661 | EPS Pac H | 0x0C56 | 04 | U16 | VA 0.1 | RO | pv_power
662 | EPS Pac L | 0x0C57 | 04 | U16 |  | RO | pv_power
663 | Loadpercent | 0x0C58 | 04 | U16 | % 0.10 | RO
664 | Power factor | 0x0C59 | 04 | U16 |  | RO | power_factor
665 | DCV | 0x0C5A | 04 | U16 |  | RO
666 | WarnCode | 0x0C60 | 04 | U16 |  | RO
667 | Vbat | 0x0C61 | 04 | U16 | V 0.01 | RO
668 | Ibat | 0x0C62 | 04 | U16 | A 0.1 | RO
669 | Vbus1 | 0x0C64 | 04 | U16 | V 0.1 | RO
670 | Vbus2 | 0x0C65 | 04 | U16 | V 0.1 | RO
671 | Ibb | 0x0C66 | 04 | U16 | A 0.1 | RO
672 | Illc | 0x0C67 | 04 | U16 | A 0.1 | RO
673 | TempA | 0x0C68 | 04 | U16 | ℃ 0.1 | RO
674 | TempB | 0x0C69 | 04 | U16 | ℃ 0.1 | RO
675 | Pdischr H | 0x0C6A | 04 | U16 | W 0.1 | RO
676 | Pdischr L | 0x0C6B | 04 | U16 |  | RO
677 | Pchr H | 0x0C6C | 04 | U16 | W 0.1 | RO
678 | Pchr L | 0x0C6D | 04 | U16 |  | RO
679 | Edischr total H_ | 0x0C6E | 04 | U16 | kWh 0.1 | RO
680 | Edischr total L_ | 0x0C6F | 04 | U16 |  | RO
681 | Echr total H_ | 0x0C70 | 04 | U16 | kWh 0.1 | RO
682 | Echr total L_ | 0x0C71 | 04 | U16 |  | RO
683 | BDC1 Flag_ | 0x0C73 | 04 | U16 |  | RO
684 | WarnCode | 0x0C77 | 04 | U16 |  | RO
685 | Vbat | 0x0C78 | 04 | U16 | V 0.01 | RO
686 | Ibat | 0x0C79 | 04 | U16 | A 0.1 | RO
687 | Vbus1 | 0x0C7B | 04 | U16 | V 0.1 | RO
688 | Vbus2 | 0x0C7C | 04 | U16 | V 0.1 | RO
689 | Ibb | 0x0C7D | 04 | U16 | A 0.1 | RO
690 | Illc | 0x0C7E | 04 | U16 | A 0.1 | RO
691 | TempA | 0x0C7F | 04 | U16 | ℃ 0.1 | RO
692 | TempB | 0x0C80 | 04 | U16 | ℃ 0.1 | RO
693 | Pdischr H | 0x0C81 | 04 | U16 | W 0.1 | RO
694 | Pdischr L | 0x0C82 | 04 | U16 |  | RO
695 | Pchr H | 0x0C83 | 04 | U16 | W 0.1 | RO
696 | Pchr L | 0x0C84 | 04 | U16 |  | RO
697 | Edischr total H_ | 0x0C85 | 04 | U16 | kWh 0.1 | RO
698 | Edischr total L_ | 0x0C86 | 04 | U16 |  | RO
699 | Echr total H_ | 0x0C87 | 04 | U16 | kWh 0.1 | RO
700 | Echr total L_ | 0x0C88 | 04 | U16 |  | RO
701 | BDC2 Flag_ | 0x0C8A | 04 | U16 |  | RO
702 | BMS WarnInfo_ | 0x0C8E | 04 | U16 |  | RO
703 | BMS SOC_ | 0x0C8F | 04 | U16 |  | RO
704 | BMS BatteryVol_t | 0x0C90 | 04 | U16 | V 0.01 | RO
705 | BMS BatteryCur_r | 0x0C91 | 04 | U16 | A 0.01 | RO
706 | BMS BatteryTe_mp | 0x0C92 | 04 | U16 | ℃ 0.1 | RO
707 | BMS MaxCurr_ | 0x0C93 | 04 | U16 | A 0.01 | RO
708 | BMS DeltaVolt_ | 0x0C94 | 04 | U16 | A 0.01 | RO
709 | BMS CycleCnt_ | 0x0C95 | 04 | U16 |  | RO
710 | BMS SOH_ | 0x0C96 | 04 | U16 |  | RO
711 | BMS ConstantV_olt | 0x0C97 | 04 | U16 | V 0.01 | RO
712 | BMS BMSInfo_ | 0x0C98 | 04 | U16 |  | RO
713 | BMS PackInfo_ | 0x0C99 | 04 | U16 |  | RO
714 | BMS UsingCap_ | 0x0C9A | 04 | U16 |  | RO
715 | BMS FW_ | 0x0C9B | 04 | U16 |  | RO
716 | BMS MCUVersi_on | 0x0C9C | 04 | U16 |  | RO
717 | BMSCommType | 0x0C9D | 04 | U16 |  | RO
718 | Debug data | 0x0CA2 | 04 | U16 |  | RO
719 | Data logger | 0x2711 | 04 | U16 |  | RO
720 | Data logger | 0x2712 | 04 | U16 |  | RO
721 | Data logger | 0x2713 | 04 | U16 |  | RO
722 | Data logger | 0x2714 | 04 | U16 |  | RO
723 | Confluence box | 0x2AF9 | 04 | U16 |  | RO
724 | AutoTest fail | 0x800000 | 04 | U16 |  | RO
725 | No Utility | 0x1000000 | 04 | U16 |  | RO
726 | PV Isolation Low | 0x2000000 | 04 | U16 |  | RO
727 | Residual I High | 0x4000000 | 04 | U16 |  | RO
728 | Output High DCI | 0x8000000 | 04 | U16 |  | RO
729 | PV Voltage high | 0x10000000 | 04 | U16 |  | RO
730 | AC V Outrange | 0x20000000 | 04 | U16 | V | RO
731 | AC F Outrange | 0x40000000 | 04 | U16 |  | RO
732 | TempratureHigh | 0x80000000 | 04 | U16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)