## 1_INFO
Stage 1 — 레지스터맵 추출 (MAPPING_RULES_V2)
제조사 | STP60
프로토콜 버전
설비 타입 | inverter
MPPT | 0
String | 0
String 모니터링 | No (MPPT당 1 String)
IV Scan | No
IV Data Points | -
IV Trackers | -
원본 파일 | STP60_SHP75_STPS60-SunSpec_Modbus-TI-en-15.pdf
추출 일시 | 2026-04-03 15:58
H01 매칭 | 15/15
DER 매칭 | 33/33
추출 레지스터 | 188
REVIEW | 0
INFO 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | DEVICE_MODEL (PDF) | PDF |  | TEXT |  | RO |  | Technical Information - SUNNY TRIPOWER 60 / SUNNY HIGHPOWER PEAK1 / SUNNY TRIPOWER STORAGE 60 - SunSpec® ®
2 | Mn | 0x9C44 | 03 | STRING |  | RO |  | Manufacturer
3 | Md | 0x9C54 | 03 | STRING |  | RO |  | Model
4 | Opt | 0x9C64 | 03 | STRING |  | RO |  | Options
5 | Vr | 0x9C6C | 03 | STRING |  | RO |  | Version
6 | SERIAL_NUMBER | 0x9C74 | 03 | STRING |  | RO |  | SN ¦ Serial number
7 | DA | 0x9C84 | 03 | UINT16 |  | RO |  | Modbus unit ID of the device
8 | TmpSnk | 0x9D1B | 03 | INT16 |  | RO |  | Heat sink temperature
9 | Time period for change of the apparent power limitation | 0x9DA9 | 03 | UINT16 |  | RO
10 | Permitted reaction time for change of the apparent power limita- | 0x9DAA | 03 | UINT16 |  | RO
11 | Snw | 0x9FB3 | 03 | INT16 |  | RO |  | Snow depth
STATUS 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | St | 0x9D1F | 03 | ENUM16 |  | RO | inverter_status | Operating status
ALARM 레지스터
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field | Comment
1 | StVnd | 0x9D20 | 03 |  |  | RO |  | Manufacturer-specific status code

## 2_H01
H01 모니터링 매칭 — 15/15
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE | S32 | V | 0.1 | DER-AVM 고정 주소 사용
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT | S32 | A | 0.1 | DER-AVM 고정 주소 사용
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER | S32 | W | 0.1 | DER-AVM 고정 주소 사용
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR | S32 |  | 0.1 | DER-AVM 고정 주소 사용
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY | S32 | Hz | 0.1 | DER-AVM 고정 주소 사용
10 | pv_voltage | HANDLER | O | - | - | U16 | V |  | handler 계산: average(MPPT_N_voltage for N if voltage > 100V)
11 | pv_current | HANDLER | O | - | - | U16 | A |  | handler 계산: 1순위: sum(STRING_N_current), 2순위: sum(MPPT_N_current)
12 | pv_power | HANDLER | O | - | - | U16 | W |  | handler 계산: 1순위: PDF Total DC Power, 2순위: sum(MPPT_N_power)
13 | cumulative_energy | PDF | O | 0x9D11 | WH | ACC32
14 | cumulative_energy_low | PDF | - | - | - |  |  |  | 소수부 레지스터 없음 (단일 레지스터)
15 | status | PDF | O | 0x9D1F | St | ENUM16
16 | alarm1 | PDF | O | 0x9D20 | StVnd
17 | alarm2 | PDF | - | - | - |  |  |  | 보조 알람 없음
18 | alarm3 | PDF | - | - | - |  |  |  | 보조 알람 없음

## 3_MPPT_STRING
MPPT & String 매칭 — MPPT 0ch / String 0ch
MPPT 채널 수 | 0
String 채널 수 | 0
String 모니터링 | No (MPPT당 1 String)
MPPT 채널 H01 매칭 (0개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
String 채널 H01 매칭 (0개)
No | H01 Field | Source | Status | Address | Definition | Type | Unit | Scale | Note
MONITORING 전체 (168개)
No | Definition | Address | FC | Type | Unit/Scale | R/W | H01 Field
1 | SID | 0x9C40 | 03 | UINT32 |  | RO
2 | ID | 0x9C42 | 03 | UINT16 |  | RO
3 | Number of the following Modbus registers in accordance with | 0x9C43 | 03 | UINT16 |  | RO
4 | Active power setpoint WSpt in 0.01 % | 0x9C57 | 03 | UINT16 |  | RW
5 | ID | 0x9C86 | 03 | UINT16 |  | RO
6 | Number of the following Modbus registers in accordance with | 0x9C87 | 03 | UINT16 |  | RO
7 | ID | 0x9C95 | 03 | UINT16 |  | RO
8 | Number of the following Modbus registers in accordance | 0x9C96 | 03 | UINT16 |  | RO
9 | Name | 0x9C97 | 03 | STRING |  | RO
10 | CfgSt | 0x9C9B | 03 | ENUM16 |  | RO
11 | ChgSt | 0x9C9C | 03 |  |  | RO
12 | Cap | 0x9C9D | 03 |  |  | RO
13 | Cfg | 0x9C9E | 03 | ENUM16 |  | RO
14 | Ctl | 0x9C9F | 03 | ENUM16 |  | RO
15 | Addr | 0x9CA0 | 03 | STRING |  | RO
16 | Msk | 0x9CA8 | 03 | STRING |  | RO
17 | Gw | 0x9CB0 | 03 | STRING |  | RO
18 | DNS1: NaN | 0x9CB8 | 03 | STRING |  | RO
19 | DNS2: NaN | 0x9CC0 | 03 | STRING |  | RO
20 | NTP1: NaN | 0x9CC8 | 03 | STRING |  | RO
21 | NTP2: NaN | 0x9CD4 | 03 | STRING |  | RO
22 | DomNam | 0x9CE0 | 03 | STRING |  | RO
23 | HostNam | 0x9CEC | 03 | STRING |  | RO
24 | ID | 0x9CF9 | 03 | UINT16 |  | RO
25 | Number of the following Modbus registers in accordance | 0x9CFA | 03 | UINT16 |  | RO
26 | A | 0x9CFB | 03 | UINT16 |  | RO
27 | AphA | 0x9CFC | 03 | UINT16 |  | RO
28 | AphB | 0x9CFD | 03 | UINT16 |  | RO
29 | AphC | 0x9CFE | 03 | UINT16 |  | RO
30 | PPVphAB | 0x9D00 | 03 | UINT16 |  | RO
31 | PPVphBC | 0x9D01 | 03 | UINT16 |  | RO
32 | PPVphCA | 0x9D02 | 03 | UINT16 |  | RO
33 | PPVphA | 0x9D03 | 03 | UINT16 |  | RO
34 | PPVphB | 0x9D04 | 03 | UINT16 |  | RO
35 | PPVphC | 0x9D05 | 03 | UINT16 |  | RO
36 | W | 0x9D07 | 03 | INT16 |  | RO
37 | Hz | 0x9D09 | 03 | UINT16 |  | RO
38 | VA | 0x9D0B | 03 | INT16 |  | RO
39 | REACTIVE_POWER | 0x9D0D | 03 | INT16 |  | RO | reactive_power
40 | POWER_FACTOR | 0x9D0F | 03 | INT16 |  | RO | power_factor
41 | WH | 0x9D11 | 03 | ACC32 |  | RO | cumulative_energy
42 | DCA | 0x9D14 | 03 | UINT16 |  | RO
43 | DCV | 0x9D16 | 03 | UINT16 |  | RO
44 | DCW | 0x9D18 | 03 | INT16 |  | RO
45 | TmpCab | 0x9D1A | 03 | INT16 |  | RO
46 | TmpTrns | 0x9D1C | 03 | INT16 |  | RO
47 | TmpOt | 0x9D1D | 03 | INT16 |  | RO
48 | Evt1 | 0x9D21 | 03 | BITFIELD32 |  | RO
49 | Evt2 | 0x9D23 | 03 | BITFIELD32 |  | RO
50 | EvtVnd1 | 0x9D25 | 03 | BITFIELD32 |  | RO
51 | EvtVnd2 | 0x9D27 | 03 | BITFIELD32 |  | RO
52 | EvtVnd3 | 0x9D29 | 03 | BITFIELD32 |  | RO
53 | EvtVnd4 | 0x9D2B | 03 | BITFIELD32 |  | RO
54 | ID | 0x9D2D | 03 | UINT16 |  | RO
55 | Number of the following Modbus registers in accordance with | 0x9D2E | 03 | UINT16 |  | RO
56 | DERTyp | 0x9D2F | 03 | ENUM16 |  | RO
57 | WRtg | 0x9D30 | 03 | UINT16 |  | RO
58 | VARtg | 0x9D32 | 03 | UINT16 |  | RO
59 | Continuous reactive power capability in quadrant 1 | 0x9D34 | 03 | INT16 |  | RO
60 | Continuous reactive power capability in quadrant 2 | 0x9D35 | 03 | INT16 |  | RO
61 | Continuous reactive power capability in quadrant 3 | 0x9D36 | 03 | INT16 |  | RO
62 | Continuous reactive power capability in quadrant 4 | 0x9D37 | 03 | INT16 |  | RO
63 | ARtg | 0x9D39 | 03 | UINT16 |  | RO
64 | Minimum displacement power factor capability in Q 1 | 0x9D3B | 03 | INT16 |  | RO
65 | Minimum displacement power factor capability in Q 2 | 0x9D3C | 03 | INT16 |  | RO
66 | Minimum displacement power factor capability in Q 3 | 0x9D3D | 03 | INT16 |  | RO
67 | Minimum displacement power factor capability in Q 4 | 0x9D3E | 03 | INT16 |  | RO
68 | WHRtg | 0x9D40 | 03 | UINT16 |  | RO
69 | Maximum energy transfer rate from the storage device (Max- | 0x9D46 | 03 | UINT16 |  | RO
70 | ID | 0x9D49 | 03 | UINT16 |  | RO
71 | Number of the following Modbus registers in accordance with | 0x9D4A | 03 | UINT16 |  | RO
72 | WMax | 0x9D4B | 03 | UINT16 |  | RO
73 | VMax | 0x9D4E | 03 | UINT16 |  | RO
74 | VMin | 0x9D4F | 03 | UINT16 |  | RO
75 | VAMax | 0x9D50 | 03 | UINT16 |  | RO
76 | VArMaxQ1 | 0x9D51 | 03 | INT16 |  | RO
77 | VArMaxQ2 | 0x9D52 | 03 | INT16 |  | RO
78 | VArMaxQ3 | 0x9D53 | 03 | INT16 |  | RO
79 | VArMaxQ4 | 0x9D54 | 03 | INT16 |  | RO
80 | WGra | 0x9D55 | 03 | UINT16 |  | RO
81 | PFMinQ1 | 0x9D56 | 03 | INT16 |  | RO
82 | PFMinQ2 | 0x9D57 | 03 | INT16 |  | RO
83 | PFMinQ3 | 0x9D58 | 03 | INT16 |  | RO
84 | PFMinQ4 | 0x9D59 | 03 | INT16 |  | RO
85 | VAr action when changing between charging and discharging | 0x9D5A | 03 | ENUM16 |  | RO
86 | ClcTotVA | 0x9D5B | 03 | ENUM16 |  | RO
87 | MaxRmpRte | 0x9D5C | 03 | UINT16 |  | RO
88 | ECPNomHz | 0x9D5D | 03 | UINT16 |  | RO
89 | ConnPh | 0x9D5E | 03 | ENUM16 |  | RO
90 | ID | 0x9D69 | 03 | UINT16 |  | RO
91 | Number of the following Modbus registers in accordance with | 0x9D6A | 03 | UINT16 |  | RO
92 | PVConn | 0x9D6B | 03 |  |  | RO
93 | StorConn | 0x9D6C | 03 |  |  | RO
94 | ECPConn | 0x9D6D | 03 |  |  | RO
95 | ActWh | 0x9D6E | 03 | ACC64 |  | RO
96 | ActVAh | 0x9D72 | 03 | ACC64 |  | RO
97 | ActVArhQ1 | 0x9D76 | 03 | ACC64 |  | RO
98 | ActVArhQ2 | 0x9D7A | 03 | ACC64 |  | RO
99 | ActVArhQ3 | 0x9D7E | 03 | ACC64 |  | RO
100 | ActVArhQ4 | 0x9D82 | 03 | ACC64 |  | RO
101 | Reactive power available independently of active power (VArA- | 0x9D86 | 03 | INT16 |  | RO
102 | WAval | 0x9D88 | 03 | UINT16 |  | RO
103 | StSetLimMsk | 0x9D8A | 03 |  |  | RO
104 | StActCtl | 0x9D8C | 03 |  |  | RO
105 | TmSrc | 0x9D8E | 03 | STRING |  | RO
106 | Tms | 0x9D92 | 03 | UINT32 |  | RO
107 | s | 0x9D94 | 03 |  |  | RO
108 | Ris | 0x9D95 | 03 | UINT16 |  | RO
109 | ID | 0x9D97 | 03 | UINT16 |  | RO
110 | Number of the following Modbus registers in accordance with | 0x9D98 | 03 | UINT16 |  | RO
111 | Time period for grid connection / disconnection | 0x9D99 | 03 | UINT16 |  | RO
112 | Conn_RvrtTms | 0x9D9A | 03 | UINT16 |  | RO
113 | Time period for change of the power limitation (WMax- | 0x9D9D | 03 | UINT16 |  | RO
114 | Permitted reaction time for change of the power limitation | 0x9D9E | 03 | UINT16 |  | RO
115 | Ramp-up time for change from current to new set value (WMax- | 0x9D9F | 03 | UINT16 |  | RO
116 | WMaxLim_Ena | 0x9DA0 | 03 | ENUM16 |  | RO
117 | OutPFSet | 0x9DA1 | 03 | INT16 |  | RW
118 | Time period for change of the power factor (Out- | 0x9DA2 | 03 | UINT16 |  | RO
119 | Permitted reaction time for change of the power factor (Out- | 0x9DA3 | 03 | UINT16 |  | RO
120 | Ramp-up time for change from current to new set value (Out- | 0x9DA4 | 03 | UINT16 |  | RO
121 | OutPFSet_Ena | 0x9DA5 | 03 | ENUM16 |  | RW
122 | VArMaxPct | 0x9DA7 | 03 | INT16 |  | RO
123 | VArAvalPct | 0x9DA8 | 03 | INT16 |  | RO
124 | Ramp-up time for change from current to new set value | 0x9DAB | 03 | UINT16 |  | RO
125 | VArPct_Mod | 0x9DAC | 03 | ENUM16 |  | RO
126 | ID | 0x9DB1 | 03 | UINT16 |  | RO
127 | Number of the following Modbus registers in accordance with | 0x9DB2 | 03 | UINT16 |  | RO
128 | ID | 0x9DCB | 03 | UINT16 |  | RO
129 | Number of the following Modbus registers in accordance with | 0x9DCC | 03 | UINT16 |  | RO
130 | ID | 0x9E0D | 03 | UINT16 |  | RO
131 | Number of the following Modbus registers in accordance with | 0x9E0E | 03 | UINT16 |  | RO
132 | ID | 0x9E19 | 03 | UINT16 |  | RO
133 | Number of the following Modbus registers in accordance with | 0x9E1A | 03 | UINT16 |  | RO
134 | ID | 0x9E29 | 03 | UINT16 |  | RO
135 | Number of the following Modbus registers in accordance with | 0x9E2A | 03 | UINT16 |  | RO
136 | ID | 0x9E6B | 03 | UINT16 |  | RO
137 | Number of the following Modbus registers in accordance with | 0x9E6C | 03 | UINT16 |  | RO
138 | ID | 0x9EAD | 03 | UINT16 |  | RO
139 | Number of the following Modbus registers in accordance with | 0x9EAE | 03 | UINT16 |  | RO
140 | ID | 0x9F2F | 03 | UINT16 |  | RO
141 | Number of the following Modbus registers in accordance with | 0x9F30 | 03 | UINT16 |  | RO
142 | ID | 0x9F6D | 03 | UINT16 |  | RO
143 | Number of the following Modbus registers in accordance with | 0x9F6E | 03 | UINT16 |  | RO
144 | ID | 0x9FAB | 03 | UINT16 |  | RO
145 | Number of the following Modbus registers in accordance with | 0x9FAC | 03 | UINT16 |  | RO
146 | TmpAmb | 0x9FAD | 03 | INT16 |  | RO
147 | RH | 0x9FAE | 03 | INT16 |  | RO
148 | Pres | 0x9FAF | 03 | INT16 |  | RO
149 | WndSpd | 0x9FB0 | 03 | INT16 |  | RO
150 | WndDir | 0x9FB1 | 03 | INT16 |  | RO
151 | Rain | 0x9FB2 | 03 | INT16 |  | RO
152 | PPT | 0x9FB4 | 03 | INT16 |  | RO
153 | ElecFld | 0x9FB5 | 03 | INT16 |  | RO
154 | SurWet | 0x9FB6 | 03 | INT16 |  | RO
155 | SoilWet | 0x9FB7 | 03 | INT16 |  | RO
156 | ID | 0x9FB8 | 03 | UINT16 |  | RO
157 | Number of the following Modbus registers in accordance with | 0x9FB9 | 03 | UINT16 |  | RO
158 | GHI | 0x9FBA | 03 | UINT16 |  | RO
159 | TmpBOM | 0x9FBB | 03 | INT16 |  | RO
160 | TmpAmb | 0x9FBC | 03 | INT16 |  | RO
161 | WndSpd | 0x9FBD | 03 | UINT16 |  | RO
162 | ID | 0x9FBE | 03 | UINT16 |  | RO
163 | Number of the following Modbus registers in accordance with | 0x9FBF | 03 | UINT16 |  | RO
164 | GHI | 0x9FC0 | 03 | UINT16 |  | RO
165 | POAI | 0x9FC1 | 03 | UINT16 |  | RO
166 | DFI | 0x9FC2 | 03 | UINT16 |  | RO
167 | DNI | 0x9FC3 | 03 | UINT16 |  | RO
168 | OTI | 0x9FC4 | 03 | UINT16 |  | RO

## 4_DER
DER-AVM 매칭 — 33/33 (Sheet 4)
No | Field | Type | Status | Address | Scale | R/W | Description
1 | DER_POWER_FACTOR_SET | S16 | O | 0x07D0 | 0.001 | RW | Power factor [-1000,-800],[800,1000]
2 | DER_ACTION_MODE | U16 | O | 0x07D1 | 1 | RW | Action mode: 0=Self, 2=DER-AVM, 5=Q(V)
3 | DER_REACTIVE_POWER_PCT | S16 | O | 0x07D2 | 0.1 | RW | Reactive power % [-484,484]
4 | DER_ACTIVE_POWER_PCT | U16 | O | 0x07D3 | 0.1 | RW | Active power % [0,1100]
5 | INVERTER_ON_OFF | U16 | O | 0x0834 | 1 | RW | On/Off: 0=ON, 1=OFF
6 | CLEAR_PV_INSULATION_WARNING | U16 | O | 0x0835 | 1 | WO | Clear PV insulation warning
7 | INVERTER_CONTROL | U16 | O | 0x6001 | 1 | WO | Inverter: 0=Power on, 1=Shut down
8 | IV_CURVE_SCAN | U16 | O | 0x600D | 1 | RW | IV scan: W 0=Stop,1=Start; R 0=Idle,1=Running,2=Finished
9 | POWER_FACTOR_DYNAMIC | S16 | O | 0x600F | 0.001 | RW | Dynamic power factor
10 | REACTIVE_POWER_DYNAMIC | S16 | O | 0x6010 | 0.01 | RW | Dynamic reactive power (%)
11 | POWER_DERATING_PCT | U16 | O | 0x3005 | 1 | RW | Active power derating [0-110]%
12 | DEA_L1_CURRENT_LOW | S32 | O | 0x03E8 | 0.1 | RO | DEA L1 current (low)
13 | DEA_L1_CURRENT_HIGH | S32 | O | 0x03E9 |  | RO | (high)
14 | DEA_L2_CURRENT_LOW | S32 | O | 0x03EA | 0.1 | RO | DEA L2 current (low)
15 | DEA_L2_CURRENT_HIGH | S32 | O | 0x03EB |  | RO | (high)
16 | DEA_L3_CURRENT_LOW | S32 | O | 0x03EC | 0.1 | RO | DEA L3 current (low)
17 | DEA_L3_CURRENT_HIGH | S32 | O | 0x03ED |  | RO | (high)
18 | DEA_L1_VOLTAGE_LOW | S32 | O | 0x03EE | 0.1 | RO | DEA L1 voltage (low)
19 | DEA_L1_VOLTAGE_HIGH | S32 | O | 0x03EF |  | RO | (high)
20 | DEA_L2_VOLTAGE_LOW | S32 | O | 0x03F0 | 0.1 | RO | DEA L2 voltage (low)
21 | DEA_L2_VOLTAGE_HIGH | S32 | O | 0x03F1 |  | RO | (high)
22 | DEA_L3_VOLTAGE_LOW | S32 | O | 0x03F2 | 0.1 | RO | DEA L3 voltage (low)
23 | DEA_L3_VOLTAGE_HIGH | S32 | O | 0x03F3 |  | RO | (high)
24 | DEA_TOTAL_ACTIVE_POWER_LOW | S32 | O | 0x03F4 | 0.1 | RO | DEA active power (low)
25 | DEA_TOTAL_ACTIVE_POWER_HIGH | S32 | O | 0x03F5 |  | RO | (high)
26 | DEA_TOTAL_REACTIVE_POWER_LOW | S32 | O | 0x03F6 | 1 | RO | DEA reactive power (low)
27 | DEA_TOTAL_REACTIVE_POWER_HIGH | S32 | O | 0x03F7 |  | RO | (high)
28 | DEA_POWER_FACTOR_LOW | S32 | O | 0x03F8 | 0.001 | RO | DEA power factor (low)
29 | DEA_POWER_FACTOR_HIGH | S32 | O | 0x03F9 |  | RO | (high)
30 | DEA_FREQUENCY_LOW | S32 | O | 0x03FA | 0.1 | RO | DEA frequency (low)
31 | DEA_FREQUENCY_HIGH | S32 | O | 0x03FB |  | RO | (high)
32 | DEA_STATUS_FLAG_LOW | S32 | O | 0x03FC | 1 | RO | DEA status flag (low)
33 | DEA_STATUS_FLAG_HIGH | S32 | O | 0x03FD |  | RO | (high)