## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=0, STR=0)
제조사 | STP60
용량 | -
MPPT | 0
String/MPPT | 2
Total Strings | 0
H01 매칭 | 15/18
DER 매칭 | 33/33
총 레지스터 | 181
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | DEVICE_MODEL (PDF) |  | TEXT |  | RO |  | Technical Information - SUNNY TRIPOWER 60 / SUNNY HIGHPOWER PEAK1 / SUNNY TRIPOWER STORAGE 60 - SunSpec® ®
2 | Mn | 0x9C44 | STRING |  | RO |  | Manufacturer
3 | Md | 0x9C54 | STRING |  | RO |  | Model
4 | Opt | 0x9C64 | STRING |  | RO |  | Options
5 | Vr | 0x9C6C | STRING |  | RO |  | Version
6 | SERIAL_NUMBER | 0x9C74 | STRING |  | RO |  | SN ¦ Serial number
7 | DA | 0x9C84 | UINT16 |  | RO |  | Modbus unit ID of the device
8 | TmpSnk | 0x9D1B | INT16 |  | RO |  | Heat sink temperature
9 | Time period for change of the apparent power limitation | 0x9DA9 | UINT16 |  | RO
10 | Permitted reaction time for change of the apparent power limita- | 0x9DAA | UINT16 |  | RO
11 | Snw | 0x9FB3 | INT16 |  | RO |  | Snow depth
H01 MONITORING (168개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | SID | 0x9C40 | UINT32 |  | RO
2 | ID | 0x9C42 | UINT16 |  | RO
3 | Number of the following Modbus registers in accordance with | 0x9C43 | UINT16 |  | RO
4 | Active power setpoint WSpt in 0.01 % | 0x9C57 | UINT16 |  | RW
5 | ID | 0x9C86 | UINT16 |  | RO
6 | Number of the following Modbus registers in accordance with | 0x9C87 | UINT16 |  | RO
7 | ID | 0x9C95 | UINT16 |  | RO
8 | Number of the following Modbus registers in accordance | 0x9C96 | UINT16 |  | RO
9 | Name | 0x9C97 | STRING |  | RO
10 | CfgSt | 0x9C9B | ENUM16 |  | RO
11 | ChgSt | 0x9C9C |  |  | RO
12 | Cap | 0x9C9D |  |  | RO
13 | Cfg | 0x9C9E | ENUM16 |  | RO
14 | Ctl | 0x9C9F | ENUM16 |  | RO
15 | Addr | 0x9CA0 | STRING |  | RO
16 | Msk | 0x9CA8 | STRING |  | RO
17 | Gw | 0x9CB0 | STRING |  | RO
18 | DNS1: NaN | 0x9CB8 | STRING |  | RO
19 | DNS2: NaN | 0x9CC0 | STRING |  | RO
20 | NTP1: NaN | 0x9CC8 | STRING |  | RO
21 | NTP2: NaN | 0x9CD4 | STRING |  | RO
22 | DomNam | 0x9CE0 | STRING |  | RO
23 | HostNam | 0x9CEC | STRING |  | RO
24 | ID | 0x9CF9 | UINT16 |  | RO
25 | Number of the following Modbus registers in accordance | 0x9CFA | UINT16 |  | RO
26 | A | 0x9CFB | UINT16 |  | RO
27 | AphA | 0x9CFC | UINT16 |  | RO
28 | AphB | 0x9CFD | UINT16 |  | RO
29 | AphC | 0x9CFE | UINT16 |  | RO
30 | PPVphAB | 0x9D00 | UINT16 |  | RO
31 | PPVphBC | 0x9D01 | UINT16 |  | RO
32 | PPVphCA | 0x9D02 | UINT16 |  | RO
33 | PPVphA | 0x9D03 | UINT16 |  | RO
34 | PPVphB | 0x9D04 | UINT16 |  | RO
35 | PPVphC | 0x9D05 | UINT16 |  | RO
36 | W | 0x9D07 | INT16 |  | RO
37 | Hz | 0x9D09 | UINT16 |  | RO
38 | VA | 0x9D0B | INT16 |  | RO
39 | REACTIVE_POWER | 0x9D0D | INT16 |  | RO | reactive_power
40 | POWER_FACTOR | 0x9D0F | INT16 |  | RO | power_factor
41 | WH | 0x9D11 | ACC32 |  | RO | cumulative_energy
42 | DCA | 0x9D14 | UINT16 |  | RO
43 | DCV | 0x9D16 | UINT16 |  | RO
44 | DCW | 0x9D18 | INT16 |  | RO
45 | TmpCab | 0x9D1A | INT16 |  | RO
46 | TmpTrns | 0x9D1C | INT16 |  | RO
47 | TmpOt | 0x9D1D | INT16 |  | RO
48 | Evt1 | 0x9D21 | BITFIELD32 |  | RO
49 | Evt2 | 0x9D23 | BITFIELD32 |  | RO
50 | EvtVnd1 | 0x9D25 | BITFIELD32 |  | RO
51 | EvtVnd2 | 0x9D27 | BITFIELD32 |  | RO
52 | EvtVnd3 | 0x9D29 | BITFIELD32 |  | RO
53 | EvtVnd4 | 0x9D2B | BITFIELD32 |  | RO
54 | ID | 0x9D2D | UINT16 |  | RO
55 | Number of the following Modbus registers in accordance with | 0x9D2E | UINT16 |  | RO
56 | DERTyp | 0x9D2F | ENUM16 |  | RO
57 | WRtg | 0x9D30 | UINT16 |  | RO
58 | VARtg | 0x9D32 | UINT16 |  | RO
59 | Continuous reactive power capability in quadrant 1 | 0x9D34 | INT16 |  | RO
60 | Continuous reactive power capability in quadrant 2 | 0x9D35 | INT16 |  | RO
61 | Continuous reactive power capability in quadrant 3 | 0x9D36 | INT16 |  | RO
62 | Continuous reactive power capability in quadrant 4 | 0x9D37 | INT16 |  | RO
63 | ARtg | 0x9D39 | UINT16 |  | RO
64 | Minimum displacement power factor capability in Q 1 | 0x9D3B | INT16 |  | RO
65 | Minimum displacement power factor capability in Q 2 | 0x9D3C | INT16 |  | RO
66 | Minimum displacement power factor capability in Q 3 | 0x9D3D | INT16 |  | RO
67 | Minimum displacement power factor capability in Q 4 | 0x9D3E | INT16 |  | RO
68 | WHRtg | 0x9D40 | UINT16 |  | RO
69 | Maximum energy transfer rate from the storage device (Max- | 0x9D46 | UINT16 |  | RO
70 | ID | 0x9D49 | UINT16 |  | RO
71 | Number of the following Modbus registers in accordance with | 0x9D4A | UINT16 |  | RO
72 | WMax | 0x9D4B | UINT16 |  | RO
73 | VMax | 0x9D4E | UINT16 |  | RO
74 | VMin | 0x9D4F | UINT16 |  | RO
75 | VAMax | 0x9D50 | UINT16 |  | RO
76 | VArMaxQ1 | 0x9D51 | INT16 |  | RO
77 | VArMaxQ2 | 0x9D52 | INT16 |  | RO
78 | VArMaxQ3 | 0x9D53 | INT16 |  | RO
79 | VArMaxQ4 | 0x9D54 | INT16 |  | RO
80 | WGra | 0x9D55 | UINT16 |  | RO
81 | PFMinQ1 | 0x9D56 | INT16 |  | RO
82 | PFMinQ2 | 0x9D57 | INT16 |  | RO
83 | PFMinQ3 | 0x9D58 | INT16 |  | RO
84 | PFMinQ4 | 0x9D59 | INT16 |  | RO
85 | VAr action when changing between charging and discharging | 0x9D5A | ENUM16 |  | RO
86 | ClcTotVA | 0x9D5B | ENUM16 |  | RO
87 | MaxRmpRte | 0x9D5C | UINT16 |  | RO
88 | ECPNomHz | 0x9D5D | UINT16 |  | RO
89 | ConnPh | 0x9D5E | ENUM16 |  | RO
90 | ID | 0x9D69 | UINT16 |  | RO
91 | Number of the following Modbus registers in accordance with | 0x9D6A | UINT16 |  | RO
92 | PVConn | 0x9D6B |  |  | RO
93 | StorConn | 0x9D6C |  |  | RO
94 | ECPConn | 0x9D6D |  |  | RO
95 | ActWh | 0x9D6E | ACC64 |  | RO
96 | ActVAh | 0x9D72 | ACC64 |  | RO
97 | ActVArhQ1 | 0x9D76 | ACC64 |  | RO
98 | ActVArhQ2 | 0x9D7A | ACC64 |  | RO
99 | ActVArhQ3 | 0x9D7E | ACC64 |  | RO
100 | ActVArhQ4 | 0x9D82 | ACC64 |  | RO
101 | Reactive power available independently of active power (VArA- | 0x9D86 | INT16 |  | RO
102 | WAval | 0x9D88 | UINT16 |  | RO
103 | StSetLimMsk | 0x9D8A |  |  | RO
104 | StActCtl | 0x9D8C |  |  | RO
105 | TmSrc | 0x9D8E | STRING |  | RO
106 | Tms | 0x9D92 | UINT32 |  | RO
107 | s | 0x9D94 |  |  | RO
108 | Ris | 0x9D95 | UINT16 |  | RO
109 | ID | 0x9D97 | UINT16 |  | RO
110 | Number of the following Modbus registers in accordance with | 0x9D98 | UINT16 |  | RO
111 | Time period for grid connection / disconnection | 0x9D99 | UINT16 |  | RO
112 | Conn_RvrtTms | 0x9D9A | UINT16 |  | RO
113 | Time period for change of the power limitation (WMax- | 0x9D9D | UINT16 |  | RO
114 | Permitted reaction time for change of the power limitation | 0x9D9E | UINT16 |  | RO
115 | Ramp-up time for change from current to new set value (WMax- | 0x9D9F | UINT16 |  | RO
116 | WMaxLim_Ena | 0x9DA0 | ENUM16 |  | RO
117 | OutPFSet | 0x9DA1 | INT16 |  | RW
118 | Time period for change of the power factor (Out- | 0x9DA2 | UINT16 |  | RO
119 | Permitted reaction time for change of the power factor (Out- | 0x9DA3 | UINT16 |  | RO
120 | Ramp-up time for change from current to new set value (Out- | 0x9DA4 | UINT16 |  | RO
121 | OutPFSet_Ena | 0x9DA5 | ENUM16 |  | RW
122 | VArMaxPct | 0x9DA7 | INT16 |  | RO
123 | VArAvalPct | 0x9DA8 | INT16 |  | RO
124 | Ramp-up time for change from current to new set value | 0x9DAB | UINT16 |  | RO
125 | VArPct_Mod | 0x9DAC | ENUM16 |  | RO
126 | ID | 0x9DB1 | UINT16 |  | RO
127 | Number of the following Modbus registers in accordance with | 0x9DB2 | UINT16 |  | RO
128 | ID | 0x9DCB | UINT16 |  | RO
129 | Number of the following Modbus registers in accordance with | 0x9DCC | UINT16 |  | RO
130 | ID | 0x9E0D | UINT16 |  | RO
131 | Number of the following Modbus registers in accordance with | 0x9E0E | UINT16 |  | RO
132 | ID | 0x9E19 | UINT16 |  | RO
133 | Number of the following Modbus registers in accordance with | 0x9E1A | UINT16 |  | RO
134 | ID | 0x9E29 | UINT16 |  | RO
135 | Number of the following Modbus registers in accordance with | 0x9E2A | UINT16 |  | RO
136 | ID | 0x9E6B | UINT16 |  | RO
137 | Number of the following Modbus registers in accordance with | 0x9E6C | UINT16 |  | RO
138 | ID | 0x9EAD | UINT16 |  | RO
139 | Number of the following Modbus registers in accordance with | 0x9EAE | UINT16 |  | RO
140 | ID | 0x9F2F | UINT16 |  | RO
141 | Number of the following Modbus registers in accordance with | 0x9F30 | UINT16 |  | RO
142 | ID | 0x9F6D | UINT16 |  | RO
143 | Number of the following Modbus registers in accordance with | 0x9F6E | UINT16 |  | RO
144 | ID | 0x9FAB | UINT16 |  | RO
145 | Number of the following Modbus registers in accordance with | 0x9FAC | UINT16 |  | RO
146 | TmpAmb | 0x9FAD | INT16 |  | RO
147 | RH | 0x9FAE | INT16 |  | RO
148 | Pres | 0x9FAF | INT16 |  | RO
149 | WndSpd | 0x9FB0 | INT16 |  | RO
150 | WndDir | 0x9FB1 | INT16 |  | RO
151 | Rain | 0x9FB2 | INT16 |  | RO
152 | PPT | 0x9FB4 | INT16 |  | RO
153 | ElecFld | 0x9FB5 | INT16 |  | RO
154 | SurWet | 0x9FB6 | INT16 |  | RO
155 | SoilWet | 0x9FB7 | INT16 |  | RO
156 | ID | 0x9FB8 | UINT16 |  | RO
157 | Number of the following Modbus registers in accordance with | 0x9FB9 | UINT16 |  | RO
158 | GHI | 0x9FBA | UINT16 |  | RO
159 | TmpBOM | 0x9FBB | INT16 |  | RO
160 | TmpAmb | 0x9FBC | INT16 |  | RO
161 | WndSpd | 0x9FBD | UINT16 |  | RO
162 | ID | 0x9FBE | UINT16 |  | RO
163 | Number of the following Modbus registers in accordance with | 0x9FBF | UINT16 |  | RO
164 | GHI | 0x9FC0 | UINT16 |  | RO
165 | POAI | 0x9FC1 | UINT16 |  | RO
166 | DFI | 0x9FC2 | UINT16 |  | RO
167 | DNI | 0x9FC3 | UINT16 |  | RO
168 | OTI | 0x9FC4 | UINT16 |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | St | 0x9D1F | ENUM16 |  | RO | inverter_status | Operating status
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | StVnd | 0x9D20 |  |  | RO |  | Manufacturer-specific status code

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | STP60
용량 | -
MPPT | 0 (PDF max 0개)
String | 0 (2/MPPT)
H01 매칭 | 15/18
DER 매칭 | 33/33
총 레지스터 | 181
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 11
MONITORING | 168
STATUS | 1
ALARM | 1
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | HANDLER | O | - | -
13 | cumulative_energy | PDF | O | 0x9D11 | WH
14 | cumulative_energy_low | PDF | - | - | -
15 | status | PDF | O | 0x9D1F | St
16 | alarm1 | PDF | O | 0x9D20 | StVnd
17 | alarm2 | PDF | - | - | -
18 | alarm3 | PDF | - | - | -