## 1_REGISTER_MAP
Stage 2 — 레지스터맵 (MPPT=9, STR=18)
제조사 | Solarize
용량 | -
MPPT | 9
String/MPPT | 2
Total Strings | 18
H01 매칭 | 60/60
DER 매칭 | 33/33
총 레지스터 | 196
REVIEW | 0
INFO 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | INNER_TEMP | 0x101C | S16 | °C 1 | RO | temperature | Inner Temperature
2 | Total Energy | 0x1021 | U32 | kWh | RO | cumulative_energy
3 | Total generation time | 0x1023 | U32 |  | RO
4 | Decimals of total energy | 0x104C | U16 |  | RO | cumulative_energy_low | Wh
5 | Device Model name | 0x1A00 | STRINGING |  | RO |  | Ex.：PV 30KTL
6 | Device Serial number | 0x1A10 | STRINGING |  | RO |  | Ex.：1234-123456789
7 | Master firmware version | 0x1A1C | STRINGING |  | RO |  | Ex.：123456
8 | Slave firmware version | 0x1A26 | STRINGING |  | RO |  | Ex.：123456
9 | MPPT_COUNT | 0x1A3B | U16 |  | RO |  | MPPT Number ¦ Ex.：1=1 MPPT
10 | Nominal Voltage | 0x1A44 | U16 |  | RO |  | Ex.：2200 = 220V
11 | Nominal Frequency | 0x1A45 | U16 |  | RO |  | Ex.：5000 = 50Hz
12 | Nominal Active Power(Low word) | 0x1A46 | U16 | W 1 | RO |  | Ex.：1500 = 1500W
13 | Grid Phase Number | 0x1A48 | U16 |  | RO |  | 1=single phase2=split phase3=three phases
14 | Nominal Active Power(High word) | 0x1A4E | U16 | W 1 | RO |  | Ex.：1 = (1*65536)W
15 | EMS Firmware Version | 0x1A60 | STRINGING |  | RO |  | Ex.：123456
16 | LCD firmware version | 0x1A8E | STRINGING |  | RO |  | Ex.：123456
H01 MONITORING (168개)
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Broadcast address | 0x0000 | U16 |  | RO
2 | Start bit | 0x0001 | U16 |  | RO
3 | Register number | 0x0002 | U16 |  | RO
4 | Read register address | 0x0003 | U16 |  | RO
5 | PV string reverse | 0x0005 | STRINGING |  | RO
6 | 0x07 | 0x0007 | U16 |  | RO
7 | Dc-link over voltage | 0x0009 | U16 |  | RO
8 | Software incompatibility | 0x000B | U16 |  | RO
9 | Data inconsistency | 0x000D | U16 |  | RO
10 | Byte number | 0x0026 | U16 |  | RO
11 | L1 Voltage | 0x1001 | U16 | V 0.1 | RO | r_voltage
12 | L1 Current | 0x1002 | U16 | A 0.01 | RO | r_current
13 | L1 Power | 0x1003 | S32 | W 0.1 | RO
14 | L1 Frequency | 0x1005 | U16 | Hz 0.01 | RO | frequency
15 | L2 Voltage | 0x1006 | U16 | V 0.1 | RO | s_voltage
16 | L2 Current | 0x1007 | U16 | A 0.01 | RO | s_current
17 | L2 Power | 0x1008 | S32 | W 0.1 | RO
18 | L2 Frequency | 0x100A | U16 | Hz 0.01 | RO | frequency
19 | L3 Voltage | 0x100B | U16 | V 0.1 | RO | t_voltage
20 | L3 Current | 0x100C | U16 | A 0.01 | RO | t_current
21 | L3 Power | 0x100D | S32 | W 0.1 | RO
22 | L3 Frequency | 0x100F | U16 | Hz 0.01 | RO | frequency
23 | MPPT1 Voltage | 0x1010 | U16 | V 0.1 | RO | mppt1_voltage
24 | MPPT1 Current | 0x1011 | S16 | A 0.01 | RO | mppt1_current
25 | MPPT1 Power | 0x1012 | U32 | W 0.1 | RO | mppt1_power
26 | MPPT2 Voltage | 0x1014 | U16 | V 0.1 | RO | mppt2_voltage
27 | MPPT2 Current | 0x1015 | S16 | A 0.01 | RO | mppt2_current
28 | MPPT2 Power | 0x1016 | U32 | W 0.1 | RO | mppt2_power
29 | MPPT3 Voltage | 0x1018 | U16 | V 0.1 | RO | mppt3_voltage
30 | MPPT3 Current | 0x1019 | S16 | A 0.01 | RO | mppt3_current
31 | MPPT3 Power | 0x101A | U32 | W 0.1 | RO | mppt3_power
32 | DAILY_ENERGY | 0x1027 | U32 | Wh | RO | daily_energy
33 | Grid total Active Power | 0x1037 | S32 | W 0.1 | RO | ac_power
34 | Grid total Reactive Power | 0x1039 | S32 |  | RO | ac_power
35 | PV Today Peak Power | 0x103B | S32 | W 0.1 | RO
36 | Power Factor | 0x103D | S16 |  | RO | power_factor
37 | MPPT4 Voltage | 0x103E | U16 | V 0.1 | RO | mppt4_voltage
38 | MPPT4 Current | 0x103F | S16 | A 0.01 | RO | mppt4_current
39 | MPPT4 Power | 0x1040 | U32 | W 0.1 | RO | mppt4_power
40 | PV total input power | 0x1048 | U32 | W 0.1 | RO | pv_power
41 | String1 input voltage | 0x1050 | U16 | V 0.1 | RO | string1_voltage
42 | String1 input current | 0x1051 | S16 | A 0.01 | RO | string1_current
43 | String2 input voltage | 0x1052 | U16 | V 0.1 | RO | string2_voltage
44 | String2 input current | 0x1053 | S16 | A 0.01 | RO | string2_current
45 | String3 input voltage | 0x1054 | U16 | V 0.1 | RO | string3_voltage
46 | String3 input current | 0x1055 | S16 | A 0.01 | RO | string3_current
47 | String4 input voltage | 0x1056 | U16 | V 0.1 | RO | string4_voltage
48 | String4 input current | 0x1057 | S16 | A 0.01 | RO | string4_current
49 | String5 input voltage | 0x1058 | U16 | V 0.1 | RO | string5_voltage
50 | String5 input current | 0x1059 | S16 | A 0.01 | RO | string5_current
51 | String6 input voltage | 0x105A | U16 | V 0.1 | RO | string6_voltage
52 | String6 input current | 0x105B | S16 | A 0.01 | RO | string6_current
53 | String7 input voltage | 0x105C | U16 | V 0.1 | RO | string7_voltage
54 | String7 input current | 0x105D | S16 | A 0.01 | RO | string7_current
55 | String8 input voltage | 0x105E | U16 | V 0.1 | RO | string8_voltage
56 | String8 input current | 0x105F | S16 | A 0.01 | RO | string8_current
57 | String9 input voltage | 0x1060 | U16 | V 0.1 | RO | string9_voltage
58 | String9 input current | 0x1061 | S16 | A 0.01 | RO | string9_current
59 | String10 input voltage | 0x1062 | U16 | V 0.1 | RO | string10_voltage
60 | String10 input current | 0x1063 | S16 | A 0.01 | RO | string10_current
61 | String11 input voltage | 0x1064 | U16 | V 0.1 | RO | string11_voltage
62 | String11 input current | 0x1065 | S16 | A 0.01 | RO | string11_current
63 | String12 input voltage | 0x1066 | U16 | V 0.1 | RO | string12_voltage
64 | String12 input current | 0x1067 | S16 | A 0.01 | RO | string12_current
65 | String13 input voltage | 0x1068 | U16 | V 0.1 | RO | string13_voltage
66 | String13 input current | 0x1069 | S16 | A 0.01 | RO | string13_current
67 | String14 input voltage | 0x106A | U16 | V 0.1 | RO | string14_voltage
68 | String14 input current | 0x106B | S16 | A 0.01 | RO | string14_current
69 | String15 input voltage | 0x106C | U16 | V 0.1 | RO | string15_voltage
70 | String15 input current | 0x106D | S16 | A 0.01 | RO | string15_current
71 | String16 input voltage | 0x106E | U16 | V 0.1 | RO | string16_voltage
72 | String16 input current | 0x106F | S16 | A 0.01 | RO | string16_current
73 | String17 input voltage | 0x1070 | U16 | V 0.1 | RO | string17_voltage
74 | String17 input current | 0x1071 | S16 | A 0.01 | RO | string17_current
75 | String18 input voltage | 0x1072 | U16 | V 0.1 | RO | string18_voltage
76 | String18 input current | 0x1073 | S16 | A 0.01 | RO | string18_current
77 | MPPT5 Voltage | 0x1080 | U16 | V 0.1 | RO | mppt5_voltage
78 | MPPT5 Current | 0x1081 | S16 | A 0.01 | RO | mppt5_current
79 | MPPT5 Power | 0x1082 | U32 | W 0.1 | RO | mppt5_power
80 | MPPT6 Voltage | 0x1084 | U16 | V 0.1 | RO | mppt6_voltage
81 | MPPT6 Current | 0x1085 | S16 | A 0.01 | RO | mppt6_current
82 | MPPT6 Power | 0x1086 | U32 | W 0.1 | RO | mppt6_power
83 | MPPT7 Voltage | 0x1088 | U16 | V 0.1 | RO | mppt7_voltage
84 | MPPT7 Current | 0x1089 | S16 | A 0.01 | RO | mppt7_current
85 | MPPT7 Power | 0x108A | U32 | W 0.1 | RO | mppt7_power
86 | MPPT8 Voltage | 0x108C | U16 | V 0.1 | RO | mppt8_voltage
87 | MPPT8 Current | 0x108D | S16 | A 0.01 | RO | mppt8_current
88 | MPPT8 Power | 0x108E | U32 | W 0.1 | RO | mppt8_power
89 | MPPT9 Voltage | 0x1090 | U16 | V 0.1 | RO | mppt9_voltage
90 | MPPT9 Current | 0x1091 | S16 | A 0.01 | RO | mppt9_current
91 | MPPT9 Power | 0x1092 | U32 | W 0.1 | RO | mppt9_power
92 | External fan speed dutypercentage | 0x120C | U16 |  | RO
93 | Q (Reference Output reactivepower) | 0x1226 | S16 |  | RO
94 | L1 watt of grid | 0x1300 | S32 | W 0.1 | RO
95 | L2 watt of grid | 0x1302 | S32 | W 0.1 | RO
96 | L3 watt of grid | 0x1304 | S32 | W 0.1 | RO
97 | Accumulated energy ofimport | 0x1306 | U32 | Wh 10 | RO | cumulative_energy
98 | Accumulated energy ofexport | 0x1308 | U32 | Wh 10 | RO | cumulative_energy
99 | L1 watt of load | 0x130A | U32 | W 0.1 | RO
100 | L2 watt of load | 0x130C | U32 | W 0.1 | RO
101 | L3 watt of load | 0x130E | U32 | W 0.1 | RO
102 | Accumulated energy of load | 0x1310 | U32 | Wh 10 | RO | cumulative_energy
103 | L1-N phase voltage of grid | 0x131A | U16 | V 0.1 | RO
104 | L2-N phase voltage of grid | 0x131B | U16 | V 0.1 | RO
105 | L3-N phase voltage of grid | 0x131C | U16 | V 0.1 | RO
106 | L1 current of grid | 0x131D | S32 | A 0.01 | RO
107 | L2 current of grid | 0x131F | S32 | A 0.01 | RO
108 | L3 current of grid | 0x1321 | S32 | A 0.01 | RO
109 | L1-N phase voltage of load | 0x1323 | U16 | V 0.1 | RO
110 | L2-N phase voltage of load | 0x1324 | U16 | V 0.1 | RO
111 | L3-N phase voltage of load | 0x1325 | U16 | V 0.1 | RO
112 | L1 current of load | 0x1326 | S32 | A 0.01 | RO
113 | L2 current of load | 0x1328 | S32 | A 0.01 | RO
114 | L3 current of load | 0x132A | S32 | A 0.01 | RO
115 | Today import Energy | 0x1332 | U32 | Wh 10 | RO
116 | Today export Energy | 0x1334 | U32 | Wh 10 | RO
117 | Today load Energy | 0x1336 | U32 | Wh 10 | RO
118 | Frequency of grid | 0x1338 | U16 | Hz 0.01 | RO
119 | Power flow direction | 0x30B2 | U16 |  | RW
120 | Maximum feed in grid power | 0x30B9 | U32 |  | RW
121 | Clear the EEPROM historyenergy record | 0x6009 | U16 |  | RW
122 | Tracker 1 voltage | 0x8000 | U16 | V 0.1 | RO
123 | String 1-1 current | 0x8040 | S16 | A 0.01 | RO | string_current
124 | String 1-2 current | 0x8080 | STRINGING | A 0.01 | RO | string_current
125 | String 1-3 current | 0x80C0 | STRINGING | A 0.01 | RO | string_current
126 | String 1-4 current | 0x8100 | STRINGING | A 0.01 | RO | string_current
127 | Tracker 2 voltage | 0x8140 | U16 | V 0.1 | RO
128 | String 2-1 current | 0x8180 | STRINGING | A 0.01 | RO | string_current
129 | String 2-2 current | 0x81C0 | STRINGING | A 0.01 | RO | string_current
130 | String 2-3 current | 0x8200 | STRINGING | A 0.01 | RO | string_current
131 | String 2-4 current | 0x8240 | STRINGING | A 0.01 | RO | string_current
132 | Tracker 3 voltage | 0x8280 | U16 | V 0.1 | RO
133 | String 3-1 current | 0x82C0 | STRINGING | A 0.01 | RO | string_current
134 | String 3-2 current | 0x8300 | STRINGING | A 0.01 | RO | string_current
135 | String 3-3 current | 0x8340 | STRINGING | A 0.01 | RO | string_current
136 | String 3-4 current | 0x8380 | STRINGING | A 0.01 | RO | string_current
137 | Tracker 4 voltage | 0x83C0 | U16 | V 0.1 | RO
138 | String 4-1 current | 0x8400 | STRINGING | A 0.01 | RO | string_current
139 | String 4-2 current | 0x8440 | STRINGING | A 0.01 | RO | string_current
140 | String 4-3 current | 0x8480 | STRINGING | A 0.01 | RO | string_current
141 | String 4-4 current | 0x84C0 | STRINGING | A 0.01 | RO | string_current
142 | Tracker 5 voltage | 0x8500 | U16 | V 0.1 | RO
143 | String 5-1 current | 0x8540 | STRINGING | A 0.01 | RO | string_current
144 | String 5-2 current | 0x8580 | STRINGING | A 0.01 | RO | string_current
145 | String 5-3 current | 0x85C0 | STRINGING | A 0.01 | RO | string_current
146 | String 5-4 current | 0x8600 | STRINGING | A 0.01 | RO | string_current
147 | Tracker 6 voltage | 0x8640 | U16 | V 0.1 | RO
148 | String 6-1 current | 0x8680 | STRINGING | A 0.01 | RO | string_current
149 | String 6-2 current | 0x86C0 | STRINGING | A 0.01 | RO | string_current
150 | String 6-3 current | 0x8700 | STRINGING | A 0.01 | RO | string_current
151 | String 6-4 current | 0x8740 | STRINGING | A 0.01 | RO | string_current
152 | Tracker 7 voltage | 0x8780 | U16 | V 0.1 | RO
153 | String 7-1 current | 0x87C0 | STRINGING | A 0.01 | RO | string_current
154 | String 7-2 current | 0x8800 | STRINGING | A 0.01 | RO | string_current
155 | String 7-3 current | 0x8840 | STRINGING | A 0.01 | RO | string_current
156 | String 7-4 current | 0x8880 | STRINGING | A 0.01 | RO | string_current
157 | Tracker 8 voltage | 0x88C0 | U16 | V 0.1 | RO
158 | String 8-1 current | 0x8900 | STRINGING | A 0.01 | RO | string_current
159 | String 8-2 current | 0x8940 | STRINGING | A 0.01 | RO | string_current
160 | String 8-3 current | 0x8980 | STRINGING | A 0.01 | RO | string_current
161 | String 8-4 current | 0x89C0 | STRINGING | A 0.01 | RO | string_current
162 | Tracker 9 voltage | 0x8A00 | U16 | V 0.1 | RO
163 | String 9-1 current | 0x8A40 | STRINGING | A 0.01 | RO | string_current
164 | String 9-2 current | 0x8A80 | STRINGING | A 0.01 | RO | string_current
165 | String 9-3 current | 0x8AC0 | STRINGING | A 0.01 | RO | string_current
166 | String 9-4 current | 0x8B00 | STRINGING | A 0.01 | RO | string_current
167 | history log 0 | 0xB600 | U16 |  | RO
168 | history log 127 | 0xB77D | U16 |  | RO
STATUS 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | Inverter Mode | 0x101D | U16 |  | RO | inverter_status | Inverter Mode Table
2 | DER-AVM digital meterconnect status | 0x1210 | U16 |  | RO
3 | DER-AVM mode | 0x1211 | U16 |  | RW |  | 0: self control1: DER-AVM control
ALARM 레지스터
No | Definition | Address | Type | Unit/Scale | R/W | H01 Field | Comment
1 | GFCI abnormal | 0x0004 | U16 |  | RO
2 | Internal communication error | 0x000A | U16 |  | RO
3 | Internal storage error | 0x000C | U16 |  | RO
4 | Inverter abnormal | 0x000E | U16 |  | RO
5 | Boost abnormal | 0x000F | U16 |  | RO
6 | Error Code1 | 0x101E | U16 |  | RO | alarm1 | Error Code Table 1
7 | Error Code2 | 0x101F | U16 |  | RO | alarm2 | Error Code Table 2
8 | Error Code3 | 0x1020 | U16 |  | RO | alarm3 | Error Code Table 3
9 | EEPROM default | 0x6006 | U16 |  | RW

## 2_REVIEW
REVIEW — 0개 미결
REVIEW 항목 없음 — 모든 레지스터 자동 분류 완료

## 3_SUMMARY
Stage 2 Summary
제조사 | Solarize
용량 | -
MPPT | 9 (PDF max 9개)
String | 18 (2/MPPT)
H01 매칭 | 60/60
DER 매칭 | 33/33
총 레지스터 | 196
REVIEW 미결 | 0
REVIEW 자동 처리 | 0
카테고리별 수량
INFO | 16
MONITORING | 168
STATUS | 3
ALARM | 9
H01 매칭 상태
No | H01 Field | Source | Status | Address | Definition
1 | r_voltage | DER | O | 0x03EE~0x03EF | DEA_L1_VOLTAGE
2 | s_voltage | DER | O | 0x03F0~0x03F1 | DEA_L2_VOLTAGE
3 | t_voltage | DER | O | 0x03F2~0x03F3 | DEA_L3_VOLTAGE
4 | r_current | DER | O | 0x03E8~0x03E9 | DEA_L1_CURRENT
5 | s_current | DER | O | 0x03EA~0x03EB | DEA_L2_CURRENT
6 | t_current | DER | O | 0x03EC~0x03ED | DEA_L3_CURRENT
7 | ac_power | DER | O | 0x03F4~0x03F5 | DEA_TOTAL_ACTIVE_POWER
8 | power_factor | DER | O | 0x03F8~0x03F9 | DEA_POWER_FACTOR
9 | frequency | DER | O | 0x03FA~0x03FB | DEA_FREQUENCY
10 | pv_voltage | HANDLER | O | - | -
11 | pv_current | HANDLER | O | - | -
12 | pv_power | PDF | O | 0x1048 | PV total input power
13 | cumulative_energy | PDF | O | 0x1306 | Accumulated energy ofimport
14 | cumulative_energy_low | PDF | O | 0x104C | Decimals of total energy
15 | status | PDF | O | 0x101D | Inverter Mode
16 | alarm1 | PDF | O | 0x101E | Error Code1
17 | alarm2 | PDF | O | 0x101F | Error Code2
18 | alarm3 | PDF | O | 0x1020 | Error Code3
19 | mppt1_voltage | PDF | O | 0x1010 | MPPT1 Voltage
20 | mppt1_current | PDF | O | 0x1011 | MPPT1 Current
21 | mppt2_voltage | PDF | O | 0x1014 | MPPT2 Voltage
22 | mppt2_current | PDF | O | 0x1015 | MPPT2 Current
23 | mppt3_voltage | PDF | O | 0x1018 | MPPT3 Voltage
24 | mppt3_current | PDF | O | 0x1019 | MPPT3 Current
25 | mppt4_voltage | PDF | O | 0x103E | MPPT4 Voltage
26 | mppt4_current | PDF | O | 0x103F | MPPT4 Current
27 | mppt5_voltage | PDF | O | 0x1080 | MPPT5 Voltage
28 | mppt5_current | PDF | O | 0x1081 | MPPT5 Current
29 | mppt6_voltage | PDF | O | 0x1084 | MPPT6 Voltage
30 | mppt6_current | PDF | O | 0x1085 | MPPT6 Current
31 | mppt7_voltage | PDF | O | 0x1088 | MPPT7 Voltage
32 | mppt7_current | PDF | O | 0x1089 | MPPT7 Current
33 | mppt8_voltage | PDF | O | 0x108C | MPPT8 Voltage
34 | mppt8_current | PDF | O | 0x108D | MPPT8 Current
35 | mppt9_voltage | PDF | O | 0x1090 | MPPT9 Voltage
36 | mppt9_current | PDF | O | 0x1091 | MPPT9 Current
37 | string1_current | PDF | O | 0x1051 | String1 input current
38 | string2_current | PDF | O | 0x1053 | String2 input current
39 | string3_current | PDF | O | 0x1055 | String3 input current
40 | string4_current | PDF | O | 0x1057 | String4 input current
41 | string5_current | PDF | O | 0x1059 | String5 input current
42 | string6_current | PDF | O | 0x105B | String6 input current
43 | string7_current | PDF | O | 0x105D | String7 input current
44 | string8_current | PDF | O | 0x105F | String8 input current
45 | string9_current | PDF | O | 0x1061 | String9 input current
46 | string10_current | PDF | O | 0x1063 | String10 input current
47 | string11_current | PDF | O | 0x1065 | String11 input current
48 | string12_current | PDF | O | 0x1067 | String12 input current
49 | string13_current | PDF | O | 0x1069 | String13 input current
50 | string14_current | PDF | O | 0x106B | String14 input current
51 | string15_current | PDF | O | 0x106D | String15 input current
52 | string16_current | PDF | O | 0x106F | String16 input current
53 | string17_current | PDF | O | 0x1071 | String17 input current
54 | string18_current | PDF | O | 0x1073 | String18 input current
55 | string19_current | PDF | O | 0x1075 | String19 input current
56 | string20_current | PDF | O | 0x1077 | String20 input current
57 | string21_current | PDF | O | 0x1079 | String21 input current
58 | string22_current | PDF | O | 0x107B | String22 input current
59 | string23_current | PDF | O | 0x107D | String23 input current
60 | string24_current | PDF | O | 0x107F | String24 input current